## Sheet1
Heat Pump calculations
| Octopus | Design temps @ -2.5 | [8 empty] | Heat Geek | Design temp 21 @ -3.3
Room (HG name) | Design Temp | Heat Loss | Current Rad | Output | Prop change | Prop Output | Outp-Loss | Loss var | Loss var% | Rad % var | Heat Loss | Rad Output | Prop change | Prop Output | Delta T30 | Outp-Loss | Delta T24 | Outp-Loss
Bathroom | 22 | 355 | Towel 1150x600 | 265 |  | 265 | -90 | 50 | 15.15% | 69.74% | 305 | 380 |  | 380 | 194.94 | -110.06 | 145.54 | -159.46
Bedroom 1 (2) | 18 | 410 | K1 600x1600 | 805 |  | 805 | 395 | -196 | -38.58% | 53.56% | 606 | 1503 | 22 1600x600 | 1503 | 771.039 | 165.039 | 575.649 | -30.351 | optional 3rd (not included)
Bedroom 2 (3) | 18 | 253 | K1 500x1100 | 469 |  | 469 | 216 | -96 | -31.89% | 54.47% | 349 | 861 | 22 1100x600 | 1870 | 959.31 | 610.31 | 716.21 | 367.21 | optional 2nd / req with update
Bedroom 3 (1) | 18 | 415 | K1 600x1300 | 654 |  | 654 | 239 | -93 | -20.15% | 54.59% | 508 | 1198 |  | 1198 | 614.574 | 106.574 | 458.834 | -49.166
Bedroom 4 (Study) | 18 | 383 | K1 500x1600 | 682 |  | 682 | 299 | -233 | -46.65% | 54.43% | 616 | 1253 | 22 1600x600 | 2720 | 1395.36 | 779.36 | 1041.76 | 425.76 | required | 3 outside walls
Dining Room | 21 | 598 | K1 400x1800 | 540 | K2 300x1400 | 608 | 10 | 109 | 20.06% | 49.27% | 489 | 1096 |  | 1096 | 562.248 | 73.248 | 419.768 | -69.232
En Suite | 21 | 251 | Towel 1250x600 | 303 |  | 303 | 52 | -57 | -20.39% | 53.63% | 308 | 565 |  | 565 | 289.845 | -18.155 | 216.395 | -91.605
Entrance Hall | 18 | 441 | K2 700x800 | 806 |  | 806 | 365 | -133 | -26.21% | 50.38% | 574 | 1600 |  | 1600 | 820.8 | 246.8 | 612.8 | 38.8
Landing | [7 empty] | -446 | -100% |  | 446 |  |  |  |  | -446 |  | -446 | Landing not listed by Octopus
Kitchen | 21 | 747 | Des 1800x445 |  | see * below | 875 | 128 | -214 | -25.06% | 0 | 961 | 1372 | act. 1179 | 1179 | 604.827 | -356.173 | 451.557 | -509.443 | Heat Geek updated after correcting to lower figure
Sitting Room | 21 | 1244 | K2 500x1000 | 672 |  | 672 | -572 | 40 | 3.268% | 45.01% | 1204 | 1493 |  | 1493 | 765.909 | -438.091 | 571.819 | -632.181
" " |  |  | K2 400x1800 | 540 |  | 540 | 540 | n/a |  | 49.27% |  | 1096 |  | 1096 | 562.248 | 562.248 | 419.768 | 419.768
Utility | 18 | 475 | K1 600x500 | 251 | K2 600x600 | 538 | 63 | -44 | -8.853% | 32.51% | 519 | 772 |  | 772 | 396.036 | -122.964 | 295.676 | -223.324
Toilet | 18 | 190 | K1 450x500 | 192 |  | 192 | 2 | -23 | -11.41% | 54.55% | 213 | 352 |  | 352 | 180.576 | -32.424 | 134.816 | -78.184
|  | 5762 |  | 6179 |  | 7409 | 1647 |  |  |  | 7098 | 13541 |  | 15824 | 8117.712 | 1019.712 | 6060.592 | -1037.408
|  | 6130 | in proposal
Guessing that Octopus quote output at 50 flow, Heat Geek quote shows standard rated output
Loss var figures: col I, difference between heat loss estimates, negative means HG larger, col J % is diff as % of mean of the two
|  |  | * | Kitchen: Octopus say must u/g to a min of 1705W, 5817BTU standard output or won't meet grant qualification: HG say fine as is
Est energy usage for year |  | 14102 | [8 empty] | 17833
Est annual elec consumption |  | 4243 | [8 empty] | 4458.25
SCOP / G'teed efficiency |  | 3.6 | [8 empty] | 395 | %
SCOP hot water |  | 2.7771