## Sheet1
datetime | on_off_bin | htg_on_off | dhw_on_off | RWT | LWT | ambient | room_temp | dhw_temp | amps_in | volts_in | capacity | setLWT | flowrate | ability | energy_in | energy_out | MD02_tmp | MD02_hmd | comp_freq | fan | energy in | LWT-RWT | energy out
2025-01-11T06:00:33 | 10000001101000 | 1 | 0 | 50 | 56 | -4 | 25 | 45 | 18 | 219 | 14 | 58 | 1.03 | 7.55 | 22306 | 1292 | 17.7 | 36.9 | 55 | 610 | 0.0657 | 6 | 0.11588
2025-01-11T06:01:33 | 10000001101000 | 1 | 0 | 49 | 58 | -4 | 25 | 45 | 23 | 217 | 14 | 58 | 0.93 | 9.42 | 22306 | 1292 | 17.7 | 36.9 | 67 | 610 | 0.083183 | 9 | 0.15694
2025-01-11T06:02:33 | 10000001101000 | 1 | 0 | 49 | 58 | -4 | 25 | 45 | 16 | 220 | 14 | 58 | 0.93 | 9.07 | 22306 | 1292 | 17.7 | 36.8 | 51 | 610 | 0.058667 | 9 | 0.15694
2025-01-11T06:03:33 | 10000001101000 | 1 | 0 | 49 | 56 | -4 | 25 | 45 | 16 | 220 | 14 | 58 | 0.95 | 6.86 | 22307 | 1292 | 17.7 | 36.8 | 51 | 610 | 0.058667 | 7 | 0.12469
2025-01-11T06:04:33 | 10000001101000 | 1 | 0 | 49 | 56 | -4 | 25 | 45 | 18 | 220 | 14 | 58 | 0.93 | 7.44 | 22307 | 1292 | 17.7 | 36.8 | 55 | 610 | 0.066 | 7 | 0.12206
2025-01-11T06:05:33 | 10000001101000 | 1 | 0 | 49 | 57 | -4 | 25 | 45 | 22 | 219 | 14 | 58 | 0.89 | 8.83 | 22307 | 1292 | 17.7 | 36.8 | 65 | 610 | 0.0803 | 8 | 0.1335
2025-01-11T06:06:33 | 10000001101000 | 1 | 0 | 49 | 57 | -4 | 25 | 45 | 16 | 221 | 14 | 58 | 0.92 | 8.95 | 22307 | 1292 | 17.7 | 36.9 | 51 | 610 | 0.058933 | 8 | 0.138
2025-01-11T06:07:33 | 10000001101000 | 1 | 0 | 49 | 56 | -4 | 25 | 45 | 16 | 221 | 14 | 58 | 0.95 | 7.21 | 22307 | 1293 | 17.7 | 36.7 | 51 | 610 | 0.058933 | 7 | 0.12469
2025-01-11T06:08:33 | 10000001101000 | 1 | 0 | 49 | 56 | -4 | 25 | 45 | 18 | 220 | 14 | 58 | 0.94 | 7.55 | 22307 | 1293 | 17.7 | 36.8 | 55 | 610 | 0.066 | 7 | 0.12337
2025-01-11T06:09:33 | 10000001101000 | 1 | 0 | 49 | 58 | -4 | 25 | 45 | 19 | 220 | 14 | 58 | 0.93 | 9.18 | 22307 | 1293 | 17.7 | 36.7 | 61 | 610 | 0.069667 | 9 | 0.15694
2025-01-11T06:10:33 | 1010000001101000 | 1 | 0 | 49 | 50 | -4 | 25 | 45 | 2 | 226 | 14 | 58 | 1.06 | 4.07 | 22307 | 1293 | 17.7 | 36.7 | 29 | 30 | 0.0075333 | 1 | 0.019875
2025-01-11T06:11:33 | 1010000001101000 | 1 | 0 | 47 | 41 | -3 | 25 | 45 | 2 | 225 | 14 | 58 | 1.41 | 4.07 | 22307 | 1293 | 17.7 | 36.7 | 37 | 0 | 0.0075 | -6 | -0.15862
2025-01-11T06:12:33 | 1010000001101000 | 1 | 0 | 44 | 35 | -2 | 25 | 45 | 3 | 225 | 14 | 58 | 1.43 | 4.07 | 22307 | 1293 | 17.7 | 36.7 | 37 | 0 | 0.01125 | -9 | -0.24131
2025-01-11T06:13:33 | 10000001101000 | 1 | 0 | 38 | 27 | 0 | 25 | 45 | 6 | 224 | 14 | 58 | 1.44 | 4.07 | 22307 | 1293 | 17.7 | 36.6 | 32 | 0 | 0.0224 | -11 | -0.297
2025-01-11T06:14:33 | 10000001101000 | 1 | 0 | 35 | 38 | 1 | 25 | 45 | 9 | 224 | 14 | 58 | 1.45 | 4.07 | 22307 | 1293 | 17.7 | 36.6 | 40 | 590 | 0.0336 | 3 | 0.081562
2025-01-11T06:15:33 | 10000001101000 | 1 | 0 | 35 | 39 | 0 | 25 | 45 | 9 | 222 | 14 | 58 | 1.41 | 4.07 | 22307 | 1293 | 17.7 | 36.6 | 41 | 610 | 0.0333 | 4 | 0.10575
2025-01-11T06:16:33 | 10000001101000 | 1 | 0 | 36 | 40 | -1 | 25 | 45 | 14 | 220 | 14 | 58 | 1.41 | 4.07 | 22307 | 1293 | 17.7 | 36.6 | 55 | 620 | 0.051333 | 4 | 0.10575
2025-01-11T06:17:33 | 10000001101000 | 1 | 0 | 37 | 42 | -2 | 25 | 45 | 18 | 218 | 14 | 58 | 1.41 | 4.07 | 22307 | 1293 | 17.7 | 36.5 | 67 | 630 | 0.0654 | 5 | 0.13219
2025-01-11T06:18:33 | 10000001101000 | 1 | 0 | 39 | 45 | -2 | 25 | 45 | 19 | 219 | 14 | 58 | 1.4 | 9.42 | 22307 | 1293 | 17.7 | 36.5 | 67 | 630 | 0.06935 | 6 | 0.1575
2025-01-11T06:19:33 | 10000001101000 | 1 | 0 | 40 | 48 | -2 | 25 | 45 | 23 | 218 | 14 | 58 | 1.39 | 11.39 | 22307 | 1294 | 17.7 | 36.5 | 75 | 630 | 0.083567 | 8 | 0.2085
2025-01-11T06:20:33 | 10000001101000 | 1 | 0 | 42 | 49 | -3 | 25 | 45 | 23 | 218 | 14 | 58 | 1.37 | 10.93 | 22307 | 1294 | 17.7 | 36.5 | 75 | 630 | 0.083567 | 7 | 0.17981
2025-01-11T06:21:33 | 10000001101000 | 1 | 0 | 43 | 50 | -3 | 25 | 45 | 23 | 218 | 14 | 58 | 1.32 | 11.04 | 22307 | 1294 | 17.7 | 36.4 | 73 | 620 | 0.083567 | 7 | 0.17325
2025-01-11T06:22:33 | 10000001101000 | 1 | 0 | 44 | 51 | -3 | 25 | 45 | 23 | 219 | 14 | 58 | 1.31 | 10.46 | 22307 | 1294 | 17.7 | 36.4 | 73 | 610 | 0.08395 | 7 | 0.17194
2025-01-11T06:23:33 | 10000001101000 | 1 | 0 | 45 | 52 | -3 | 25 | 45 | 23 | 219 | 14 | 58 | 1.3 | 10.81 | 22308 | 1294 | 17.7 | 36.4 | 73 | 610 | 0.08395 | 7 | 0.17062
2025-01-11T06:24:33 | 10000001101000 | 1 | 0 | 46 | 53 | -3 | 25 | 45 | 23 | 219 | 14 | 58 | 1.38 | 10.81 | 22308 | 1294 | 17.6 | 36.5 | 73 | 610 | 0.08395 | 7 | 0.18113
2025-01-11T06:25:33 | 10000001101000 | 1 | 0 | 46 | 53 | -3 | 25 | 45 | 23 | 218 | 14 | 58 | 1.39 | 11.28 | 22308 | 1294 | 17.6 | 36.5 | 72 | 610 | 0.083567 | 7 | 0.18244
2025-01-11T06:26:33 | 10000001101000 | 1 | 0 | 47 | 54 | -3 | 25 | 45 | 23 | 218 | 14 | 58 | 1.37 | 10.93 | 22308 | 1294 | 17.7 | 36.6 | 71 | 610 | 0.083567 | 7 | 0.17981
2025-01-11T06:27:33 | 10000001101000 | 1 | 0 | 48 | 54 | -4 | 25 | 45 | 23 | 218 | 14 | 58 | 1.38 | 10.81 | 22308 | 1295 | 17.6 | 36.5 | 71 | 610 | 0.083567 | 6 | 0.15525
2025-01-11T06:28:33 | 10000001101000 | 1 | 0 | 48 | 55 | -4 | 25 | 45 | 24 | 218 | 14 | 58 | 1.38 | 10.81 | 22308 | 1295 | 17.6 | 36.6 | 71 | 600 | 0.0872 | 7 | 0.18113
2025-01-11T06:29:33 | 10000001101000 | 1 | 0 | 48 | 55 | -4 | 25 | 45 | 24 | 219 | 14 | 58 | 1.38 | 11.04 | 22308 | 1295 | 17.6 | 36.6 | 71 | 610 | 0.0876 | 7 | 0.18113
2025-01-11T06:30:33 | 10000001101000 | 1 | 0 | 49 | 56 | -4 | 25 | 45 | 24 | 218 | 14 | 58 | 1.4 | 11.16 | 22308 | 1295 | 17.6 | 36.6 | 72 | 610 | 0.0872 | 7 | 0.18375
2025-01-11T06:31:33 | 10000001101000 | 1 | 0 | 49 | 56 | -4 | 25 | 45 | 24 | 218 | 14 | 58 | 1.37 | 10.58 | 22308 | 1296 | 17.6 | 36.6 | 71 | 610 | 0.0872 | 7 | 0.17981
2025-01-11T06:32:33 | 10000001101000 | 1 | 0 | 50 | 57 | -4 | 25 | 45 | 24 | 219 | 14 | 58 | 1.39 | 10.93 | 22308 | 1296 | 17.6 | 36.6 | 71 | 610 | 0.0876 | 7 | 0.18244
2025-01-11T06:33:33 | 10000001101000 | 1 | 0 | 50 | 57 | -4 | 25 | 45 | 21 | 221 | 14 | 58 | 1.27 | 11.04 | 22308 | 1296 | 17.6 | 36.7 | 64 | 610 | 0.07735 | 7 | 0.16669
2025-01-11T06:34:33 | 10000001101000 | 1 | 0 | 50 | 56 | -4 | 25 | 45 | 21 | 221 | 14 | 58 | 1.15 | 9.18 | 22308 | 1296 | 17.6 | 36.7 | 64 | 610 | 0.07735 | 6 | 0.12937
2025-01-11T06:35:33 | 10000001101000 | 1 | 0 | 49 | 57 | -4 | 25 | 45 | 23 | 220 | 14 | 58 | 1.02 | 8.6 | 22309 | 1297 | 17.6 | 36.6 | 68 | 610 | 0.084333 | 8 | 0.153
2025-01-11T06:36:33 | 10000001101000 | 1 | 0 | 49 | 58 | -4 | 25 | 45 | 23 | 219 | 14 | 58 | 0.93 | 9.65 | 22309 | 1297 | 17.6 | 36.7 | 69 | 600 | 0.08395 | 9 | 0.15694
2025-01-11T06:37:33 | 10000001101000 | 1 | 0 | 49 | 58 | -4 | 25 | 45 | 21 | 220 | 14 | 58 | 0.94 | 9.76 | 22309 | 1297 | 17.6 | 36.7 | 64 | 600 | 0.077 | 9 | 0.15862
2025-01-11T06:38:33 | 10000001101000 | 1 | 0 | 50 | 56 | -4 | 25 | 45 | 18 | 222 | 14 | 58 | 1.03 | 7.09 | 22309 | 1297 | 17.6 | 36.7 | 55 | 610 | 0.0666 | 6 | 0.11588
2025-01-11T06:39:33 | 10000001101000 | 1 | 0 | 49 | 56 | -4 | 25 | 45 | 20 | 220 | 14 | 58 | 1.04 | 7.44 | 22309 | 1297 | 17.6 | 36.7 | 62 | 610 | 0.073333 | 7 | 0.1365
2025-01-11T06:40:33 | 10000001101000 | 1 | 0 | 49 | 58 | -4 | 25 | 45 | 24 | 218 | 14 | 58 | 0.96 | 10.23 | 22309 | 1297 | 17.7 | 36.6 | 69 | 610 | 0.0872 | 9 | 0.162
2025-01-11T06:41:33 | 10000001101000 | 1 | 0 | 49 | 58 | -4 | 25 | 45 | 20 | 219 | 14 | 58 | 0.94 | 9.88 | 22309 | 1297 | 17.6 | 36.6 | 62 | 610 | 0.073 | 9 | 0.15862
2025-01-11T06:42:33 | 10000001101000 | 1 | 0 | 50 | 56 | -4 | 25 | 45 | 17 | 221 | 14 | 58 | 1.05 | 7.32 | 22309 | 1297 | 17.6 | 36.6 | 53 | 610 | 0.062617 | 6 | 0.11812
2025-01-11T06:43:33 | 10000001101000 | 1 | 0 | 50 | 56 | -4 | 25 | 45 | 18 | 220 | 14 | 58 | 1.05 | 7.32 | 22309 | 1298 | 17.7 | 36.6 | 55 | 610 | 0.066 | 6 | 0.11812
2025-01-11T06:44:33 | 10000001101000 | 1 | 0 | 49 | 57 | -4 | 25 | 45 | 23 | 218 | 14 | 58 | 0.96 | 8.37 | 22309 | 1298 | 17.6 | 36.7 | 67 | 610 | 0.083567 | 8 | 0.144
2025-01-11T06:45:33 | 10000001101000 | 1 | 0 | 49 | 58 | -4 | 25 | 45 | 20 | 219 | 14 | 58 | 0.91 | 9.65 | 22309 | 1298 | 17.6 | 36.6 | 63 | 610 | 0.073 | 9 | 0.15356
2025-01-11T06:46:33 | 10000001101000 | 1 | 0 | 49 | 56 | -4 | 25 | 45 | 16 | 220 | 14 | 58 | 0.93 | 6.86 | 22309 | 1298 | 17.7 | 36.6 | 51 | 610 | 0.058667 | 7 | 0.12206
2025-01-11T06:47:33 | 10000001101000 | 1 | 0 | 49 | 55 | -4 | 25 | 45 | 18 | 219 | 14 | 58 | 0.94 | 7.09 | 22310 | 1298 | 17.6 | 36.6 | 56 | 610 | 0.0657 | 6 | 0.10575
2025-01-11T06:48:33 | 10000001101000 | 1 | 0 | 49 | 56 | -4 | 25 | 45 | 22 | 218 | 14 | 58 | 0.92 | 8.14 | 22310 | 1298 | 17.6 | 36.6 | 65 | 610 | 0.079933 | 7 | 0.12075
2025-01-11T06:49:33 | 10000001101000 | 1 | 0 | 49 | 58 | -4 | 25 | 45 | 19 | 220 | 14 | 58 | 0.93 | 9.53 | 22310 | 1298 | 17.7 | 36.5 | 60 | 610 | 0.069667 | 9 | 0.15694
2025-01-11T06:50:33 | 10000001101000 | 1 | 0 | 49 | 56 | -4 | 25 | 45 | 16 | 221 | 14 | 58 | 0.94 | 7.09 | 22310 | 1298 | 17.7 | 36.6 | 51 | 610 | 0.058933 | 7 | 0.12337
2025-01-11T06:51:33 | 10000001101000 | 1 | 0 | 49 | 56 | -4 | 25 | 45 | 18 | 220 | 14 | 58 | 0.96 | 7.44 | 22310 | 1299 | 17.6 | 36.6 | 55 | 610 | 0.066 | 7 | 0.126
2025-01-11T06:52:33 | 10000001101000 | 1 | 0 | 49 | 57 | -4 | 25 | 45 | 22 | 219 | 14 | 58 | 0.93 | 8.6 | 22310 | 1299 | 17.7 | 36.6 | 65 | 610 | 0.0803 | 8 | 0.1395
2025-01-11T06:53:33 | 1010000001101000 | 1 | 0 | 49 | 51 | -4 | 25 | 45 | 4 | 224 | 14 | 58 | 0.94 | 3.95 | 22310 | 1299 | 17.7 | 36.6 | 29 | 480 | 0.014933 | 2 | 0.03525
2025-01-11T06:54:33 | 1010000001101000 | 1 | 0 | 48 | 45 | -3 | 25 | 45 | 2 | 226 | 14 | 58 | 1.41 | 3.95 | 22310 | 1299 | 17.7 | 36.6 | 35 | 0 | 0.0075333 | -3 | -0.079312
2025-01-11T06:55:33 | 1010000001101000 | 1 | 0 | 45 | 37 | -2 | 25 | 45 | 2 | 226 | 14 | 58 | 1.43 | 3.95 | 22310 | 1299 | 17.7 | 36.5 | 37 | 0 | 0.0075333 | -8 | -0.2145
2025-01-11T06:56:33 | 1010000001101000 | 1 | 0 | 40 | 27 | -1 | 25 | 45 | 6 | 224 | 14 | 58 | 1.44 | 3.95 | 22310 | 1299 | 17.7 | 36.5 | 37 | 0 | 0.0224 | -13 | -0.351
2025-01-11T06:57:33 | 10000001101000 | 1 | 0 | 35 | 33 | 1 | 25 | 45 | 5 | 224 | 14 | 58 | 1.45 | 3.95 | 22310 | 1299 | 17.7 | 36.5 | 29 | 370 | 0.018667 | -2 | -0.054375
2025-01-11T06:58:33 | 10000001101000 | 1 | 0 | 36 | 38 | 1 | 25 | 45 | 9 | 224 | 14 | 58 | 1.43 | 3.95 | 22310 | 1299 | 17.7 | 36.4 | 41 | 550 | 0.0336 | 2 | 0.053625
2025-01-11T06:59:33 | 10000001101000 | 1 | 0 | 36 | 40 | 0 | 25 | 45 | 14 | 222 | 14 | 58 | 1.43 | 3.95 | 22310 | 1299 | 17.7 | 36.4 | 55 | 550 | 0.0518 | 4 | 0.10725
|  |  |  | 46.1667 | 51.2333 |  |  |  | 17.2167 | 220.3667 |  |  | 1.1713 |  | 4 | 7 |  |  |  |  | 4.4769 |  | 6.6766 | 1.4913
These are the Midea
rounded 'running totals', end of hour minus start of hour provides a sanity check on the calculated values
Mean values for the hour for variables shown
The calculated values in row 62
are the values that apear in the
hour data file (calculated by a
python script). The other minute
rows are the minute values,
normally bever seen but added here for interest's sake. Sums aren't identical to calculated value due to rounding errors. Note how during defrosts the energy out goes negative, relecting the fact energy is flowing the 'wrong way'. Also note that strictly speaking these values are kW (power) for each minute but when summed over the hour they become energy (kWh), 4.48kW for one hour is 4.48kWh etc
60m
trailing
COP