## Overvoltage
| GRID DATA |  |  | Givenergy | Solaredge |  | INVERTER DATA |  | Octopus |  | NOTES
DATE | MAX VOLTAGE | NUMBER OF EVENTS OVER 253V | TOTAL DAILY RECORDS | TOTAL SOLAR PROD. Kw | TOTAL SOLAR PROD. Kw | ratio GE/SE | MAX VOLTAGE | Time of peak voltage. within 15 mins grid /inverter | 30-min export periods ≥2.7 kWh | Diff between Grid & inverter peak voltage |  | Peak solar prod around midday to 1pm
21.5.26 | 252.7 | 0 | 407 | 34.3 | 11.3 | 3.0354 | 258.6 | 17.13 | 2 | 5.9
22.5.26 | 254 | 4 | 420 | 38.3 | 11.5 | 3.3304 | 260.1 | 16.02 | 9 | 6.1
23.5.26 | 254.4 | 27 | 358 | 28.52 | 10.9 | 2.6165 | 260.7 | 16.11 | 7 | 6.3 |  | Overvoltage events 11.00-16.00
24.5.26 | 255 | 32 | 279 | 34.18 | 11.3 | 3.0248 | 260.4 | 16.06 | 6 | 5.4 |  | Overvoltage events 13.00-17.00
25.5.26 | 253.9 | 5 | 279 | 37.9 | 11.1 | 3.4144 | 260 | 16.5 | 7 | 6.1
26.5.26 | 253.2 | 2 | 380 | 35.7 | 10.2 | 3.5 | 259.2 | 16.55 | n | 6
27.5.26 | 252.9 | 0 | 283 | 38 | 10.9 | 3.4862 | 258.3 | 16.04 | n | 5.4
28.5.26 | 254.2 | 4 | 281 | 28.87 | 8.54 | 3.3806 | 260.2 | 16.49 | 6 | 6
29.5.26 | 254.4 | 13 | 289 | 20.1 | 9.06 | 2.2185 | 260.6 | 14.42 | n | 6.2
30.5.26 | 254.8 | 59 | 435 | 29.9 | 11.1 | 2.6937 | 260.5 | 16.03 | n | 5.7 |  | Overvoltage events 13.00-16.30
31.5.26 | 253.2 | 2 | 347 | 22.89 | 7.29 | 3.1399 | 259.4 | 16.12 | n | 6.2
1.6.26 | 248.8 | 0 | 268 | 13.5 | 3.43 | 3.9359 | 255 | 8.38 | n | 6.2
2.6.26 | 254.3 | 6 | 363 | 24.1 | 7.08 | 3.404 | 260.1 | 11.08 | n | 5.8
3.6.26 | 254 | 29 | 409 | 12.96/OFF | 4.44/off | 2.92 | 260.1 | 12.46 | n | 6.1 | solar off | SSE grid recorder installed 14.30. Overvoltage events 11.00-13.30
4.6.26 | 248.4 | 0 | 334 | OFF | off |  | 252.9 | 13.21 | n | 4.5 | solar off | SSE grid recorder
5.6.26 | 249.2 | 0 | 290 | OFF | off |  | 253.5 | 11.25 | n | 4.3 | solar off | SSE grid recorder
6.6.26 | 248.9 | 0 | 321 | 12 | 3.04 | 3.9474 | 254 | 8.38 | n | 5.1 |  | SSE grid recorder
7.6.26 | 251.1 | 0 | 371 | 20.9 | 6.2 | 3.371 | 256.4 | 15.25 | n | 5.3 |  | SSE grid recorder
8.6.26 | 254.6 | 37 | 590 | 28 | 10.1 | 2.7723 | 260.4 | 12.12 | 8 | 5.8 |  | SSE grid recorder removed 10.00. Overvoltage events 12.00-15.00
0
9.6.26 | 251.5 | 0 | 349 | 28.6 | 7.59 | 3.7681 | 257.5 | 10.47 | 2 | 6 | phase changed around 10.00am
10.6.26 | 250.2 | 0 | 342 | 28 | 8.04 | 3.4826 | 256 | 11.27 | 2 | 5.8
11.6.26 | 250 | 0 | 362 | 17.3 | 4.95 | 3.4949 | 255.2 | 13.07 | n | 5.2
12.6.26 | 249.4 | 0 | 298 | 22 | 7.26 | 3.0303 | 255 | 12.26 | n | 5.6
13.6.26 | 251.9 | 0 | 574 | 40.1 | 11.8 | 3.3983 | 257.9 | 16.02 | 7 | 6
14.6.26 | 250.2 | 0 | 371 | 35.9 | 10.4 | 3.4519 | 256 | 3.47 | 10 | 5.8
15.6.26 | 249.8 | 0 | 507 | 35.3 | 10 | 3.53 | 255.6 | 13 | 4 | 5.8
16.6.26 | 250.9 | 0 | 359 | 24.7 | 7.55 | 3.2715 | 256.9 | 13.16 | 4 | 6
17.6.26 | 251.1 | 0 | 442 | 21.5 | 6.05 | 3.5537 | 257.2 | 18.38 | n | 6.1
18.6.26 | 251.8 | 0 | 363 | 29.4 | 9.91 | 2.9667 | 257.1 | 13.2 | 5 | 5.3
19.6.26 | 252.3 | 0 | 304 | 38.3 | 10.8 | 3.5463 | 258.3 | 16.06 | 9 | 6 |  | a few clouds around midday for 1 hour or so
20.6.26 | 252.2 | 0 | 270 | 26.6 | 8.34 | 3.1894 | 258.3 | 15.1 | 4 | 6.1 |  | mixed cloud+sun all day
21.6.26 | 252.4 | 0 | 277 | 35.9 | 10 | 3.59 | 258.6 | 14.04 | 6 | 6.2 |  | mostly sun with high cloud
22.6.26 | 252.5 | 0 | 278 | 33.2 | 8.85 | 3.7514 | 258.7 | 14.34 | 7 | 6.2 |  | mostly sun with some high cloud. Mid/late afternoon clouds
23.6.26 | 250.5 | 0 | 282 | 36.7 | 10.7 | 3.4299 | 255.8 | 9.56 | 9 | 5.3 |  | mostly sun. Very hot 32deg
24.6.26 | 251.3 | 0 | 314 | 36.6 | 10.3 | 3.5534 | 257.3 | 10.26 | 9 | 6 |  | mostly sun. Very hot 36deg
25.6.26 | 251.9 | 0 | 272 | 37.8 | 10.5 | 3.6 | 258 | 12.26 | 7 | 6.1 |  | mostly sun. Very hot 36deg
26.6.26 | 253.4 | 1 | 316 | 38.4 | 10.5 | 3.6571 | 259.4 | 14.11 | 6 | 6 |  | Mostly sunny, hot 30°C
27.6.26 | 254 | 1 | 315 | 29 | 9.24 | 3.1385 | 258.7 | 13.41 | n | 4.7 |  | sun with some clouds. Very warm 26deg
28.6.26 | 253.2 | 2 | 268 | 31.1 | 9.71 | 3.2029 | 259.2 | 14.25 | 2 | 6 |  | part sun with some clouds. warm 23deg
29.6.26 | 250.2 | 0 | 284 | 21.9 | 5.87 | 3.7308 | 256.2 | 15.4 | 1 | 6 |  | mostly cloud 21deg
30.6.26 | 253.6 | 2 | 287 | 27.3 | 8.29 | 3.2931 | 259.4 | 13.04 | n | 5.8 |  | part sun with some clouds. 21deg
1.7.26 | 254.3 | 3 | 288 | 34 | 10.1 | 3.3663 | 260.3 | 16.3 | 6 | 6 |  | mostly sun. some clouds. 21deg
2.7.26 | 253.4 | 1 | 291 | 35.9 | 11.4 | 3.1491 | 259.3 | 14.03 | 3 | 5.9 |  | mostly sun. 23 deg
3.7.26 | 254.1 | 12 | 326 | 37.7 | 10.9 | 3.4587 | 260.1 | 14.38 | 7 | 6 |  | mostly sun 24deg
4.7.26 | 254 | 53 | 356 | 28.2 | 9.79 | 2.8805 | 260 | 13.52 | n | 6 |  | part cloud am. Mostly sun pm 24deg
5.7.26 | 253.9 | 25 | 392 | 32.9 | 10.6 | 3.1038 | 259.9 | 13.31 | 4 | 6 |  | part cloud am. Mostly sun pm 25deg
6.7.26 | 251.4 | 0 | 420 | 36.7 | 10.6 | 3.4623 | 257.4 | 14.31 | 2 | 6 |  | part cloud am. Mostly sun pm 29deg
7.7.26 | 251.2 | 0 | 478 | 36.7 | 10.9 | 3.367 | 257.3 | 16.26 | 1 | 6.1 |  | part cloud am. Mostly sun pm 28deg
8.7.26 | 251.5 | 0 | 436 | 37.1 | 10.6 | 3.5 | 257.4 | 15.25 | 7 | 5.9 |  | mostly sun 30deg
9.7.26 | 250.9 | 0 | 531 | 36.3 | 10.7 | 3.3925 | 257 | 16.3 | 10 | 6.1 |  | mostly sun 32deg
10.7.26 | 249.7 | 0 | 303 | 31.3 | 8.38 | 3.7351 | 255.9 | 15.04 |  | 6.2 |  | mostly sun + haze 33deg
11.7.26 | [9 empty] | 0 |  | mostly sun + haze 33deg
12.7.26 | [9 empty] | 0
13.7.26 | [9 empty] | 0
14.7.26 | [9 empty] | 0
15.7.26 | [9 empty] | 0
16.7.26 | [9 empty] | 0
17.7.26 | [9 empty] | 0
18.7.26 | [9 empty] | 0
Other observations:
no sign of undervoltage events even with high draw. Ocasionally 230v, mostly 236v+
Night draw might include 7kw EV, 2.5kw battery, 3kw+ ASHP etc
Note
Forced discharge of batteries mean likely discharge near 6kw for sustained periods on sunny days
Not all overvoltage events lead to inverter reset.

## Undervoltage
| GRID DATA |  |  |  | GRID DATA |  | NOTES
DATE | MAX VOLTAGE | Time of peak voltage. | No OF EVENTS OVER 253V/ under 216v | TOTAL DAILY RECORDS | MIN VOLTAGE | Time of min voltage.
2.1.26 | 244.2 | 20.17 |  | 562 | 231.4 | 9.12 | This was the coldest sustained spell of the winter around Yeovilton. Daytime temperatures were generally only 3–8°C, with overnight minima falling to around -7 to -8°C on several days.
3.1.26 | 244.4 | 13.09 |  | 492 | 227 | 7.47
4.1.26 | 245.2 | 11.28 |  | 709 | 225.6 | 10.17
5.1.26 | 243.6 | 22.44 |  | 284 | 230.7 | 8.54
6.1.26 | 243.3 | 11.47 |  | 347 | 227.8 | 10.03
7.1.26 | 244.5 | 10.48 |  | 295 | 224.7 | 16.2
8.1.26 | 244.4 | 21.19 |  | 844 | 231.8 | 14.44
13.2.26 | 246 | 13.13 |  | 282 | 230.5 | 9.12 | Another relatively cold spell, with daytime highs typically around 6–8°C and colder nights before temperatures became milder later in the month.
14.2.26 | 247.3 | 12.38 |  | 281 | 229.1 | 3.09
15.2.26 | 244.8 | 14.56 |  | 282 | 235.2 | 17.17
16.2.26 | 244.6 | 21.27 |  | 283 | 230.2 | 8.27
17.2.26 | 244.7 | 23.17 |  | 281 | 225.7 | 16.15
18.2.26 | 243.2 | 5.55 |  | 281 | 224.7 | 10.52
19.2.26 | 243.1 | 22.1 |  | 279 | 230.3 | 18.09