## introduction
|  | Tel: | 02380 274833 | This tool has been written to conform to MIS3005 v4.3 and v5.0
|  | E-mail: | sales@freedomhp.co.uk | september 20 2017
|  | Web Address | www.freedomhp.co.uk | http://www.microgenerationcertification.org/mcs-standards/installer-standards
Welcome to the Freedom Heat pumps heat load estimation, system selection and radiator selector sheet
to use this excel first enter the property details into the data entry sheet, only fill in the orange cells
to comply with MCS regulations you must use design conditions stated in the heat load sheet
these will automatically be selected when you state where the property is in the country. Choose from the drop down list
you have to calculate the loss on a room by room basis, the calculator only needs to know the length of any external walls
it will work out the area of the walls for you.
you must enter the floor and ceiling areas and the area of the window in the room as well.
to speed up the process you can enter the building construction details at the top of the sheet and select as above for each room
Note if you are doing a ground floor room and you select an internal ceiling it will assume there is not heat loss to upstairs.
the same is true with the floor on the first floor rooms.
next choose the ventilation loss, again the calculator will use the mcs figures when you select from the drop dowlist
once the rooms heat loss is complete choose wheteher you want to use rads or ufh to heat it. If you put in a radiator size the
calculator will tell you wheteher it is undersized or not, it will also recommend a radiator from the myson range which will do the job
and it will recommend a heat output so you can size the rad yourself in line with the mcs heat emitter guide.
Now repeat for the next room
once every room has been completed you can see the total load at the top of the sheet and the total heated area.
To choose your heat pump go to the Equipment tab and look at the graph.
The house heat load is shown on the graph using the black line, you must choose a unit in which the output line is above the black line at all times
If you know your heat load already you can input the figure manually and you can also provide a SAP figure (Box 39) and the calculator with give you the heat load requirement in kW
use the drop downs to select a unit and wheter or not you want a hybrid system, the system must provide at least 100% of the heating requirement (Plus the hot water requirement) to qualify for MCS.
The run costs will be generated in the "MCS calc and run costs" sheet
enter the current heating system type and the new one you want to use, it will work out the run costs, savings and the co2 and the saving for you
The "Performance estimate" sheet will fill in automatically as you go, it lists the heating system you have chosen, run costs
any RHI and lists every radiator that needs changing.
Noise test can be used to determine whether the unit needs planning permission or not, fill in the orange boxes and the calculator will say if you pass or fail
version information
2014-04-07
v19, added mcs compliance certificate
v19.1 modification to rhi calculator on mcs run cost sheet
2014-04-11
v 20 added spf sheet to calculator to prove spfs of over 2.5
v 20 added rhi disclaimer now rhi launched, to run cost sheet
2014-05-12
v20.1 added split calulations to calculator
v20.1 added volume calculation to rads in heat loss sheet
v20.2 add links to mcs web page for units
v20.2 hide spf calculator
v20.2 add 7 day legionella option
v20.2 extra pump run cost function in run costs and calcs corrected to £s/yr
v20.3 deleted option for secondary glazing from top section of the heat loss calculator so reduction in u value cant be done twice
v20.4 MCS numbers inserted & links given.
v20.5 changed calculation for more than 3 pumps, error found in maths
v20.5 changed direct debit information to work with hybrids and non hybrids
v20.5 changed heat loss sheet so radiators default to 0 if UFH selected
v20.5 changed Summary sheet to say no to radiator changes if hybrid chosen
v20.5 new samsung logo
v20.5 simplify heat loss calculator
v20.6 mcs compliance sheet now lists exact unit in mcs number
v20.6 we now increase load in high ceiling areas by up to 6% at 8m
v20.6 set default of secondary glazing to no and changed formula in c13 to suit
v20.7 added rad sizes to summary sheet and parts required
v21.1 changed print size for compliance sheet
v21.1 modified radiator temperature calc in all rooms after room 1
v21.1 peak heat output figures inserted on graphs
v21.1 added peak values of the graphs
v21.2 error in total floor area found and removed
v22 changed round the calulations, added rad uplift factor, added new rad sizing tool and myson catalogue
v22 added star rating, simplified run cost calcs
v22 moved secondary glazing to the window type
v22 moved hp selector to graph page and added manaul hp selector
v22.1 modification to selected radiator size to suit myson sheet
v22.1 corrected selection of glasgow and edinburgh
v22.2 corrected mcs number
v22.3 further revision to rads see 22.1
v22.4 added 12s to graphs
v22.4 degree days modified to new figures
v22.4 added solar pv data
v22.4 changed compliance air temp to 21
v22.4 solar maths added
v22.5 adjusted run costs in hybrid mode to show average heating cost per kwHr
v23 changed ref to mcs v4.1 21/2/15
v23.1 allowed more choice of old and new boiler in mcs run cost page
v23.2 hide all the maths in the mcs run cost calc
v23.2 add mcs performance estimate to sheet
v24 changed pv figure to value per kw of pv installed
v24 added the new MCS performance estimate sheet
v24 commercial rhi deleted from heat load calculation
v24.1 add jersey data and add a box to change the electricity price to the run costs
v24.2 added formatting to every room to show tick and cross, updated rhi to 7.42p/kwhr
v24.2 added added the jersey maths which didn’t work
v 24.2 nat gas and hp maths stopped working on run cost now fixed
v 30 new gen 4 units added
v30 new sound checker added for gen 4
v 30 check maths of the performance estimate
v30 add mcs numbers to excel
v30 new capacity data added
v30 added 12kW x 2 data
v30.1 adjusted the co2 maths for an error in hybrid mode
v30.2 change ref to v3.4 of mcs
v30.3 changed air calc to suit adjusted psychometrics.
v40 new calulator now hav vaillant, eco forest, full scop data and pool calulator included
v40.1 add scop make it visible add ground coil sizing.
v40.3 changed vent losses, add gshp loop pricing
v40.3 Freedom1 and add slinkys
v41.0 add pricing and manual heat loss tools to equipment tab
v41.0 splits prices into labour and kit in ground loop and sorts out cylinder sizing in mutiple systems
v41.1 Modifications to MCS maths for hot water
v41.2 New cylinder recovery calc including immersions and cost
v41.3 Calculated oversize factors to account for hot water demands
v42 Aesthetics
v43 Added more functionality for pricing in equipment tab
v44 revised maths for the vent loss as it was giving a high reading now matches sap
v44.1 Made changes to the equipment tabs pricing functions. Also put in a discliamer on both the MCS calcs tab AND the ground loop tab
v44.2 Increased boiler takeover temp on hybrids
v44.3 Revised run costs fuel prices and ground loop size for slinks
v44.4 Revamped Ground loop calculations
v44.5 Automated Cylinder's coil size based on Gledhill data for HP Cylinders and Tidied up a load of the back math for the pricing on the equipment page
v46 Data entry sheet, tidies up heat loss calculator tab.
v46 Added UFH covers option for room by rooms
v46 Revamped performance estimate to show UFH covers etc
v46 Automated almost all of MCS compliance sheet
v46 Added Clausius units to equipment tab and linked maths for the rest of the excel
v46.1 Changed cylinder selection to suite Telford Spec for cylinder sizes and coil sizes
v46.2 remeved "classic and elite" options for clausius units at Graham's request
v46.2 Added 7-50kW Clausius Strong unit to equipment and sebsequent math
v46.3 Added 12kW heat pump
v46.3 Added figures for new RHI (Spring 2017)
v46.4 House heat load line on equipment graph now tracks the MCS ambient temperature
v46.4 Sorted out rad sizing math
v46.5 Slight changes to Spring 2017 RHI maths
v46.5 Revamped Hybrid run cost math
v46.6 Added fuction for working out heat loss from EPC figures
v50 - Updated for MIS3005v5
v50 - Added full hitachi range
v50 - Changed formatting on unit selection graph to show only the selected unit and auto sclaes axis to fit
v50.1 - Updated Fuel cost prices
v 50.2 | new rhi rules added

## Data Entry Sheet
| Data Entry Sheet |  | Version 50.2 |  |  | 2017-09-20 |  |  | Reference data table
Window U values
| Project info | [7 empty] | From Data Entry | 2.8
| Project | 26 Church Lane | [6 empty] | Single glazed metal | 5.8
| Installer | Egensys Ltd | [6 empty] | Single glazed wood/plastic | 4.8
| Reference | H17.176 | [6 empty] | Double glazed metal | 4.2
[9 empty] | solid wood door | 3
| General Information | [7 empty] | secondary glazing | 3
| Name of the owner | [7 empty] | Double glazed wood/plastic | 2.8
| Address of the owner | [7 empty] | Building regs Part L | 2.2
| Address at which the heating system is installed, if different to above | [7 empty] | code 3, 2011 | 2
| MCS certification number of installation company | NIC5717 | [6 empty] | extension | 2
| Name of MCS installation company | Egensys Ltd | [6 empty] | code 4, 2013 | 1.2
| Address of MCS installation company | Enterprise Business Centre, Carlton Road, Worksop, S81 7QF | [6 empty] | code 5 and 6, 2016 | 0.7
| Commissioning date of the installation | [7 empty] | custom
Contact details
Customer E-mail address
Customer Telephone
Customer Mobile
| Other (please state) | [7 empty] | Wall U-values
[9 empty] | From Data Entry | 2.11
[9 empty] | internal no loss | -0.15
[9 empty] | concrete 150mm plaster | 3.12
[9 empty] | brick 100mm | 2.97
| Geographics |  |  |  | System Selection |  |  |  | stone 300mm | 2.78
| location | Birmingham |  |  | Heating Design water flow temp C |  | 50 | °C | stone 450mm | 2.23
| MCS Ambient temp | -3.4 |  | °C | Radiator Uplift Factor |  | 2.4 |  | brick 228mm | 2.11
| MCS Ground temp | 9.8 |  | °C | Star Rating |  | *** |  | plasterboard studding plasterboard | 1.72
| height above sea level | 100 |  |  | System Type |  | Heating and Hot Water |  | stone 600mm | 1.68
| Corrected Amb temp | -4 |  | °C | ambient temp the boiler begins heating? |  | not a hybrid |  | brick 343mm | 1.64
| Corrected Gnd temp | 9.2 |  | °C | If Hybrid (Which other heating appliance is present? |  | Not a hybrid |  | plaster concrete block plaster | 1.58
[9 empty] | plaster block cavity block plaster | 1.02
[9 empty] | brick cavity block plaster | 0.77
[9 empty] | brick cavity thermal block plaster | 0.59
| Water Cylinder Selection | [7 empty] | brick cavity brick plaster | 0.56
| Is solar thermal being installed | No | [6 empty] | celotex 50mm | 0.44
| number of bedrooms | 3 | [6 empty] | brick cavity filled block plaster | 0.42
| number of people in the house | 4 | [6 empty] | brick cavity filled thermal block plaster | 0.36
| recommended tank size | 220 |  | Litres |  |  |  |  | Building regs part L | 0.35
| tank size available choose from list | 170LTR |  | Litres |  |  |  |  | renovation and extension | 0.35
| Hot water cylinder temperature | 50 |  | °C | 50C is the standard setting but up to 60 can be selected for HT units |  |  |  | code 3, 2011 | 0.25
[9 empty] | celotex 100mm | 0.22
[9 empty] | code 4, 2013 | 0.2
[9 empty] | code 5 and 6, 2016 | 0.15
| Building Details | Material |  |  | U-value |  |  |  | celotex 200mm | 0.11
| External Wall type | brick 228mm |  |  | 2.11 |  |  |  | celotex 300mm | 0.073
| Window type | Double glazed wood/plastic |  |  | 2.8 |  |  |  | custom
| Roof / Ceiling type | Pitched felt 200mm insulation regs Part L |  |  | 0.2
| Floor type | concrete floor no insulation |  |  | 1
if your house is built of more than one material its possible to enter this data for each room in heat loss tab
Floor U-values
All heat loads are calculated using the figures provided by the customer, All calculations are based on information supplied, it is your responsibility to check these figures are correct. | [8 empty] | From Data Entry | 1
Freedom Heat pumps take no responsibility for this calculation, it should be used as a guideline only | [8 empty] | internal no loss | -0.15
This calculator is based on EN12831 and MCS guidelines in MIS3005 v4.3, 16/9/2015 | [8 empty] | concrete floor 200mm to outside | 1.82
All recommended radiator sizes are based on Myson Select Compact range 2014 see myson tab for details | [8 empty] | wood, airgap, board to outside | 1.75
Notes: | [8 empty] | suspended wood | 1.1
Insert notes here: | [8 empty] | concrete floor no insulation | 1
[9 empty] | suspended wood with 50mm insulation | 0.45
[9 empty] | celotex 50mm | 0.44
[9 empty] | concrete floor 50mm insulation | 0.41
[9 empty] | wood 100mm insulation board to outside | 0.33
[9 empty] | concrete floor 100mm insulation | 0.26
[9 empty] | suspended wood with 100mm insualtion | 0.26
[9 empty] | Building regs Part L | 0.25
[9 empty] | renovation | 0.25
[9 empty] | extension | 0.25
[9 empty] | code 3, 2011 | 0.22
[9 empty] | celotex 100mm | 0.22
[9 empty] | code 4, 2013 | 0.2
[9 empty] | code 5 and 6, 2016 | 0.15
[9 empty] | celotex 200mm | 0.11
[9 empty] | celotex 300mm | 0.073
custom
Yes
No
Roof U-values
[9 empty] | From Data Entry | 0.2
[9 empty] | internal | -0.15
[9 empty] | Double glazed glass UPVC | 2.8
[9 empty] | Plasterboard 8 inch cavity T&G boards | 1.7
[9 empty] | Flat 50mm insulation | 0.54
[9 empty] | Pitched no felt 100mm insulation | 0.44
[9 empty] | celotex 50mm | 0.44
[9 empty] | Pitched w felt and 100mm insulation | 0.35
[9 empty] | Flat 100mm insulation | 0.32
[9 empty] | renovation extension flat | 0.25
[9 empty] | celotex 100mm | 0.22
[9 empty] | Pitched felt 200mm insulation regs Part L | 0.2
[9 empty] | code 3, 2011 | 0.19
[9 empty] | renovation extension pitched | 0.19
[9 empty] | thatch | 0.17
[9 empty] | code 4, 2013 | 0.16
[9 empty] | code 5 and 6, 2016 | 0.13
[9 empty] | celotex 200mm | 0.11
[9 empty] | celotex 300mm | 0.073
custom
[9 empty] | design ambient temperatures | air temp | gnd temp | altitude m
[9 empty] | Plymouth | -0.2 | 11 | 27
[9 empty] | Belfast | -1.2 | 10.5 | 68
[9 empty] | Cardiff | -1.6 | 9.9 | 67
[9 empty] | London | -1.8 | 10.2 | 25
[9 empty] | Manchester | -2.2 | 10 | 75
[9 empty] | Birmingham | -3.4 | 9.8 | 96
[9 empty] | Edinburgh | -3.4 | 8.5 | 35
[9 empty] | Glasgow | -3.9 | 8.5 | 5
[9 empty] | Jersey | -0.2 | 11 | 0
[9 empty] | Ventilation rate | AC/hr
[9 empty] | From Data Entry | #REF!
[9 empty] | Heat recovery 66% efficent | 0.2
[9 empty] | Code 4 or higher | 0.58
[9 empty] | Code 3 or higher | 0.7
[9 empty] | Living rooms/Hallways | 1.5
[9 empty] | Dining rooms | 1.5
[9 empty] | Bedroom | 1
[9 empty] | Kitchen | 2
[9 empty] | Bathroom | 2
[9 empty] | Toilet | 2
Custom
[9 empty] | flow temperature | uplift factor | spf | Star rating
[9 empty] | 35 | 6.8 | 3.6 | ******
[9 empty] | 40 | 4.3 | 3.4 | *****
[9 empty] | 45 | 3.1 | 3 | ****
[9 empty] | 50 | 2.4 | 2.7 | ***
[9 empty] | 55 | 1.9 | 2.4 | **
[9 empty] | 60 | 1.4 | 2.1 | *
[9 empty] | 65 | 1.2 | n/a | Zero
Not a hybrid
Standard boiler
Condensing boiler
Combi Boiler
Back boiler
High or Unknown Thermal Capacity boiler
Wall or flue mounted boiler (balanced on open flue) - Pre 1998
Combined Primary Source Units (CPSU)
Open fire with back boiler
Closed room heater (stove) with back boiler
Range cooker boiler (integral oven and boiler)
Community Heating
Storage heaters
Warm air system
Heat pump
Fire or wall heater
Electric panel convector or Radiant heaters
Electric underfloor /ceiling heating
Default-portable electric heaters)
Other
Note on D27: the design temperatures are set in MCS, this design temperature is altered 0.6C for every 100m above sea level.
Note on I28: We recommend a heating design temperature of 45°C for UFH and 50°C for radiators to keep the radiator size manageable.

## Heat Loss Calculator
Heat loss In accordance with EN12831 |  |  | Results |  |  |  | Reference data table
|  |  | Total Heat loss |  | 6462.9998 | W | Window U values
|  |  | heated floor area |  | 81.7 | m^2 | From Data Entry | 2.8
[7 empty] | Single glazed metal | 5.8
Room Name | [6 empty] | Single glazed wood/plastic | 4.8
| Kitchen | [5 empty] | Double glazed metal | 4.2
Desired Room Temperature C | 18 | U Values | Results |  | Total Heat Loss |  | solid wood door | 3
Average Ceiling Height m | 2.4 | [5 empty] | secondary glazing | 3
Total length Of All External Walls m | 7.2 | [5 empty] | Double glazed wood/plastic | 2.8
External Wall Type | brick cavity filled block plaster | 0.42 | 169.0392 | W | 997.8503 |  | Building regs Part L | 2.2
Total Window Area m^2 | 3.8 |  |  |  | heat loss W/m^2 |  | code 3, 2011 | 2
Window Type | From Data Entry | 2.8 | 246.62 | W | 76.7577 |  | extension | 2
External Roof Area * m^2 | 0 |  |  |  | System Volume |  | code 4, 2013 | 1.2
Roof light Area m^2 | 0 |  |  |  | 0 | litres | code 5 and 6, 2016 | 0.7
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W |  |  | custom
Floor Area m^2 | 13
Floor Construction | From Data Entry | 1 | 131.56 | W
Ventilation loss Air change/hr | Kitchen | 2 | 453.024 | W
Heat Emitters | [6 empty] | Wall U-values
[7 empty] | From Data Entry | 2.11
Emitter Type | UFH Covering type | UFH Pipe Centre |  |  |  |  | internal no loss | -0.15
Radiators | Tiles | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return) |  | concrete 150mm plaster | 3.12
[7 empty] | brick 100mm | 2.97
[5 empty] | amb temp rad is sized |  | stone 300mm | 2.78
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize |  |  | stone 450mm | 2.23
0 | 0 | DP+type21 | 0 | -100% | 18 | C | brick 228mm | 2.11
|  |  |  | delta t |  |  | plasterboard studding plasterboard | 1.72
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 2394.8407 | W | stone 600mm | 1.68
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load. | [6 empty] | brick 343mm | 1.64
[7 empty] | plaster concrete block plaster | 1.58
Myson Radiator Height mm | Myson Radiator width mm | Radiator type |  |  |  |  | plaster block cavity block plaster | 1.02
0 | #DIV/0! | DC type 22 |  |  |  |  | brick cavity block plaster | 0.77
[7 empty] | brick cavity thermal block plaster | 0.59
[7 empty] | brick cavity brick plaster | 0.56
Room Name | [6 empty] | celotex 50mm | 0.44
| WC | [5 empty] | brick cavity filled block plaster | 0.42
Desired Room Temperature C | 18 | U Values | Results |  | Total Heat Loss |  | brick cavity filled thermal block plaster | 0.36
Average Ceiling Height m | 2.4 | [5 empty] | Building regs part L | 0.35
Total length Of All External Walls m | 4.2 | [5 empty] | renovation and extension | 0.35
External Wall Type | brick cavity filled block plaster | 0.42 | 111.3552 | W | 381.6823 |  | code 3, 2011 | 0.25
Total Window Area m^2 | 1.2 |  |  |  | heat loss W/m^2 |  | celotex 100mm | 0.22
Window Type | From Data Entry | 2.8 | 77.88 | W | 88.7633 |  | code 4, 2013 | 0.2
External Roof Area * m^2 | 0 |  |  |  | System Volume |  | code 5 and 6, 2016 | 0.15
Roof light Area m^2 | 0 |  |  |  | 2.19 | litres | celotex 200mm | 0.11
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W |  |  | celotex 300mm | 0.073
Floor Area m^2 | 4.3 | [5 empty] | custom
Floor Construction | From Data Entry | 1 | 43.516 | W
Ventilation loss Air change/hr | Toilet | 2 | 149.8464 | W
Floor U-values
Heat Emitters | [6 empty] | From Data Entry | 1
[7 empty] | internal no loss | -0.15
Emitter Type | UFH Covering type | UFH Pipe Centre |  |  |  |  | concrete floor 200mm to outside | 1.82
Radiators | Tiles | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return) |  | wood, airgap, board to outside | 1.75
[7 empty] | suspended wood | 1.1
[7 empty] | concrete floor no insulation | 1
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize | amb temp rad is sized |  | suspended wood with 50mm insulation | 0.45
500 | 600 | SC_type11 | 250.6875 | -34.32% | 3.5505 | C | celotex 50mm | 0.44
|  |  |  | delta t |  |  | concrete floor 50mm insulation | 0.41
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 916.0375 | W | wood 100mm insulation board to outside | 0.33
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load. | [6 empty] | concrete floor 100mm insulation | 0.26
[7 empty] | suspended wood with 100mm insualtion | 0.26
Myson Radiator Height mm | Myson Radiator width mm | Radiator type |  |  |  |  | Building regs Part L | 0.25
500 | 503.6272 | DC type 22 |  |  |  |  | renovation | 0.25
[7 empty] | extension | 0.25
[7 empty] | code 3, 2011 | 0.22
Room Name | [6 empty] | celotex 100mm | 0.22
| Lounge | [5 empty] | code 4, 2013 | 0.2
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss |  | code 5 and 6, 2016 | 0.15
Average Ceiling Height m | 2.4 | [5 empty] | celotex 200mm | 0.11
Total length Of All External Walls m | 4.3 | [5 empty] | celotex 300mm | 0.073
External Wall Type | From Data Entry | 2.11 | 503.98 | W | 1123.7751 |  | custom
Total Window Area m^2 | 1.4 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 103.25 | W | 93.6479 |  | Yes
External Roof Area * m^2 | 0 |  |  |  | System Volume |  | No
Roof light Area m^2 | 0 |  |  |  | 7.83 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W |  |  | Roof U-values
Floor Area m^2 | 12 | [5 empty] | From Data Entry | 0.2
Floor Construction | From Data Entry | 1 | 162.84 | W |  |  | internal | -0.15
[7 empty] | Double glazed glass UPVC | 2.8
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 356.4 | W |  |  | Plasterboard 8 inch cavity T&G boards | 1.7
[7 empty] | Flat 50mm insulation | 0.54
Heat Emitters | [6 empty] | Pitched no felt 100mm insulation | 0.44
[7 empty] | celotex 50mm | 0.44
Emitter Type | UFH Covering type | UFH Pipe Centre |  |  |  |  | Pitched w felt and 100mm insulation | 0.35
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return) |  | Flat 100mm insulation | 0.32
[7 empty] | renovation extension flat | 0.25
[5 empty] | amb temp rad is sized |  | celotex 100mm | 0.22
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize |  |  | Pitched felt 200mm insulation regs Part L | 0.2
600 | 900 | DC_type22 | 789.9088 | -29.71% | 3.4273 | C | code 3, 2011 | 0.19
|  |  |  | delta t |  |  | renovation extension pitched | 0.19
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 2697.0602 | W | thatch | 0.17
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load. | [6 empty] | code 4, 2013 | 0.16
[7 empty] | code 5 and 6, 2016 | 0.13
Myson Radiator Height mm | Myson Radiator width mm | Radiator type |  |  |  |  | celotex 200mm | 0.11
600 | 1363.5069 | DC type 22 |  |  |  |  | celotex 300mm | 0.073
custom
Room Name | [6 empty] | design ambient temperatures | air temp | gnd temp | altitude m
| Dining Room | [5 empty] | Plymouth | -0.2 | 11 | 27
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss |  | Belfast | -1.2 | 10.5 | 68
Average Ceiling Height m | 2.4 | [5 empty] | Cardiff | -1.6 | 9.9 | 67
Total length Of All External Walls m | 4.3 | [5 empty] | London | -1.8 | 10.2 | 25
External Wall Type | From Data Entry | 2.11 | 498.33 | W | 1125.496 |  | Manchester | -2.2 | 10 | 75
Total Window Area m^2 | 1.5 |  |  |  | heat loss W/m^2 |  | Birmingham | -3.4 | 9.8 | 96
Window Type | From Data Entry | 2.8 | 110.625 | W | 93.7913 |  | Edinburgh | -3.4 | 8.5 | 35
External Roof Area * m^2 | 0 |  |  |  | System Volume |  | Glasgow | -3.9 | 8.5 | 5
Roof light Area m^2 | 0 |  |  |  | 5.8 | litres | Jersey | -0.2 | 11 | 0
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W |  |  | Ventilation rate | AC/hr
Floor Area m^2 | 12 | [5 empty] | From Data Entry | #REF!
Floor Construction | From Data Entry | 1 | 162.84 | W |  |  | Heat recovery 66% efficent | 0.2
[7 empty] | Code 4 or higher | 0.58
Ventilation loss Air change/hr | Dining rooms | 1.5 | 356.4 | W |  |  | Code 3 or higher | 0.7
[7 empty] | Living rooms/Hallways | 1.5
Heat Emitters | [6 empty] | Dining rooms | 1.5
[7 empty] | Bedroom | 1
Emitter Type | UFH Covering type | UFH Pipe Centre |  |  |  |  | Kitchen | 2
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return) |  | Bathroom | 2
[7 empty] | Toilet | 2
[5 empty] | amb temp rad is sized |  | Custom
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
500 | 800 | DC_type22 | 585.1176 | -48.01% | 8.0031 | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 2701.1903 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
[7 empty] | flow temperature | uplift factor | spf | Star rating
Myson Radiator Height mm | Myson Radiator width mm | Radiator type |  |  |  |  | 35 | 6.8 | 3.6 | ******
500 | 1638.7138 | DC type 22 |  |  |  |  | 40 | 4.3 | 3.4 | *****
[7 empty] | 45 | 3.1 | 3 | ****
[7 empty] | 50 | 2.4 | 2.7 | ***
Room Name | [6 empty] | 55 | 1.9 | 2.4 | **
| Landing | [5 empty] | 60 | 1.4 | 2.1 | *
Desired Room Temperature C | 18 | U Values | Results |  | Total Heat Loss |  | 65 | 1.2 | n/a | Zero
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 2 | [5 empty] | Not a hybrid
External Wall Type | From Data Entry | 2.11 | 164.076 | W | 406.4134 |  | Standard boiler
Total Window Area m^2 | 1.5 |  |  |  | heat loss W/m^2 |  | Condensing boiler
Window Type | From Data Entry | 2.8 | 97.35 | W | 90.3141 |  | Combi Boiler
External Roof Area * m^2 | 4.5 |  |  |  | System Volume |  | Back boiler
Roof light Area m^2 | 0 |  |  |  | 0 | litres | High or Unknown Thermal Capacity boiler
Roof / Ceiling Construction | From Data Entry | 0.2 | 28.35 | W |  |  | Wall or flue mounted boiler (balanced on open flue) - Pre 1998
Floor Area m^2 | 4.5 | [5 empty] | Combined Primary Source Units (CPSU)
Floor Construction | internal no loss | -0.15 | 0 | W |  |  | Open fire with back boiler
Closed room heater (stove) with back boiler
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 117.612 | W |  |  | Range cooker boiler (integral oven and boiler)
Community Heating
Heat Emitters | [6 empty] | Storage heaters
Warm air system
Emitter Type | UFH Covering type | UFH Pipe Centre |  |  |  |  | Heat pump
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return) |  | Fire or wall heater
Electric panel convector or Radiant heaters
[5 empty] | amb temp rad is sized |  | Electric underfloor /ceiling heating
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize |  |  | Default-portable electric heaters)
0 | 0 | SC_type11 | 0 | -100% | 18 | C | Other
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 975.3921 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
0 | #DIV/0! | DC type 22
Room Name
Bed 3
Desired Room Temperature C | 18 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 3.4
External Wall Type | From Data Entry | 2.11 | 341.0792 | W | 625.603
Total Window Area m^2 | 1.3 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 84.37 | W | 73.6003
External Roof Area * m^2 | 8.5 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.015 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 53.55 | W
Floor Area m^2 | 8.5
Floor Construction | internal no loss | -0.15 | 0 | W
Ventilation loss Air change/hr | Bedroom | 1 | 148.104 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
500 | 1100 | SC_type11 | 459.5938 | -26.54% | 1.8379 | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 1501.4471 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
500 | 825.4789 | DC type 22
Room Name
Bed 2
Desired Room Temperature C | 18 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 4.3
External Wall Type | From Data Entry | 2.11 | 463.3904 | W | 787.3662
Total Window Area m^2 | 1 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 64.9 | W | 71.5787
External Roof Area * m^2 | 11 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 2.628 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 69.3 | W
Floor Area m^2 | 11
Floor Construction | internal no loss | -0.15 | 0 | W
Ventilation loss Air change/hr | Bedroom | 1 | 191.664 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
300 | 1200 | SC_type11 | 300.825 | -61.79% | 9.5946 | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 1889.679 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
300 | 1731.5408 | DC type 22
Room Name
Bed 1
Desired Room Temperature C | 18 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 7.2
External Wall Type | brick cavity filled block plaster | 0.42 | 194.1192 | W | 594.2023
Total Window Area m^2 | 1.8 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 116.82 | W | 49.5169
External Roof Area * m^2 | 12 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 2.628 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 75.6 | W
Floor Area m^2 | 12
Floor Construction | internal no loss | -0.15 | 0 | W
Ventilation loss Air change/hr | Bedroom | 1 | 209.088 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
300 | 1200 | SC_type11 | 300.825 | -49.37% | 6.8621 | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 1426.0854 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
300 | 1306.7432 | DC type 22
Room Name
En Suite
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 4.2
External Wall Type | brick cavity filled block plaster | 0.42 | 126.54 | W | 420.6113
Total Window Area m^2 | 1.2 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 88.5 | W | 95.5935
External Roof Area * m^2 | 4.4 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 2.628 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 32.34 | W
Floor Area m^2 | 4.4
Floor Construction | internal no loss | -0.15 | 0 | W
Ventilation loss Air change/hr | Bathroom | 2 | 174.24 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
300 | 1200 | SC_type11 | 283.1294 | -32.69% | 4.1716 | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 1009.4672 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
300 | 1020.6783 | DC type 22
Room Name
Room 10
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 11
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 12
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 13
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 14
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 15
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 16
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 17
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 18
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 19
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 20
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 21
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 22
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 23
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 24
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 25
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 26
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 27
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 28
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 29
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 30
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 31
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 32
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 33
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 34
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 35
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 36
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 37
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22
Room Name
Room 38
Desired Room Temperature C | 21 | U Values | Results |  | Total Heat Loss
Average Ceiling Height m | 2.4
Total length Of All External Walls m | 0
External Wall Type | From Data Entry | 2.11 | 0 | W | 0
Total Window Area m^2 | 0 |  |  |  | heat loss W/m^2
Window Type | From Data Entry | 2.8 | 0 | W | #DIV/0!
External Roof Area * m^2 | 0 |  |  |  | System Volume
Roof light Area m^2 | 0 |  |  |  | 4.38 | litres
Roof / Ceiling Construction | From Data Entry | 0.2 | 0 | W
Floor Area m^2 | 0
Floor Construction | From Data Entry | 1 | 0 | W
Ventilation loss Air change/hr | Living rooms/Hallways | 1.5 | 0 | W
Heat Emitters
Emitter Type | UFH Covering type | UFH Pipe Centre
Radiators | Carpet | 150mm |  | 0 | UFH flow rate l/min at 5C delta T (flow - return)
amb temp rad is sized
Current Radiator Height mm | Current Rad width mm | Radiator type | output W | % Oversize
600 | 1000 | SC_type11 | 471.8824 | #DIV/0! | #DIV/0! | C
|  |  |  | delta t | #REF!
Radiator output Watts required if you want to select one yourself at 50C delta T from a radiator table to suit heat emmitter guide |  |  |  |  | 0 | W
this uses the uplift factor from the top of the sheet. However from the Myson table (see Myson tab) you can see the radiator below will also cope with the load.
Myson Radiator Height mm | Myson Radiator width mm | Radiator type
600 | 0 | DC type 22

## equipment
*Insert your Logo Here* | Heat Pump Selection |  |  |  |  | Project | 26 Church Lane
| you can fill in the heat loss manually here or if you use the heat loss calulator it will do this for you. |  |  |  |  | Installer | Egensys Ltd
[6 empty] | Reference | H17.176
Select your heat pump
Annual Space heating Demand | 0 | kWh
Annual Hot Water Demand | 0 | kWh | Choose heat pump here | Samsung 9kW mono |  |  | % of heat LOAD HP can provide | 100.3%
Heat Loss From EPC | 0 | kW
|  |  | System Type | Heating and Hot Water |  |  | % of annual heat load boiler will provide | 0%
Figure from box "January, 39" | 0
Heat Loss from SAP | 0 | kW | ambient temp the boiler begin heating? | not a hybrid |  |  | % required for heating AND hot water | 105.1%
Heat loss if known | 0 | kW | House Heat Load | 6.463 | kW |  | % of heat load system will meet | 100.3%
heat loss from the calculator | 6.463 | kW | oversize factor required for Hot water | 5.077% |  |  | Will the system qualify for MCS? | No Not MCS
Cylinder Recovery |  |  |  |  | Glycol
Output of heat pump (50C flow and -2C amb) |  | 6.48 | kW
Cylinder coil size m^2 |  | 3 | m^2 |  | Approx system volume |  | 187.419 | Litres
Average coil heating capacity |  | 9.72 | kW
actual energy heat pump can put into coil |  | 6.48 | kW
no of kJoules needed to heat whole tank from cold |  | 28424 | kJ
no of kJoules needed to heat tank after delay time |  | -10456 | kJ
immersion heater power |  | 3 | kW |  | Glycol recommended |  | 46.8547 | Litres
immersion delay before starting |  | 100 | mins |  | expansion vessel size |  | 10.6829 | Litres
time immersion runs for |  | 0 | mins
time taken to heat tank (Including Immersion) |  | 73.107 | mins
time to heat with hp only |  | 73.107 | [8 empty] | 0
Estimated run cost
| 874.2505 | per year
Estimation of RHI until october 2017 (an EPC will determine your actual RHI payments)
Current Tarrifs until October 2017 | renewable heat kWhrs from mcs calc
estimation of RHI Per year between | 716.9045 | and | 1147.0471
estimation of RHI over 7yrs, between | 5018.3312 | and | 8029.3299
Everything below this line will not print.
Heat Pump Price | Not MCS |  | Heat pump discount | 0% |  | Your Margin | x
Including accessories at list price plus VAT
Ground Loop Price | 0 |  | Cylinder Discount | 0% |  | Installed System Total | #VALUE!
See ground loop tab for more info | [5 empty] | System at your Price | #VALUE! | As per your discount
Cylinder price | #N/A |  | Cost Of Glycol | 228 |  | Margin Total | #VALUE!
Samsung 5kW mono | 4.04
Samsung 9kW mono | 6.48
Samsung 12kW mono | 9.21
Samsung 16kW mono | 11.42
2 x Samsung 9kW mono | 12.96
Samsung 16kW + 9kW mono | 17.9
2 x Samsung 16kW mono | 22.84
Samsung 6kW Split | 4.68
Samsung 9kW Split | 7.11
Samsung 16kW Split | 12.11
Hitachi Split 2.0
Hitachi Combi 2.0
Hitachi Split 3.0
Hitachi Combi 3.0
Hitachi Mono 3.0
Hitachi Split 4.0 | [12 empty] | 50
Hitachi Combi 4.0 | [12 empty] | 50
Hitachi Mono 4.0 |  |  | 170LTR | 170 | [8 empty] | 50
Hitachi S80 HT 4.0 |  |  | 200LTR | 200 | [8 empty] | 50
Hitachi Split 6.0 |  |  | 250LTR | 250 | [8 empty] | 50
Hitachi Combi 6.0 |  |  | 300LTR | 300 | [8 empty] | 50
Hitachi Mono 6.0 |  |  | 400LTR | 400
Hitachi S80 HT 6.0 |  |  | 500LTR | 500
Hitachi Split 8.0
Hitachi Split 10.0
Temperature |  |  | % of degree days |  | 6.48
-1 |  |  | 0.04
0 |  |  | 0.08
1 |  |  | 0.12 |  | 6.48
2 |  |  | 0.17
3 |  |  | 0.25
4 |  |  | 0.32
5 |  |  | 0.4
6 |  |  | 0.5
7 |  |  | 0.6
50 Degrees C Flow
ambient temperature | 2 x Samsung 16kW mono | Samsung 16kW + 9kW mono | 2 x Samsung 9kW mono | Samsung 16kW mono | Samsung 9kW mono | Samsung 5kW mono | Samsung 12kW mono | Samsung 4kW Split | Samsung 6kW Split | Samsung 9kW Split | Samsung 16kW Split | Hitachi Split 2.0 | Hitachi Combi 2.0 | Hitachi Split 3.0 | Hitachi Combi 3.0 | Hitachi Mono 3.0 | Hitachi Split 4.0 | Hitachi Combi 4.0 | Hitachi Mono 4.0 | Hitachi S80 HT 4.0 | Hitachi Split 6.0 | Hitachi Combi 6.0 | Hitachi Mono 6.0 | Hitachi S80 HT 6.0 | Hitachi Split 8.0 | Hitachi Split 10.0
-10 | 24.12 | 18.44 | 12.76 | 12.06 | 6.38 | 4.02 | 8.39 | 3.68 | 4.59 | 6.67 | 11.48 | 4.02 | 4.02 | 5.46 | 5.46 | 5.46 | 7.79 | 7.79 | 7.79 | 12.39 | 10.77 | 10.77 | 10.77 | 16.01 | 13.65 | 16.37
-7 | 25.3 | 19.18 | 13.06 | 12.65 | 6.53 | 4.6 | 8.93 | 3.95 | 4.94 | 7.2 | 12.42 | 4.41 | 4.41 | 6.05 | 6.05 | 6.05 | 9.87 | 9.87 | 9.87 | 12.5 | 11.83 | 11.83 | 11.83 | 16.15 | 15.7 | 18.36
-2 | 22.84 | 17.9 | 12.96 | 11.42 | 6.48 | 4.04 | 9.21 | 3.74 | 4.68 | 7.11 | 12.11 | 4.45 | 4.45 | 6.82 | 6.82 | 6.82 | 10 | 10 | 10 | 12.98 | 12.98 | 12.98 | 12.98 | 16.37 | 16.75 | 18.97
0 | 20.74 | 16.625 | 12.51 | 10.37 | 6.255 | 3.86 | 9.4275 | 4.01 | 4.995 | 7.035 | 11.8775 | 4.575 | 4.575 | 7.13 | 7.13 | 7.13 | 10.45 | 10.45 | 10.45 | 13.32 | 13.44 | 13.44 | 13.44 | 16.455 | 17.165 | 18.715
2 | 20.04 | 16.2 | 12.36 | 10.02 | 6.18 | 3.8 | 9.5 | 4.1 | 5.1 | 7.01 | 11.8 | 4.7 | 4.7 | 7.44 | 7.44 | 7.44 | 10.9 | 10.9 | 10.9 | 13.66 | 13.9 | 13.9 | 13.9 | 16.54 | 17.58 | 18.46
7 | 29.2 | 22.65 | 16.1 | 14.6 | 8.05 | 4.6 | 10.95 | 4.3 | 5.35 | 8.4 | 14.95 | 6.1 | 6.1 | 9.86 | 9.86 | 9.86 | 13.88 | 13.88 | 13.88 | 14.5 | 17.1 | 17.1 | 17.1 | 17.97 | 24.01 | 28.05
15 | 34.72 | 27.49 | 20.26 | 17.36 | 10.13 | 4.93 | 11.91 | 4.95 | 6.16 | 10.76 | 17.42 | 7.65 | 7.65 | 11.2 | 11.2 | 11.2 | 15.39 | 15.39 | 15.39 | 15.62 | 17.5 | 17.5 | 17.5 | 19.43 | 25.5 | 29
% output provided | 3.534 | 2.7696 | 2.0053 | 1.767 | 0.6251 | 1.0026 | 1.425 | 0.57868 | 0.72412 | 1.1001 | 1.8737 | 0.68853 | 0.68853 | 1.0552 | 1.0552 | 1.0552 | 1.5473 | 1.5473 | 1.5473 | 2.0084 | 2.0084 | 2.0084 | 2.0084 | 2.5329 | 2.5917 | 2.9352
15 | 0
-4 | 6.463
45 Degrees C Flow
ambient temperature | 2 x Samsung 16kW mono | Samsung 16kW + 9kW mono | 2 x Samsung 9kW mono | Samsung 16kW mono | Samsung 9kW mono | Samsung 5kW mono | Samsung 12kW mono | Samsung 4kW Split | Samsung 6kW Split | Samsung 9kW Split | Samsung 16kW Split | Hitachi Split 2.0 | Hitachi Combi 2.0 | Hitachi Split 3.0 | Hitachi Combi 3.0 | Hitachi Mono 3.0 | Hitachi Split 4.0 | Hitachi Combi 4.0 | Hitachi Mono 4.0 | Hitachi Split 6.0 | Hitachi Combi 6.0 | Hitachi Mono 6.0 | Hitachi Split 8.0 | Hitachi Split 10.0
-10 | 25.38 | 19.41 | 13.44 | 12.69 | 6.72 | 4.23 | 8.83 | 3.65 | 4.69 | 6.86 | 11.91 | 4.38 | 4.38 | 5.7 | 5.7 | 5.7 | 9.35 | 9.35 | 9.35 | 11.63 | 11.63 | 11.63 | 15.14 | 17.12
-7 | 27 | 20.65 | 14.3 | 13.5 | 7.15 | 4.5 | 9.39 | 3.88 | 4.99 | 7.33 | 12.74 | 4.6 | 4.6 | 6.4 | 6.4 | 6.4 | 10 | 10 | 10 | 12.5 | 12.5 | 12.5 | 16.6 | 18.5
-2 | 24.06 | 18.86 | 13.66 | 12.03 | 6.83 | 4.25 | 9.7 | 3.68 | 4.74 | 7.29 | 12.39 | 4.7 | 4.7 | 7.14 | 7.14 | 7.14 | 10.6 | 10.6 | 10.6 | 13.56 | 13.56 | 13.56 | 17.66 | 19.89
0 | 22.58 | 17.96 | 13.34 | 11.29 | 6.67 | 4.125 | 9.85 | 3.59 | 4.62 | 7.27 | 12.22 | 4.75 | 4.75 | 7.42 | 7.42 | 7.42 | 11.05 | 11.05 | 11.05 | 14.02 | 14.02 | 14.02 | 18.08 | 20.445
2 | 21.1 | 17.05 | 13 | 10.55 | 6.5 | 4 | 10 | 3.49 | 4.48 | 7.24 | 12.04 | 4.8 | 4.8 | 7.7 | 7.7 | 7.7 | 11.5 | 11.5 | 11.5 | 14.48 | 14.48 | 14.48 | 18.5 | 21
7 | 29.4 | 22.8 | 16.2 | 14.7 | 8.1 | 4.7 | 11.4 | 4.2 | 5.4 | 8.6 | 15.3 | 6.2 | 6.2 | 10 | 10 | 10 | 14.1 | 14.1 | 14.1 | 17.3 | 17.3 | 17.3 | 25 | 32
15 | 36.54 | 28.93 | 21.32 | 18.27 | 10.66 | 5.99 | 14.43 | 4.69 | 6.03 | 10.05 | 17.75 | 7.7 | 7.7 | 11.5 | 11.5 | 11.5 | 16.02 | 16.02 | 16.02 | 18 | 18 | 18 | 26.5 | 33.2
% output provided | 3.7227 | 2.9181 | 2.1136 | 1.8614 | 0.65759 | 1.0568 | 1.5009 | 0.5694 | 0.73341 | 1.128 | 1.9171 | 0.72722 | 0.72722 | 1.1048 | 1.1048 | 1.1048 | 1.6401 | 1.6401 | 1.6401 | 2.0981 | 2.0981 | 2.0981 | 2.7325 | 3.0775
40 Degrees C Flow
ambient temperature | 2 x Samsung 16kW mono | Samsung 16kW + 9kW mono | 2 x Samsung 9kW mono | Samsung 16kW mono | Samsung 9kW mono | Samsung 5kW mono | Samsung 12kW mono | Samsung 4kW Split | Samsung 6kW Split | Samsung 9kW Split | Samsung 16kW Split | Hitachi Split 2.0 | Hitachi Combi 2.0 | Hitachi Split 3.0 | Hitachi Combi 3.0 | Hitachi Mono 3.0 | Hitachi Split 4.0 | Hitachi Combi 4.0 | Hitachi Mono 4.0 | Hitachi Split 6.0 | Hitachi Combi 6.0 | Hitachi Mono 6.0 | Hitachi Split 8.0 | Hitachi Split 10.0
-10 | 25.28 | 19.57 | 13.86 | 12.64 | 6.93 | 4.32 | 9.25 | 3.65 | 4.69 | 6.86 | 11.91 | 4.51 | 4.51 | 6 | 6 | 6 | 9.8 | 9.8 | 9.8 | 11.95 | 11.95 | 11.95 | 15.77 | 18.13
-7 | 26.9 | 20.83 | 14.76 | 13.45 | 7.38 | 4.6 | 9.85 | 3.88 | 4.99 | 7.33 | 12.74 | 4.66 | 4.66 | 6.58 | 6.58 | 6.58 | 10.31 | 10.31 | 10.31 | 12.67 | 12.67 | 12.67 | 17.24 | 19.74
-2 | 24.98 | 19.55 | 14.12 | 12.49 | 7.06 | 4.43 | 9.87 | 3.68 | 4.74 | 7.29 | 12.39 | 4.93 | 4.93 | 7.53 | 7.53 | 7.53 | 11 | 11 | 11 | 13.81 | 13.81 | 13.81 | 18.36 | 20.36
0 | 25.94 | 19.87 | 13.8 | 12.97 | 6.9 | 4.34 | 9.885 | 3.59 | 4.62 | 7.27 | 12.22 | 5.04 | 5.04 | 7.915 | 7.915 | 7.915 | 11.4 | 11.4 | 11.4 | 14.27 | 14.27 | 14.27 | 18.805 | 20.605
2 | 23.06 | 18.28 | 13.5 | 11.53 | 6.75 | 4.25 | 9.9 | 3.49 | 4.48 | 7.24 | 12.04 | 5.15 | 5.15 | 8.3 | 8.3 | 8.3 | 11.8 | 11.8 | 11.8 | 14.73 | 14.73 | 14.73 | 19.25 | 20.85
7 | 30.7 | 23.9 | 17.1 | 15.35 | 8.55 | 4.85 | 11.7 | 4.2 | 5.4 | 8.6 | 15.3 | 6.6 | 6.6 | 10.49 | 10.49 | 10.49 | 14.65 | 14.65 | 14.65 | 17.55 | 17.55 | 17.55 | 25.25 | 32
15 | 37.96 | 29.99 | 22.02 | 18.98 | 11.01 | 6.11 | 14.88 | 4.69 | 6.03 | 10.05 | 17.75 | 8.16 | 8.16 | 11.8 | 11.8 | 11.8 | 16.25 | 16.25 | 16.25 | 18.3 | 18.3 | 18.3 | 26.9 | 33.5
% output provided | 3.8651 | 3.0249 | 2.1847 | 1.9325 | 0.68544 | 1.0924 | 1.5272 | 0.5694 | 0.73341 | 1.128 | 1.9171 | 0.7628 | 0.7628 | 1.1651 | 1.1651 | 1.1651 | 1.702 | 1.702 | 1.702 | 2.1368 | 2.1368 | 2.1368 | 2.8408 | 3.1502
35 Degrees C Flow
ambient temperature | 2 x Samsung 16kW mono | Samsung 16kW + 9kW mono | 2 x Samsung 9kW mono | Samsung 16kW mono | Samsung 9kW mono | Samsung 5kW mono | Samsung 12kW mono | Samsung 4kW Split | Samsung 6kW Split | Samsung 9kW Split | Samsung 16kW Split | Hitachi Split 2.0 | Hitachi Combi 2.0 | Hitachi Split 3.0 | Hitachi Combi 3.0 | Hitachi Mono 3.0 | Hitachi Split 4.0 | Hitachi Combi 4.0 | Hitachi Mono 4.0 | Hitachi Split 6.0 | Hitachi Combi 6.0 | Hitachi Mono 6.0 | Hitachi Split 8.0 | Hitachi Split 10.0
-10 | 25.2 | 19.74 | 14.28 | 12.6 | 7.14 | 4.42 | 9.68 | 3.65 | 4.69 | 6.86 | 11.91 | 4.64 | 4.64 | 6.4 | 6.4 | 6.4 | 10.25 | 10.25 | 10.25 | 12.27 | 12.27 | 12.27 | 16.39 | 18.5
-7 | 26.8 | 21 | 15.2 | 13.4 | 7.6 | 4.7 | 10.3 | 3.88 | 4.99 | 7.33 | 12.74 | 4.7 | 4.7 | 6.71 | 6.71 | 6.71 | 10.62 | 10.62 | 10.62 | 13 | 13 | 13 | 17.9 | 21
-2 | 25.9 | 20.25 | 14.6 | 12.95 | 7.3 | 4.6 | 10.05 | 3.68 | 4.74 | 7.29 | 12.39 | 5.16 | 5.16 | 7.92 | 7.92 | 7.92 | 11.83 | 11.83 | 11.83 | 14.06 | 14.06 | 14.06 | 19.06 | 21
0 | 25.45 | 19.875 | 14.3 | 12.725 | 7.15 | 4.55 | 9.925 | 3.59 | 4.62 | 7.27 | 12.22 | 5.33 | 5.33 | 8.41 | 8.41 | 8.41 | 12.315 | 12.315 | 12.315 | 14.53 | 14.53 | 14.53 | 19.53 | 21.35
2 | 25 | 19.5 | 14 | 12.5 | 7 | 4.5 | 9.8 | 3.49 | 4.48 | 7.24 | 12.04 | 5.5 | 5.5 | 8.9 | 8.9 | 8.9 | 12.8 | 12.8 | 12.8 | 15 | 15 | 15 | 20 | 21.7
7 | 32 | 25 | 18 | 16 | 9 | 5 | 12 | 4.2 | 5.4 | 8.6 | 15.3 | 7 | 7 | 11 | 11 | 11 | 15.2 | 15.2 | 15.2 | 17.8 | 17.8 | 17.8 | 25.5 | 32
15 | 39.38 | 31.05 | 22.72 | 19.69 | 11.36 | 6.23 | 15.32 | 4.69 | 6.03 | 10.05 | 17.75 | 8.4 | 8.4 | 11.9 | 11.9 | 11.9 | 16.48 | 16.48 | 16.48 | 18.6 | 18.6 | 18.6 | 27.1 | 34.7
% output provided | 4.0074 | 3.1332 | 2.259 | 2.0037 | 0.71174 | 1.1295 | 1.555 | 0.5694 | 0.73341 | 1.128 | 1.9171 | 0.79839 | 0.79839 | 1.2254 | 1.2254 | 1.2254 | 1.8304 | 1.8304 | 1.8304 | 2.1755 | 2.1755 | 2.1755 | 2.9491 | 3.2493
55 degrees C Flow |  |  |  | 60 Degrees C Flow |  |  |  | 65 Degrees C Flow |  |  |  | 70 Degrees C Flow
ambient temperature | Hitachi S80 HT 4.0 | Hitachi S80 HT 6.0 |  | ambient temperature | Hitachi S80 HT 4.0 | Hitachi S80 HT 6.0 |  | ambient temperature | Hitachi S80 HT 4.0 | Hitachi S80 HT 6.0 |  | ambient temperature | Hitachi S80 HT 4.0 | Hitachi S80 HT 6.0
-10 | 12.22 | 15.87 |  | -10 | 12.16 | 15.58 |  | -10 | 12.1 | 15.3 |  | -10 | 11.81 | 15.17
-7 | 12.5 | 16.1 |  | -7 | 12.5 | 16.05 |  | -7 | 12.5 | 16 |  | -7 | 12.37 | 15.44
-2 | 13.06 | 16.21 |  | -2 | 12.9 | 16.38 |  | -2 | 12.74 | 16.56 |  | -2 | 12.54 | 15.94
0 | 13.35 | 16.255 |  | 0 | 13.06 | 16.515 |  | 0 | 12.84 | 16.78 |  | 0 | 12.61 | 16.135
2 | 13.64 | 16.3 |  | 2 | 13.22 | 16.65 |  | 2 | 12.94 | 17 |  | 2 | 12.68 | 16.33
7 | 14.49 | 17.92 |  | 7 | 14.49 | 17.92 |  | 7 | 14.49 | 17.92 |  | 7 | 14.27 | 17.5
15 | 15.3 | 19.65 |  | 15 | 15.31 | 19.09 |  | 15 | 15.31 | 18.53 |  | 15 | 15.26 | 18.5
Ambient |  |  |  | 75 Degrees C Flow |  |  |  | 80 Degrees C Flow
-10 | 6.38 |  |  | ambient temperature | Hitachi S80 HT 4.0 | Hitachi S80 HT 6.0 |  | ambient temperature | Hitachi S80 HT 4.0 | Hitachi S80 HT 6.0
-7 | 6.53 |  |  | -10 | 11.23 | 14.9 |  | -10 | 10.8 | 14.7
-2 | 6.48 |  |  | -7 | 12.1 | 14.33 |  | -7 | 11.9 | 13.5
0 | 6.255 |  |  | -2 | 12.14 | 14.7 |  | -2 | 11.84 | 13.78
2 | 6.18 |  |  | 0 | 12.155 | 14.85 |  | 0 | 11.815 | 13.89
7 | 8.05 |  |  | 2 | 12.17 | 15 |  | 2 | 11.79 | 14
15 | 10.13 |  |  | 7 | 13.83 | 16.64 |  | 7 | 13.5 | 16
|  |  |  | 15 | 15.17 | 18.44 |  | 15 | 15.1 | 18.4
Output of SELECTED unit at 35 - 50 Degrees C
Ambient | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80
| 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
-10 | 7.14 | 6.93 | 6.72 | 6.38 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
-7 | 7.6 | 7.38 | 7.15 | 6.53 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
-2 | 7.3 | 7.06 | 6.83 | 6.48 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
0 | 7.15 | 6.9 | 6.67 | 6.255 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | 7 | 6.75 | 6.5 | 6.18 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
7 | 9 | 8.55 | 8.1 | 8.05 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
15 | 11.36 | 11.01 | 10.66 | 10.13 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
% of heat LOAD HP can provide | 1.1295 | 1.0924 | 1.0568 | 1.0026 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Note on H40: To choose the correct heat pump you must select the unit which lies above the black House load line at all times up to and including the design temperature DON’T use the peak values
Note on B47: Heat Pump Sizing 4.2.1d) A heat pump shall be selected that will provide at least 100% of the calculated design space heating power requirement at the selected internal and external temperatures in Tables 1 and 2, the selection being made after taking into consideration the flow temperature at the heat pump when it is doing space heating. Performance data from both the heat pump manufacturer and the emitter system designer should be provided to support the heat pump selection. Heat pump thermal power output for the purposes of this selection shall not include any heat supplied by a supplementary electric heater. Where clauses 4.2.1d and/or 4.2.1e cannot be met, then clause 4.2.1f shall apply. e) When selecting an air source heat pump, the heat pump shall provide 100% of the calculated design space heating power requirement at the selected ambient temperature and emitter temperature, after the inclusion of any energy required for defrost cycles.

## MCS calc and run costs
Run cost calculator | total kW/hr heat p/a inc hot water |  | kWhrs heat provided by heat pump |  | kWhrs heat provided by boiler | kWhrs provided by immersion |  |  |  |  | unit | Samsung 9kW mono
MCS location | Birmingham | [9 empty] | run temp | 50
[5 empty] | P specific is the amount of heat lost when the ambient temperature | [5 empty] | scop at 55 | 0
P specific | 0.25852 |  | load kw | 6.463 | is 1 degree lower than the room temp | [5 empty] | scop at 50 | 0
[11 empty] | scop at 45 | 0
cylinder volume | 170 | L | [8 empty] | scop at 40 | 0
[11 empty] | scop at 35 | 0
| 18030.3835 |  | 17927.7413 |  | 0 | 102.6422 |  |  |  |  | rhi rate | 0.0763 | 0.102
Current Heating System | estimated run cost /yr |  | current electricity price | [7 empty] | Cap | 20000
LPG** | 1365.9381 |  | 0.15 | £/kwhr | Run cost estimation per month of heat pump
New Heating System | estimated run cost /yr | saving over old system | CO2 saving kg per year
HEAT PUMP (electric) | 874.2505 | 36% | 427344.8785 |  | Month | % energy used/ month | Actual cost / month | direct debit for heating / month |  |  |  | #N/A
Assumes that natural gas is 4.3p/kW/hr, oil is 60p/Litre And LPG is 38p/Litre.
Domestic RHI |  |  |  |  | January | 16.81% | 147.0052 | 72.8506
|  |  | Is the house new build ? |  | February | 15.77% | 137.8693 | 72.8506 |  |  | solar pv available | kwhrs/mnth / 3 | solar pv contribution
[5 empty] | March | 12.54% | 109.631 | 72.8506 |  |  |  | used |  |  |  |  | london | plymouth | manchester | edinburgh | belfast | birmingham | glasgow | cardiff
RHI for units pre 20-9-17 |  |  |  |  | April | 8.455% | 73.9179 | 72.8506 |  |  | 136.71 | 1090.7814 | 136.71 | 6.1415 |  | jan | 142.91 | 157.48 | 112.53 | 115.63 | 110.98 | 136.71 | 102.61 | 130.82
| renewable heat kWhrs from mcs calc |  |  |  | May | 4.56% | 39.8658 | 72.8506 |  |  | 188.16 | 1022.9927 | 188.16 | 8.4528 |  | feb | 197.68 | 218.4 | 177.52 | 185.36 | 180.04 | 188.16 | 167.44 | 189.84
| 12527.8192 |  | no |  | June | 1.8% | 15.7365 | 72.8506 |  |  | 359.6 | 813.4641 | 359.6 | 16.1545 |  | mar | 372 | 415.4 | 344.1 | 341 | 334.8 | 359.6 | 308.14 | 359.6
[5 empty] | July | 1.8% | 15.7365 | 72.8506 |  |  | 432 | 548.472 | 432 | 19.407 |  | apr | 462 | 507 | 402 | 423 | 432 | 432 | 405 | 438
estimation of RHI Per year between | 716.9045 | and | 1147.0471 |  | August | 1.615% | 14.1191 | 72.8506 |  |  | 480.5 | 295.8051 | 295.8051 | 13.2886 |  | may | 486.7 | 545.6 | 452.6 | 508.4 | 502.2 | 480.5 | 477.4 | 480.5
[5 empty] | September | 2.375% | 20.7634 | 72.8506 |  |  | 471 | 116.7652 | 116.7652 | 5.2455 |  | jun | 489 | 537 | 441 | 438 | 450 | 471 | 432 | 480
estimation of RHI over 7yrs, between | 5018.3312 | and | 8029.3299 |  | October | 5.795% | 50.6628 | 72.8506 |  |  | 474.3 | 116.7652 | 116.7652 | 5.2455 |  | jul | 480.5 | 520.8 | 437.1 | 449.5 | 440.2 | 474.3 | 427.8 | 471.2
[5 empty] | November | 11.59% | 101.3256 | 72.8506 |  |  | 409.2 | 104.7643 | 104.7643 | 4.7064 |  | aug | 427.8 | 480.5 | 372 | 403 | 381.3 | 409.2 | 368.9 | 409.2
potential saving using 4KW of PV is installed on the roof |  |  | 109.7057 |  | December | 16.88% | 147.5735 | 72.8506 |  |  | 351 | 154.0652 | 154.0652 | 6.9211 |  | sep | 375 | 426 | 315 | 336 | 315 | 351 | 295.8 | 354
[5 empty] | total | 99.99% | 874.2068 |  |  |  | 252.03 | 375.919 | 252.03 | 11.3221 |  | oct | 270.32 | 296.36 | 227.85 | 238.39 | 212.66 | 252.03 | 203.36 | 252.34
[11 empty] | 161.7 | 751.838 | 161.7 | 7.2641 |  | nov | 173.4 | 202.2 | 141.6 | 157.5 | 142.8 | 161.7 | 131.4 | 161.7
Tarrifs from 20th September 2017 onwards
renewable heat kWhrs from mcs calc
| 12527.8192 |  | no
[11 empty] | 123.69 | 1094.9979 | 123.69 | 5.5566 |  | dec | 123.69 | 143.53 | 110.67 | 95.79 | 103.54 | 123.69 | 81.22 | 122.76
estimation of RHI Per year between | 958.3782 | and | 1277.8376
estimation of RHI over 7yrs, between | 6708.6472 | and | 8944.8629
potential saving using 4KW of PV is installed on the roof |  |  | 109.7057
MCS Calculation | [13 empty] | 109.7057
Heating | [5 empty] | Additional Pumps
annual space heating requirement for building |  |  | 15045.8635 | kWhrs
annual space heating to be supplied by installed renewable heating technology |  |  | 15045.8635 | kWhrs |  |  |  | Pump Wattage
SCOP of the unit at design temperature |  |  | 3.32 |  |  | Pump 1 |  | 0
electrical energy input to heat pump from SCOP |  |  | 4531.8866 | kWhrs |  | Pump 2 |  | 0
% of space heating provided by the heat pump (exc aux heaters/ backup boiler) |  |  | 100% | % |  | Pump 3 |  | 0
heat supplied by external backup heater (samsung don’t use backup electrical heaters) |  |  | 0 | kWhrs |  | Pump 4 |  | 0
total electrical input for heating HP |  |  | 4531.8866 | kWhrs |  | Pump 5 |  | 0
Hot water
annual water heating DHW requirement for building |  |  | 2984.52 | kWhrs
annual water heating DHW to be supplied by the installed renewable technology |  |  | 2881.8778 | kWhrs
electrical energy input to HP at 2.5 SPF (HW IS ALWAYS CALCULATED AT 2.5 SPF) |  |  | 1152.7511 | kWhrs
% of hot water heating DHW provided by the heat pump (exc aux heaters) |  |  | 96.56% | % |  | Estimation of pump run cost
how many times will legionella function be performed per week? |  |  | 1
heat supplied by immersion heater including 1hr for legionella/week |  |  | 102.6422 | kWhrs |  |  |  | 0
total electrical input for DHW HP + immersion |  |  | 1255.3933 | kWhrs |  | Cost of one cylinder heating cycle
For MCS paperwork | [5 empty] | Immersion cost |  | 0
% of space heating and water heating demand provided by the heat pump (exc aux heaters) |  |  | 99.43% | % |  | Heat Pump cost |  | 0.44215
Total installed capacity |  |  | Samsung 9kW mono | kW |  | Total |  | 0.44215
Declared net capacity |  |  | 9 | kW
Total electrical input for heating and hot water (including aux heaters) |  |  | 5787.2799 | kWhrs
total renewable energy provided by HP for heating and HW, estimated annual generation |  |  | 12527.8192 | kWhrs
mcs number of unit installed |  |  | MCS HP0227/02
degree days |  | Degree Day data from CIBSE Guide A (base temperature 15.5 °C) 1976-1995 |  |  |  |  | Cost of running single fuel heating system
Belfast | 2360 | [5 empty] | Fuel | Energy Price per KWhr this can be adjusted | Efficency % and SPF (seasonal COP) | cost of heat per kWhr | estimated heating and hw bill p/a | % saving using heat pump | Carbon Intensity kgCO2/kWhr | Carbon Intensity kgCO2/kWhr heat | CO2 emmissions per year. kg
Birmingham | 2425
Manchester | 2388 | [5 empty] | HEAT PUMP (electric) | 0.15 | 3.32 | 0.045181 | 858.8542 |  | 0.445 | 0.13418 | 2419.3299
Plymouth | 1858 | [5 empty] | Old heating oil boiler | 0.6 | 60% | 0.1 | 1803.0384 | 52.37% | 0.26876 | 44.7933 | 807640.9797 | Boiler + heat pump
cardiff | 2161 | [5 empty] | New heating oil boiler* | 0.6 | 90% | 0.066667 | 1202.0256 | 28.55% | 0.26876 | 29.8622 | 538427.3198 | Boiler + heat pump
london | 2033 | [5 empty] | LPG** | 0.45 | 90% | 0.075758 | 1365.9381 | 37.12% | 0.21452 | 23.8356 | 429764.2084 | LPG+ heat pump
glasgow | 2494 | [5 empty] | Natural gas OFGEM | 0.044 | 83.5% | 0.052695 | 950.104 | 9.604% | 0.18404 | 22.0407 | 397402.609 | Nat Gas + heat pump
Edinburgh | 2577 | [5 empty] | Natural Gas old boiler 10yr+ | 0.044 | 70% | 0.062857 | 1133.3384 | 24.22% | 0.18404 | 26.2914 | 474044.5408 | Nat Gas + heat pump
Jersey | 1750 | [5 empty] | Natural Gas new boiler | 0.044 | 83.5% | 0.052695 | 950.104 | 9.604% | 0.18404 | 22.0407 | 397402.609 | Nat Gas + heat pump
[7 empty] | Electricity - UK | 0.15 | 100% | 0.15 | 2704.5575 | 68.24% | 0.44548 | 44.548 | 803217.5256
[7 empty] | Economy 7 heating | 0.06 | 100% | 0.06 | 1081.823 | 20.61% | 0.44548 | 44.548 | 803217.5256
[7 empty] | Coal | 0.054 | 50% | 0.108 | 1947.2814 | 55.89% | 0.31304 | 62.608 | 1128846.2523
[7 empty] | Not a hybrid |  |  | cost of fossil fuel / kwhr |  |  | cost of heat pump p/a | estimated backup boiler run cost p/a
[7 empty] | Boiler + heat pump | 0.044924 |  | 0.1 | 809.9883 | -6.033% | 809.9883 | 0 | 2405.5573
[7 empty] | LPG+ heat pump | 0.044924 |  | 0.075758 | 809.9883 | -6.033% | 809.9883 | 0 | 2405.5573
[7 empty] | Nat Gas + heat pump | 0.044924 |  | 0.062857 | 809.9883 | -6.033% | 809.9883 | 0 | 2405.5573
[7 empty] | HEAT PUMP (electric) | 0.14 | 3.32 | 0.045181 | 858.8542 |  | 0.445
at temp
model | kW nominal | actual output -2 and 50c | mcs number | 80 | 75 | 70 | 65 | 60 | 55 | 50 | 45 | 40 | 35 | rhi rate | Spring 2017 tariff
|  |  |  | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Samsung 5kW mono | 5 | 4.04 | MCS HP0227/01 | 10: 2.78; 11: 3.22; 12: 3.66; 13: 3.97; 14: 4.27 | 0.0763 | 0.102
Samsung 9kW mono | 9 | 6.48 | MCS HP0227/02 | 10: 3; 11: 3.32; 12: 3.63; 13: 3.88; 14: 4.13 | 0.0763 | 0.102
Samsung 12kW mono | 12 |  | MCS HP0227/03 | 10: 2.87; 11: 3.24; 12: 3.62; 13: 4; 14: 4.39 | 0.0763 | 0.102
Samsung 14kW mono | 14 |  | MCS HP0227/04 | 10: 2.68; 11: 3.17; 12: 3.66; 13: 3.82; 14: 3.98 | 0.0763 | 0.102
Samsung 16kW mono | 16 | 11.42 | MCS HP0227/05 | 10: 2.5; 11: 2.99; 12: 3.49; 13: 3.71; 14: 3.94 | 0.0763 | 0.102
2 x Samsung 9kW mono | 18 | 12.96 | MCS HP0227/02 | 10: 3; 11: 3.32; 12: 3.63; 13: 3.88; 14: 4.13 | 0.0763 | 0.102
2 x Samsung 12kW mono | 24 |  | MCS HP0227/03 | 10: 2.87; 11: 3.24; 12: 3.62; 13: 4; 14: 4.39 | 0.0763 | 0.102
Samsung 16kW + 9kW mono | 25 | 17.9 | MCS HP0227/02 and /05 | 10: 2.75; 11: 3.155; 12: 3.56; 13: 3.795; 14: 4.035 | 0.0763 | 0.102
2 x Samsung 16kW mono | 32 | 22.84 | MCS HP0227/05 | 10: 2.5; 11: 2.99; 12: 3.49; 13: 3.71; 14: 3.94 | 0.0763 | 0.102
Samsung 4kW Split | 4 |  | TBC | 10: 3.147; 11: 3.4908; 12: 3.8345; 13: 4.1783; 14: 4.522 | 0.0763 | 0.102
Samsung 6kW Split | 6 | 4.68 | TBC | 10: 3.163; 11: 3.507; 12: 3.851; 13: 4.195; 14: 4.539 | 0.0763 | 0.102
Samsung 9kW Split | 9 | 7.11 | TBC | 10: 3.26; 11: 3.5892; 12: 3.9185; 13: 4.2477; 14: 4.577 | 0.0763 | 0.102
Samsung 12kw Split | 12 |  | TBC | 10: 2.833; 11: 3.2815; 12: 3.73; 13: 4.1785; 14: 4.627 | 0.0763 | 0.102
Samsung 14kW Split | 14 |  | TBC | 10: 2.847; 11: 3.17; 12: 3.66; 13: 3.82; 14: 3.98 | 0.0763 | 0.102
Samsung 16kW Split | 16 | 12.11 | TBC | 10: 2.854; 11: 3.2692; 12: 3.6845; 13: 4.0997; 14: 4.515 | 0.0763 | 0.102
Hitachi Split 2.0 | 4 |  | MCS HP0032/57 | 10: 3.3438; 11: 3.7077; 12: 4.0715; 13: 4.3966; 14: 4.7217 | 0.0763 | 0.102
Hitachi Combi 2.0 | 4 |  | MCS HP0032/74/75 | 10: 3.3438; 11: 3.7077; 12: 4.0715; 13: 4.3966; 14: 4.7217 | 0.0763 | 0.102
Hitachi Split 3.0 | 7 |  | MCS HP0032/59 | 10: 2.92; 11: 3.27; 12: 3.62; 13: 3.64; 14: 3.65 | 0.0763 | 0.102
Hitachi Combi 3.0 | 7 |  | MCS HP0032/78/79 | 10: 2.92; 11: 3.27; 12: 3.62; 13: 3.64; 14: 3.65 | 0.0763 | 0.102
Hitachi Mono 3.0 | 7 |  | MCS HP0032/50 | 10: 2.92; 11: 3.27; 12: 3.62; 13: 3.64; 14: 3.65 | 0.0763 | 0.102
Hitachi Split 4.0 | 11 |  | MCS HP0032/61 | 10: 3.2646; 11: 3.6532; 12: 4.0419; 13: 4.267; 14: 4.4922 | 0.0763 | 0.102
Hitachi Combi 4.0 | 11 |  | MCS HP0032/80/82 | 10: 3.2646; 11: 3.6532; 12: 4.0419; 13: 4.267; 14: 4.4922 | 0.0763 | 0.102
Hitachi Mono 4.0 | 11 |  | MCS HP0032/51 | 10: 3.2646; 11: 3.6532; 12: 4.0419; 13: 4.267; 14: 4.4922 | 0.0763 | 0.102
Hitachi S80 HT 4.0 | 11 |  | MCS HP0032/71 |  |  |  | 2.97 | 3.26 | 3.55 | 3.76 | 3.97 | 4.23 | 4.48 | 0.0763 | 0.102
Hitachi Split 6.0 | 16 |  | MCS HP0032/65 | 10: 2.66; 11: 3.06; 12: 3.47; 13: 3.53; 14: 3.6 | 0.0763 | 0.102
Hitachi Combi 6.0 | 16 |  | MCS HP0032/88/90 | 10: 2.66; 11: 3.06; 12: 3.47; 13: 3.53; 14: 3.6 | 0.0763 | 0.102
Hitachi Mono 6.0 | 16 |  | MCS HP0032/55 | 10: 2.66; 11: 3.06; 12: 3.47; 13: 3.53; 14: 3.6 | 0.0763 | 0.102
Hitachi S80 HT 6.0 | 16 |  | MCS HP0032/73 |  |  |  | 2.8 | 2.97 | 3.13 | 3.22 | 3.31 | 3.45 | 3.6 | 0.0763 | 0.102
Hitachi Split 8.0 | 18 |  | MCS HP0032/66 | 10: 2.92; 11: 3.15; 12: 3.38; 13: 3.48; 14: 3.58 | 0.0763 | 0.102
Hitachi Split 10.0 | 20 |  | MCS HP0032/67 | 10: 2.86; 11: 3.03; 12: 3.21; 13: 3.35; 14: 3.49 | 0.0763 | 0.102
Note on D20: New builds will not get RHI, retro fit and self builds will.
Note on D31: New builds will not get RHI, retro fit and self builds will.
Note on I49: Where the number of circulation pumps exceeds two, the electricity costs associated with the operation of the collector and emitter pumpsneeds to be calculated. This extra run cost will be shown in the box below
Note on A127: From MIS3005 v4.1: For installations where other heat sources are available to the same building, the heat sources shall be fully and correctly integrated into a single control system. A heat pump shall be selected such that the combined system will provide at least 100% of the calculated design space heating requirement at the selected internal and external temperatures. It shall be clearly stated by the Contractor what proportion of the building’s space heating and domestic hot water has been designed to be provided by the heat pump. If the heat required by the building exceeds the heat available the calculator will show Not MCS and no value you need to select a bigger unit or a hybrid boiler backup system. 4.3.3 This estimate, when communicated to the client, shall be accompanied by the following disclaimer: ‘The performance of microgeneration heat pump systems is impossible to predict with certainty due to the variability of the climate and its subsequent effect on both heat supply and demand. This estimate is based upon the best available information but is given as guidance only and should not be considered as a guarantee.’ the RHI was launched on 9/4/14. RHI will be calculated from the figures in the energy performance certificate. The EPC calculation is completley different from this MCS calculation so these figures for RHI are only to be used as an estimation. Please tell your customer this. Ofgem states that "It will be misleading to quote these figures when estimating RHI" they also say "you may wish to use them to estimate savings for your customer.

## MCS020 sound test
Freedom Heat pumps heat pump sound checker
MCS020
[11 empty] | note 1 and 2 |  | Note 4
| Heat pump | power dBa | pressure dBa | Sighting the outdoor unit:
| Samsung 5kW mono | 61 | 45 | [9 empty] | Q (STEP 2 RESULT) | Distance from Heat Pump (metres) (STEP 3 RESULT)
| Samsung 9kW mono | 63 | 48 | In a recent change to the rules installers will no longer require planning permission for heat pumps. | [9 empty] | 1 | 1.5 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35
| Samsung 12kW mono | 64 | 50 | As part of the PDR (Permitted Development Rights) planning permission will no longer | [8 empty] | 2 | -8 | -11 | -14 | -17 | -20 | -21 | -23 | -26 | -26 | -28 | -28 | -29 | -29 | -31 | -31 | -31 | -31 | -31 | -31 | -31 | -34 | -34 | -34 | -34 | -34 | -36 | -36 | -36 | -36 | -36 | -37 | -37 | -37 | -37 | -37 | -37
| Samsung 16kW mono | 65 | 51 | be required as long as a few rules are adhered too. | [8 empty] | 4 | -5 | -8 | -11 | -14 | -17 | -19 | -20 | -23 | -23 | -25 | -25 | -26 | -26 | -28 | -28 | -28 | -28 | -28 | -28 | -28 | -31 | -31 | -31 | -31 | -31 | -33 | -33 | -33 | -33 | -33 | -34 | -34 | -34 | -34 | -34 | -34
| Samsung 4kW Split | 53 | 61 | There is a form in MCS called MCS020 which needs to be filled in to meet this requirement | [8 empty] | 8 | -2 | -5 | -8 | -11 | -14 | -16 | -17 | -20 | -20 | -22 | -22 | -23 | -23 | -25 | -25 | -25 | -25 | -25 | -25 | -25 | -28 | -28 | -28 | -28 | -28 | -30 | -30 | -30 | -30 | -30 | -31 | -31 | -31 | -31 | -31 | -31
| Samsung 6kW Split | 57 | 61 | the calculator below duplicates the MCS020 and makes it easy to use
| Samsung 9kW Split | 57 | 64
| Samsung 12kW Split | 59 | 64 | Planning permission, rules for air source heat pumps:
| Samsung 14kW Split | 60 | 64
| Samsung 16kW Split | 61 | 66 | Only one heat pump can be installed without planning permission
| Hitachi 2.0 | 46 | 57 | DON’T use this calculator if more than 1 heat pump is being installed, two units need planning permission.
| Hitachi 3.0 | 50 | 53 | About the unit
| Hitachi 4.0 | 49 | 62 | It must be less than 1m^3 in size
| Hitachi 6.0 | 50 | 59 | It must not be mounted on the side of the building facing the highway or be visible from the highway.
| Hitachi 8.0 | 59 | 61 | It must not exceed 45dBa as measured at the nearest window of the next door neighbour’s property.
| Hitachi 10.0 | 60 | 62 | It must be installed by MCS installer as part of the MCS scheme.
all details are in the table here from MIS3005
Step | [6 empty] | results
0 | what unit are you installing taken from mcs run page |  |  |  | Samsung 9kW mono
1 | sound power level from table above | [5 empty] | 63 | dBa
2 | databook sound pressure level from table above | [5 empty] | 48 | dBa |  |  | Air
2a | how many surfaces (walls, floor and roof) are within 1m of the unit |  |  |  | 3 |  | 8 | directivity
3 | measure the shortest distance in metres from the middle of the heat pump to the nearest door or window of the neighbours
property.We call this the assesment point. The measurement must be to a room other than a bathroom, shower room, toilet or kitchen.
3a | type in distance metres, whole numbers rounded up please |  |  |  | 10 | m | 10
4 | decibel reduction | [5 empty] | -22 | dBa
5 | answer yes to only one of the following | [9 empty] | note 2a
5a | if you stand in front of the heat pump can you see the assesment point window / door |  |  |  | no |  | FALSE
5b | if you move 25cm from the unit can you see the assesment point window / door from the heat pump |  |  |  | no |  | FALSE
5c | is there a solid wall or fence between the heat pump and the neighbours house |  |  |  | yes |  | -10
| decibel reduction | [5 empty] | -10 |  |  |  | no of walls | directivity
6 | calculated Sound pressure level of installation | [5 empty] | 31 | dBa |  |  | 1 | 2
7 | mcs assumed background noise level | [5 empty] | 40 | dBa |  |  | 2 | 4
8 | difference between heat pump noise and background | [5 empty] | 9 | dBa |  |  | 3 | 8
9 | correction factor | [5 empty] | 0.5 | dBa |  |  | 4 | fail sound test
9a | New corrected Sound pressure level | [5 empty] | 40.5 | dBa
10 | the figure in step 9a MUST be below 42dBa to pass as permitted development | [5 empty] | PASS |  |  |  | note 7
[11 empty] | diff from note 8 | correction
[11 empty] | -15 | 0.1
[11 empty] | -14 | 0.2
[11 empty] | -13 | 0.2
[11 empty] | -12 | 0.3
[11 empty] | -11 | 0.3 |  | Distance from Heat Pump (metres) (STEP 3 RESULT) 3: step 4
[11 empty] | -10 | 0.4 |  | Distance from Heat Pump (metres) (STEP 3 RESULT) 3: FALSE
[11 empty] | -9 | 0.5 |  | Distance from Heat Pump (metres) (STEP 3 RESULT) 3: FALSE
[11 empty] | -8 | 0.6 |  | Distance from Heat Pump (metres) (STEP 3 RESULT) 3: -22
[11 empty] | -7 | 0.8 |  | Distance from Heat Pump (metres) (STEP 3 RESULT) 3: -22
[11 empty] | -6 | 1
[11 empty] | -5 | 1.2
[11 empty] | -4 | 1.5
[11 empty] | -3 | 1.8
[11 empty] | -2 | 2.1
[11 empty] | -1 | 2.5
[11 empty] | 0 | 3
[11 empty] | 1 | 2.5
[11 empty] | 2 | 2.1
[11 empty] | 3 | 1.8
[11 empty] | 4 | 1.5
[11 empty] | 5 | 1.2
[11 empty] | 6 | 1
[11 empty] | 7 | 0.8
[11 empty] | 8 | 0.6
[11 empty] | 9 | 0.5
[11 empty] | 10 | 0.4
[11 empty] | 11 | 0.3
[11 empty] | 12 | 0.3
[11 empty] | 13 | 0.2
[11 empty] | 14 | 0.2
[11 empty] | 15 | 0.1
[9 empty] | Samsung 5kW mono | Samsung 5kW mono
[9 empty] | Samsung 9kW mono | Samsung 9kW mono
[9 empty] | Samsung 12kW mono | Samsung 12kW mono
[9 empty] | Samsung 16kW mono | Samsung 16kW mono
[9 empty] | Samsung 4kW Split | Samsung 4kW Split
[9 empty] | Samsung 6kW Split | Samsung 6kW Split
[9 empty] | Samsung 9kW Split | Samsung 9kW Split
[9 empty] | Samsung 12kw Split | Samsung 12kw Split
[9 empty] | Samsung 14kW Split | Samsung 14kW Split
[9 empty] | Samsung 16kW Split | Samsung 16kW Split
[9 empty] | Hitachi Split 2.0 | Hitachi 2.0
[9 empty] | Hitachi Combi 2.0 | Hitachi 2.0
[9 empty] | Hitachi Split 3.0 | Hitachi 3.0
[9 empty] | Hitachi Combi 3.0 | Hitachi 3.0
[9 empty] | Hitachi Mono 3.0 | Hitachi 3.0
[9 empty] | Hitachi Split 4.0 | Hitachi 4.0
[9 empty] | Hitachi Combi 4.0 | Hitachi 4.0
[9 empty] | Hitachi Mono 4.0 | Hitachi 4.0
[9 empty] | Hitachi S80 HT 4.0 | Hitachi 4.0
[9 empty] | Hitachi Split 6.0 | Hitachi 6.0
[9 empty] | Hitachi Combi 6.0 | Hitachi 6.0
[9 empty] | Hitachi Mono 6.0 | Hitachi 6.0
[9 empty] | Hitachi S80 HT 6.0 | Hitachi 6.0
[9 empty] | Hitachi Split 8.0 | Hitachi 8.0
[9 empty] | Hitachi Split 10.0 | Hitachi 10.0
Note on A4: This tool is designed to allow installation companies to establish clearly whether an installation will comply with the MCS Planning Standard and includes a calculation procedure designed to confirm whether the permitted development noise limit of 42 dB LAeq,5 mins* would be met. The Standard, and the notes and calculations carried out by installation companies, will also be used by local planning authorities and the MCS to verify compliance.
Note on A49: 4.4.1 Heat pumps should be located according to the manufacturer’s instructions. For air source heat pumps, these will include consideration of factors that may detrimentally affect the performance of the heat pump system such as recirculation of chilled air. 4.4.3 Heat pumps should not be located adjacent to sleeping areas or on floors that can transmit vibration. 4.4.4 Anti-vibration pads/mats/mounts and flexible hose connections should be installed according to the manufacturer’s instructions to reduce the effects of vibration on the building structure. 4.4.5 The location of external fans and heat pump compressors should be chosen to avoid nuisance to neighbours and comply with planning requirements. 4.4.7 For air source heat pumps, consideration should be given to the removal of condensate water produced during a defrost cycle from the outdoor coil. The installation should make provision to deal with this water transferring it to a suitable drain or soak away thus preventing ice build-up within the unit or its location during extreme winter conditions. Don't forget to use pre-insulated pipe to take the heat from the heat pump to the house when installing the unit further away from the dwelling that is being heated by the heat pump.
Note on O103: From MIS3005 v4.1: For installations where other heat sources are available to the same building, the heat sources shall be fully and correctly integrated into a single control system. A heat pump shall be selected such that the combined system will provide at least 100% of the calculated design space heating requirement at the selected internal and external temperatures. It shall be clearly stated by the Contractor what proportion of the building’s space heating and domestic hot water has been designed to be provided by the heat pump. If the heat required by the building exceeds the heat available the calculator will show Not MCS and no value you need to select a bigger unit or a hybrid boiler backup system. 4.3.3 This estimate, when communicated to the client, shall be accompanied by the following disclaimer: ‘The performance of microgeneration heat pump systems is impossible to predict with certainty due to the variability of the climate and its subsequent effect on both heat supply and demand. This estimate is based upon the best available information but is given as guidance only and should not be considered as a guarantee.’ the RHI was launched on 9/4/14. RHI will be calculated from the figures in the energy performance certificate. The EPC calculation is completley different from this MCS calculation so these figures for RHI are only to be used as an estimation. Please tell your customer this. Ofgem states that "It will be misleading to quote these figures when estimating RHI" they also say "you may wish to use them to estimate savings for your customer.

## MCS Compliance Certificate
MCS Compliance Certificate
Heat Pump
1. General information |  |  |  | Notes
1.1 | Name of the owner |  | 0 | This sheet is unlocked
1.2 | Address of the owner |  | 0 | so please be careful not to delete formulas,
1.3 | Address at which the heating system is installed, if different to above |  | 0 | Orange cells need to be filled manually
1.4 | MCS certification number of installation company |  | NIC5717 | those in blue are automatically filled in
1.5 | Name of MCS installation company |  | Egensys Ltd
1.6 | Address of MCS installation company |  | Enterprise Business Centre, Carlton Road, Worksop, S81 7QF
1.7 | Commissioning date of the installation |  | 0
2. Purpose of installation
2.1 | Does the installation provide:
| i. Space heating |  | Yes
| ii. Domestic hot water |  | Yes
iii. Other (please state)
2.2 | Is the installation designed for intermittent or continuous heating? |  | Continuous
2.3 | Are the heating services to the building bivalent/multivalent? |  | No
3. Regulations and approvals
3.1 | i. Have all regulations been met and approvals obtained (including planning approval as required)? |  | Yes
| ii. If installed in England, does the installation comply with MCS 020 where permitted development is required (air source heat pumps only)? |  | Yes
4. Heating calculations
4.1 | i. Has a heat loss calculation been carried out for every heated room? |  | Yes
| ii. Heat loss calculator used (name and version) |  | Freedom heat pumps heat loss tool v46.4
| iii. Design external temperature (°C) |  | -4
| iv. Design ground temperature (°C) (for solid floor losses only) |  | 9.2
| v. Design internal temperatures (°C) |  | 21
| vi. Total building heat loss in kW |  | 6.463
4.2 | If the installation has been designed for intermittent heating, what uplift factor has been applied to the building heat loss when sizing the: |  | N/A
| i. Heat source |  | N/A
| ii. Heat emitters |  | N/A
4.3 | i. Has the Domestic Hot Water (DHW) system been designed by considering the number and types of points of use and anticipated consumption within the property? |  | Yes
| ii. Has the reheat time of the hot water storage vessel been estimated and agreed with the customer? |  | Yes
4.4 | Have the implications of the system design on the costs associated with providing space heating and domestic hot water to the building been explained in writing to the owner? |  | Yes
5. Heat emitter design
5.1 | i. Lowest of the oversize factors or pipe spacing (as appropriate) for the heat emitters that are to be used |  | 1.68
| ii. What heat emitters are installed? (List all that apply using Heat Emitter Guide (HEG)) |  | The table below answers all three of these questions
iii. Floor covering (If underfloor heating)
iv. All Room heat losses in watts (W) (or W/m2 together with floor areas)
Room Name | Heat Loss (W/m²) | Emitter Type | UFH Floor Covering (If Apliccable)
Kitchen | 76.7577 | Radiators | Not Applicable
WC | 88.7633 | Radiators | Not Applicable
Lounge | 93.6479 | Radiators | Not Applicable
Dining Room | 93.7913 | Radiators | Not Applicable
Landing | 90.3141 | Radiators | Not Applicable
Bed 3 | 73.6003 | Radiators | Not Applicable
Bed 2 | 71.5787 | Radiators | Not Applicable
Bed 1 | 49.5169 | Radiators | Not Applicable
En Suite | 95.5935 | Radiators | Not Applicable
Room 10 | #DIV/0! | Radiators | Not Applicable
Room 11 | #DIV/0! | Radiators | Not Applicable
Room 12 | #DIV/0! | Radiators | Not Applicable
Room 13 | #DIV/0! | Radiators | Not Applicable
Room 14 | #DIV/0! | Radiators | Not Applicable
Room 15 | #DIV/0! | Radiators | Not Applicable
Room 16 | #DIV/0! | Radiators | Not Applicable
Room 17 | #DIV/0! | Radiators | Not Applicable
Room 18 | #DIV/0! | Radiators | Not Applicable
Room 19 | #DIV/0! | Radiators | Not Applicable
Room 20 | #DIV/0! | Radiators | Not Applicable
Room 21 | #DIV/0! | Radiators | Not Applicable
Room 22 | #DIV/0! | Radiators | Not Applicable
Room 23 | #DIV/0! | Radiators | Not Applicable
Room 24 | #DIV/0! | Radiators | Not Applicable
Room 25 | #DIV/0! | Radiators | Not Applicable
Room 26 | #DIV/0! | Radiators | Not Applicable
Room 27 | #DIV/0! | Radiators | Not Applicable
Room 28 | #DIV/0! | Radiators | Not Applicable
Room 29 | #DIV/0! | Radiators | Not Applicable
Room 30 | #DIV/0! | Radiators | Not Applicable
Room 31 | #DIV/0! | Radiators | Not Applicable
Room 32 | #DIV/0! | Radiators | Not Applicable
Room 33 | #DIV/0! | Radiators | Not Applicable
Room 34 | #DIV/0! | Radiators | Not Applicable
Room 35 | #DIV/0! | Radiators | Not Applicable
Room 36 | #DIV/0! | Radiators | Not Applicable
Room 37 | #DIV/0! | Radiators | Not Applicable
Room 38 | #DIV/0! | Radiators | Not Applicable
| vi. Temperature (°C) of the water leaving the heat pump when supplying space heating at the design external temperature? |  | 50
| vii. What is the Temperature Star Rating for the whole heating system? |  | ***
| viii. Has the customer been provided with a copy of the calculations carried out for the HEG? |  | Yes |  | these are incuded in the heat load calculator
6. Hot water system
6.1 | i. Is hot water heating provided by the heat pump? |  | Yes
| ii. Maximum flow temperature (°C) of the heat pump while providing hot water |  | 55°C
| iii. Fraction of hot water supplied by the heat pump, excluding the immersion heater |  | 96.56%
| iv. Volume of the cylinder in litres and note evidence for the choice |  | 170 |  | Litres
| v. Is the cylinder including the heat exchanger designed to operate with a heat pump? |  | Yes |  | If the coil is 2.5m^2 put yes , if not DON’T use it
7. Heat pump selection
7.1 | i. Make and model name of the installed heat pump |  | Samsung 9kW mono
| ii. MCS product certification number for the heat pump |  | MCS HP0227/02 |  | full codes found on "MCS calc and run cost" sheet, column K & L, rows 55 to 76
| iii. Heat output from the heat pump in kW (excluding heat from any supplementary heaters) at the design external and design flow temperatures |  | 9
| iv. Does the heat pump provide a full or partial heating service? |  | Full |  | If it’s a hybrid put in "PARTIAL", if its not a hybrid put in "FULL"
| v. If partial, what is the percentage of annual space heating requirements met by the heat pump (excluding supplementary heaters)? |  | 100%
| vi. Does the heat pump provide full or partial hot water heating? |  | Full |  | If it’s a hybrid put in "PARTIAL", if its not a hybrid put in "FULL" | Samsung 9kW mono | BBA 0104/01
| vii. If partial, what is the percentage of annual hot water requirements met by the heat pump (excluding supplementary heaters)? |  | 96.56% |  |  | Samsung 16kW mono | BBA 0104/10
8. Design of ground heat exchanger | [6 empty] | BBA 0104/13
8.1 | i. Has the customer been provided with a completed copy of Table 3 from MIS 3005? |  | N/A |  |  | Samsung 6kW split | BBA 0104/07
| ii. Annual energy (kWh/yr) assumed for the ground heat exchanger design |  | N/A |  |  | Samsung 7kW split | BBA 0104/06
| iii. Confirm that: |  | N/A |  |  | Samsung 8kW split | BBA 0104/05
| a. the flow of thermal transfer fluid is turbulent in the ground heat exchanger active elements |  | N/A |  |  | Samsung 11kW split | BBA 0104/04
| b. the closed-loop ground collector system pumping power at the lowest operating temperature is less than 3% of the heat pump heating capacity |  | N/A |  |  | Samsung 14kW split | BBA 0104/03
| c. the method used is location specific taking account of UK average ground temperatures |  | N/A |  |  | Samsung 16kW split | BBA 0104
| d. the temperature of the thermal transfer fluid entering the heat pump been designed to be not less than 0°C at all times for 20 years |  | N/A
| iv. Type of ground heat exchanger |  | N/A
9. System performance calculations and annual energy figures
9.1 | i. Annual space heating demand (kWh/yr) |  | 15045.8635
| ii. Annual water heating demand (kWh/yr) |  | 2984.52
| iii. Percentage of space heating and water heating demand provided by the heat pump (excluding auxiliary and immersion heaters) |  | 99.43%
| iv. Annual electricity consumption of the heat pump (excluding auxiliary and immersion heaters) (kWh/yr) |  | 5684.6377
| v. Annual electricity consumption of auxiliary and immersion heaters (kWh/yr) |  | 102.6422
| vi. Annual energy consumption of other heat sources (kWh/yr) |  | 102.6422
| vii. SCOP of the heat pump at the design water temp |  | 3.32
9.2 | i. (Optional) If intended as domestic RHI installation, maximum qualifying renewable heat (kWh/yr) from the Energy Performance Certificate (EPC) where available
10. Installation
10.1 | i. Does the installation conform to the design? |  | Yes
| ii. Have all manufacturers’ instructions been followed including installation location and condensate drainage (as appropriate)? |  | Yes
| iii. Where the requirements of MIS 3005 exceed those of the manufacturer, have the requirements of MIS 3005 been met? |  | Yes
10.2 | If intended as a domestic RHI installation:
| i. Does the installation conform to the MCS Domestic RHI Metering Guidance? |  | Yes
| ii. What is the outcome of Procedure A in the MCS Domestic RHI Metering Guidance? |  | if ts a hybrid you have to allow for a meter, if its 100% heat pump you don’t. See check list to right.
| iii. Is the installation meter ready? If not, please state why. |  | Yes
10.3 | For ground source heat pumps: |  | N/A
| i. Has the system been flushed, purged, filled and pressure tested according to MIS 3005? |  | yes
| ii. What make and type of antifreeze has been added to make up the thermal transfer fluid? |  | Propelene Glycol
| iii. Is the antifreeze mixed to at least -10 °C and has it been tested twice with a refractometer? |  | yes
| iv. Has the recommended biocide been added in the quantity specified? |  | yes
11. Commissioning and handover
11.1 | i. Explain how the controls have been set to ensure that the system operating temperature is no higher than TFSH at the design external temperature |  | weather compensated in built thermostat controls flow temperature Tfsh to a maximum of 52C
| ii. Record the control settings |  | Tfsh set to 52°C at -2°C ambient 37C at +15C
11.2 | i. Has the heat pump and other components of the system been commissioned according to the manufacturers' instructions and system design parameters? |  | Yes
| ii. Has a label been attached to the system in accordance with MIS 3005? |  | Sticker is supplied with the instruction manual
11.3 | i. Have you given the customer a handover pack?
| ii. State the issue number of MIS 3005 used |  | MIS3005v5
| iii. Have you informed the customer that they will receive an MCS installation certificate that they should keep with their handover pack? |  | Yes
12. Confirmation
12.1 | I am authorised to sign this certificate on behalf of the MCS installation company named above and I confirm that: (i) the heating installation at the premises whose address is shown above has been designed and installed in accordance with MIS 3005; (ii) the design included a heat loss calculation for every room of the building that is heated by the installation; (iii) the installation conforms to the design; (iv) controls to ensure TFSH have been installed and set correctly.
Signature:
Full name and job title:
Date:

## SPF Calculator (hidden)
Domestic RHI Heat Pump SPF Calculator
Details of MCS-certified installer completing this form | [7 empty] | Domestic RHI applicant details | [6 empty] | Version: | 1.1 | March 2014
• Always save this spreadsheet as a 'Macro-enabled' workbook ('.xlsm')
Installer name: |  | Egensys Ltd | [5 empty] | Name: | [7 empty] | [File > Save As > Excel Macro-Enabled Workbook]
MCS Certificated Company Name: |  |  |  | Egensys Ltd |  |  |  | Installation address:
MCS Certificated Company MCS Number: |  |  |  | NIC5717 | [10 empty] | Who needs to use this tool?
Company address: |  | Enterprise Business Centre, Carlton Road, Worksop, S81 7QF
[8 empty] | Installation's MCS Certificate Number: | [6 empty] | • This tool is for MCS certified installers who have been commissioned to assess the Seasonal Performance Factor (SPF) of a heat pump on behalf of legacy applicants to the Domestic RHI
[8 empty] | MCS Certificated Product Number: |  |  |  | #REF!
Company phone number: | [14 empty] | • This tool must be completed in line with the MCS Heat Emitter Guide for Domestic Heat Pumps
[8 empty] | Please confirm that the heat pump(s) at the address above are providing heat to only one single domestic property | [5 empty] | Yes
• All MCS certified installers will need to complete this spreadsheet if an spf of over 2.5 is claimed
Type of heat pump: |  | Air Source Heat Pump |  |  |  | Does system contain a blending valve? |  |  | No | [5 empty] | What should I do next?
• Email a copy of the completed SPF Calculator in the following format:
Number of heated rooms in property: | [5 empty] | Number of unheated rooms:
Number of rooms heated by radiators:
Number of rooms heated by underfloor: | [5 empty] | Design external temp. (°C): |  | #REF! | [6 empty] | To: |  | DomesticRHI@ofgem.gov.uk
Rooms heated by radiators | [14 empty] | Subject: |  | <[MCS-XXXXXXXX-X] [applicant name] SPF Calculator>
[5 empty] | Design int. temp. (°C) | Heat loss power (W) | Rated output of radiators at MW-AT 50°C |  |  |  |  | Flow temperature (°C) | Room star rating |  | Attachments: |  | <A copy of this spreadsheet, saved as 'MCS-XXXXXXXX-X SPF Calculator.xlsm'>
|  | Label (eg bedroom 1) | [7 empty] | Oversize factor
[15 empty] | Text: |  | Installation postcode:
Room 1 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | *** |  |  |  | Applicant name:
Room 2 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | *** |  |  |  | MCS Certificate number:
Room 3 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | *** |  |  |  | MCS Certificated Product Number:
Room 4 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | ***
Room 5 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | ***
Room 6 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | ***
Room 7 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | ***
Room 8 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | ***
Room 9 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | ***
Room 10 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | ***
Room 11 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | ***
Room 12 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | ***
Room 13 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | ***
Room 14 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | ***
Room 15 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | ***
Room 16 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | ***
Room 17 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | ***
Room 18 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | ***
Room 19 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | ***
Room 20 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | ***
Room 21 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | ***
Room 22 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | ***
Room 23 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | ***
Room 24 |  | #REF! |  |  | #REF! | #REF! | #REF! |  |  | #REF! |  | #REF! | ***
5
Rooms heated by underfloor |  |  |  |  | we have assumed here that the radiators NOW installed with the heat pump running are as per the heat loss calc sheet
[5 empty] | Design int. temp. (°C) | Specific heat loss power (W/m2) |  | Underfloor heating type |  | Floor covering | Pipe spacing | Flow temperature (°C) | Room star rating
Label (eg bedroom 1)
Room 1 |  | #REF! |  |  | #REF! | #REF! | [5 empty] | 45 | ****
Room 2 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
Room 3 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
Room 4 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
Room 5 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
Room 6 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
Room 7 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
Room 8 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
Room 9 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
Room 10 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
Room 11 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
Room 12 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
Room 13 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
Room 14 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
Room 15 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
Room 16 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
Room 17 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
Room 18 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
Room 19 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
Room 20 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
Room 21 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
Room 22 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
Room 23 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
Room 24 |  | #REF! |  |  | #REF! | #REF! | [6 empty] | ****
6
[5 empty] | Star rating of worst room: | [6 empty] | 7
Worst performing room: | [7 empty] | SPF:
9
11
Please confirm that the heat loss calculations for the room losses entered above have been done in accordance with BS EN 12831 | [11 empty] | Yes
I declare that, to the best of my knowledge and belief, the information provided as part of this form is accurate with respect to the property for which these calculations are provided.
14
MCS-certified installer signature: | [6 empty] | Date: |  |  |  |  | 15
16
17
18
19
20
| 0 |  | Ground Source Heat Pump
| 1 |  | Air Source Heat Pump
2
| 3 |  | Yes |  | 35
| 4 |  | No |  | 40
| 5 |  |  |  | 45
| 6 |  | Screed |  | 50
| 7 |  | Alu. Panel |  | 55
| 8 |  |  |  | 60
| 9 |  | Tile |  | >60
| 10 |  | Wood
| 11 |  | Carpet |  | Yes
| 12 |  |  |  | No
| 13 |  | PS≤100
| 14 |  | PS≤150
| 15 |  | PS≤200
| 16 |  | PS≤250
| 17 |  | PS≤300
18
| 19 |  | *
| 20 |  | **
| 21 |  | ***
| 22 |  | ****
| 23 |  | *****
| 24 |  | ******
25
| 26 |  | 2.7
| 27 |  | 2.8
| 28 |  | 3.0
| 29 |  | 3.1
| 30 |  | 3.4
3.6
3.7
4.1
4.3

## MCS performance estimate
MCS Performance Estimate
Project Reference: | H17.176
Customer Name: | 0
Installation Address : | 0
Phone Number/Mobile: | 0
Customer Email: | 0
Survey carried out by:
Date of survey:
Your heat pump is expected to provide | 100% | % of your space heating
and | 96.56% | % of your hot water
You will need an immersion heater to heat | 3.439% | % of your hot water
System Design Temperature (°C ) |  | 50
Temperature Star Rating |  | ***
ASHP SCOP at design condition |  | 3.32
Room Name | Heat Loss (W/m²) | Emitter Type |  | UFH Floor Covering (If Apliccable) | UFH Pipe Centre
Kitchen | 76.7577 | Radiators |  | Not Applicable | Not Applicable
WC | 88.7633 | Radiators |  | Not Applicable | Not Applicable
Lounge | 93.6479 | Radiators |  | Not Applicable | Not Applicable
Dining Room | 93.7913 | Radiators |  | Not Applicable | Not Applicable
Landing | 90.3141 | Radiators |  | Not Applicable | Not Applicable
Bed 3 | 73.6003 | Radiators |  | Not Applicable | Not Applicable
Bed 2 | 71.5787 | Radiators |  | Not Applicable | Not Applicable
Bed 1 | 49.5169 | Radiators |  | Not Applicable | Not Applicable
En Suite | 95.5935 | Radiators |  | Not Applicable | Not Applicable
Room 10 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 11 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 12 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 13 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 14 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 15 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 16 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 17 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 18 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 19 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 20 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 21 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 22 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 23 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 24 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 25 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 26 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 27 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 28 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 29 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 30 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 31 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 32 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 33 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 34 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 35 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 36 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 37 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Room 38 | #DIV/0! | Radiators |  | Not Applicable | Not Applicable
Your Estimated RHI Calculation based on the Heat Loss Calculation
Estimated energy eligible for RHI | 12527.8192 | kWh
Tariff: | 7.63 | (p/kWh)
Your Estimated RHI Income based on HLC | 955.8726 | £ / yr
Running costs
estimated heat energy provided by Heat pump | 17927.7413 | kwhrs/yr
Assuming an electricity unit price of | 0.15 | £/kWhr
Costs for space heating | 679.783 | £ / yr
Costs for hot water heating | 179.0712 | £ / yr
Costs for immersion heating | 15.3963 | £ / yr
total cost of heating and Hot water | 874.2505 | £ / yr
Payback
| Predicted heat usage as stated on your heat load calculation | (kWh/yr) | 18030.3835
A | Estimate for your current heating cost per year | (£/yr) | 1365.9381
The proposed heat pump will run on electricity and is able to supply the same heat demand whilst consuming less energy
B | We estimate that your new annual running costs will be | (£/yr) | 874.2505
C | Calculate annual energy saving (A-B) | (£/yr) | 491.6876
D | Annual system output from your Heat load calculation | (kWh/yr) | 17927.7413
E | Estimated Annual RHI income | (£/yr) | 1118.1079 | This is assuming the system is installed after 16/12/16 on the new "Spring 2017" tariff
F | Estimated Total income and savings per year (C + E) | (£/yr) | 1609.7955
G | Total cost of installation (inc VAT) | (£) | #REF!
H | Over seven years the system benefit would be (7xF) | £ | 11268.5684
payback period | Payback calculated by dividing the fully installed cost (G) by the annual system benefit (F) | (yrs) | #REF!
Cylinder reheat time | 73.107 | mins
Heat pump chosen for project | Samsung 9kW mono
Ambient temperature boiler will take over heating | Not a Hybrid
Will the system qualify for MCS | No Not MCS
does the system pass the mcs noise test | PASS
The Microgeneration Certification Scheme (MCS) requires us to provide to the customer a performance estimate based on the standard procedure set out in the Microgeneration Installer Standard for Heat Pumps – MIS 3005.
The estimate is based upon the best available information but is given as guidance only and should not be considered as a guarantee.'
Your energy needs:
Based on the detailed technical survey attached, we have estimated the energy required to heat your property to a comfortable level and provide you with sufficient hot water. The EPC on which your Renewable Heat Incentive payments will be based differs from that used to size the system and is likely to produce a different result.
Installation design
Your heat pump is designed to provide 100% of your space heating needs for 99% of the year. It is possible you may need supplementary space heating for the coldest 1% of the hours. You may also need supplementary heating if: the building is being heated from a cold state or you frequently use large amounts of hot water during cold weather.
Your calculation (attached) works out how much energy is needed to heat each room in your property where the heat pump will be installed. This is known as a heat loss calculation. Once complete we will discuss with you the star rating and the best method to heat each room (radiators or underfloor heating for example). and the benefits of increaseing the insulation. The heat loss calculation was carried out using a method that complies with British Standard BS EN 12831 as specified by the Microgeneration MCS Scheme.
The Renewable Heat Incentive
Under the Renewable Heat Incentive (RHI), you will receive regular payments for seven years as an incentive to use renewable heat technology. The amount of money that is paid to you will depend on the amount of heat your property requires. You will receive a quarterly payment based on the amount of heat your property needs and the efficiency of your system. The rates will change annually in line with the Retail Price Index (RPI).
The RHI will be paid on each kilowatt hour (kWh) of renewable heat the installation generates, not the total heat.
The system's efficiency, known as the Seasonal Performance Factor (SPF), it is the average efficency across the whole year. A heat pump with an SPF of 2.7 generates 2.7 kWh of heat for every one kWh of electricity it uses. This means that nearly two thirds of the heat from that heat pump will be eligible for RHI payments.
Estimating your RHI payments
Your RHI payments will be based on the Energy Performance Certificate (EPC) produced following the Green Deal assessment.
We cannot accuratley calculate your RHI income using the heat loss calulator. It is important to note that the annual heat use provided by this method is just an estimate and will not replace the information provided by an EPC, which is produced by a qualified assessor during a Green Deal Assessment of your property.
Estimating your RHI from the MCS heat loss calculation:
we have estimated the savings compared to the costs of your present system. The proposed heat pump will run on electricity, and is able to supply the same heat demand whilst consuming less energy.
Payback:
To estimate how long the system will take to “pay for itself” (payback), we compare what you pay for the system with our estimate of how much you will receive in RHI payments and save on your energy use.
The Government have stated that RHI payments will be linked to inflation rates and energy prices may well fluctuate, however, as we cannot accurately predict these changes and for simplicity, we have assumed no increase in either RHI payments or energy prices.
It must however be remembered that the RHI will only be paid for a period of seven years.
One of the following calculations to be carried out dependent on whether the system will pay for itself within 7 years. Payback may be omitted from the Performance Estimate if required.
the run cost of the unit is calculated by:
(the energy required to heat the property / SPF) X unit price of electricity
This tool automatically gets filled in as the heat loss is completed please just fill in the orange boxes

## swimming pools (hidden)
| Project | [5 empty] | Wall U-values | u value
| Installer | [5 empty] | part L for internal pools | 0.25
| Reference | [5 empty] | celotex 100mm | 0.22
| 2016-04-22 |  |  | Version 1.1 |  |  | celotex 200mm | 0.11
Heat loss for Pools | [6 empty] | celotex 300mm | 0.073
custom
location | London | -1.8 | MCS Ambient temp |  | 2.85 |  | no cover | n/a
height above sea level | 1 | 10.2 | MCS Ground temp |  | 0 |  | foam filled slats | 1.2
[5 empty] | 0.0099722 |  | 400 grade plastic | 4.22
Ambient design temp | 10 | 10.194 |  |  |  |  | 0.5mm cover | 3.68
Pool wall construction | part L for internal pools | 0.25 | u value |  |  |  | 0.8mm cover | 2.85
cover type | 0.8mm cover | 2.85 | u value | water evaporation | 0 | l/sec | design ambient temperatures | air temp | gnd temp | altitude m
Desired pool Temperature C | 30 | C |  | pool volume litres | 75000 | l | Plymouth | -0.2 | 11 | 27 | #REF!
pool length | 10 | m |  | pool surface area | 50 |  | Belfast | -1.2 | 10.5 | 68
pool width | 5 | m |  | temp drop with cover off | 0.29539 | C/hr | Cardiff | -1.6 | 9.9 | 67
pool depth deep end | 2 | m |  | heat loss into ground | 2.8966 | kW | London | -1.8 | 10.2 | 25
pool depth shallow end | 1 | m |  | heat loss from surface | 3.42 | kW | Manchester | -2.2 | 10 | 75
wind velocity | outdoor moderate | 2.2 | m/sec | Total Heat loss | 6.3166 | kW | Birmingham | -3.4 | 9.8 | 96
pool start temperature | 10 | C |  | heat up duty | 17.9167 | kW | Edinburgh | -3.4 | 8.5 | 35
Required heat up time hours | 96 | hours |  | heat pump required | 24.2333 | kW | Glasgow | -3.9 | 8.5 | 5
[7 empty] | Jersey | -0.2 | 11 | 0
wind velocity
All heat loads are calculated using the figures provided by the customer, | [6 empty] | indoor | 0.5
Freedom Heat pumps take no responsibility for this calculation, it should be used as a guideline only | [6 empty] | outdoor | 1.5
All calculations are based on information supplied, it is your responsibility to check these figures are correct. | [6 empty] | outdoor moderate | 2.2
[7 empty] | outdoor extreme | 4.5
Notes:
customer signature and date
For a 25 m x 20 m swimming pool and 0.5 m/s air velocity above the surface, the evaporation can be calculated as:
gs = ( 25 + 19 (0.5 m/s)) ((25 m) (20 m)) ((0.02 kg/kg) - (0.0098kg/kg)) / 3600
= 0.049 kg/s
The evaporation heat supply required to maintain the temperature of the water can be calculated as:
q = (2257 kJ/kg) (0.049 kg/s)
= 110.6 kW

## myson (hidden)
At 30C delta t
height | length | model no | type 11 | W/M^2 | kW/m length | volume l | l/m^2 | model no | type 21 | W/M^2 | kW/m length | volume l | l/m^2 | model no | type 22 | W/M^2 | kW/m length | volume l | l/m^2
mm | mm |  | W | [5 empty] | W | [5 empty] | W
450 | 400 | PM45SC 40 | 150 | 833.3333 | 0.375 | 1.36 | 7.5556 | PM45DPX 40 | 219 | 1216.6667 | 0.5475 | 2.68 | 14.8889 | PM45DC 40 | 279 | 1550 | 0.6975 | 2.68 | 14.8889
450 | 500 | PM45SC 50 | 190 | 844.4444 | 0.38 | 1.7 | 7.5556 | PM45DPX 50 | 277 | 1231.1111 | 0.554 | 3.35 | 14.8889 | PM45DC 50 | 353 | 1568.8889 | 0.706 | 3.35 | 14.8889
450 | 600 | PM45SC 60 | 229 | 848.1481 | 0.38167 | 2.04 | 7.5556 | PM45DPX 60 | 335 | 1240.7407 | 0.55833 | 4.02 | 14.8889 | PM45DC 60 | 427 | 1581.4815 | 0.71167 | 4.02 | 14.8889
450 | 700 | PM45SC 70 | 268 | 850.7937 | 0.38286 | 2.38 | 7.5556 | PM45DPX 70 | 392 | 1244.4444 | 0.56 | 4.69 | 14.8889 | PM45DC 70 | 499 | 1584.127 | 0.71286 | 4.69 | 14.8889
450 | 800 | PM45SC 80 | 308 | 855.5556 | 0.385 | 2.72 | 7.5556 | PM45DPX 80 | 450 | 1250 | 0.5625 | 5.36 | 14.8889 | PM45DC 80 | 573 | 1591.6667 | 0.71625 | 5.36 | 14.8889
450 | 900 | PM45SC 90 | 347 | 856.7901 | 0.38556 | 3.06 | 7.5556 | PM45DPX 90 | 507 | 1251.8519 | 0.56333 | 6.03 | 14.8889 | PM45DC 90 | 646 | 1595.0617 | 0.71778 | 6.03 | 14.8889
450 | 1000 | PM45SC 100 | 387 | 860 | 0.387 | 3.4 | 7.5556 | PM45SC 100 | 564 | 1253.3333 | 0.564 | 6.7 | 14.8889 | PM45DC 100 | 720 | 1600 | 0.72 | 6.7 | 14.8889
450 | 1100 | PM45SC 110 | 426 | 860.6061 | 0.38727 | 3.74 | 7.5556 | PM45SC 110 | 622 | 1256.5657 | 0.56545 | 7.37 | 14.8889 | PM45DC 110 | 793 | 1602.0202 | 0.72091 | 7.37 | 14.8889
450 | 1200 | PM45SC 120 | 465 | 861.1111 | 0.3875 | 4.08 | 7.5556 | PM45SC 120 | 679 | 1257.4074 | 0.56583 | 8.04 | 14.8889 | PM45DC 120 | 866 | 1603.7037 | 0.72167 | 8.04 | 14.8889
450 | 1400 | PM45SC 140 | 544 | 863.4921 | 0.38857 | 4.76 | 7.5556 | PM45SC 140 | 794 | 1260.3175 | 0.56714 | 9.38 | 14.8889 | PM45DC 140 | 1013 | 1607.9365 | 0.72357 | 9.38 | 14.8889
450 | 1600 | PM45SC 160 | 623 | 865.2778 | 0.38938 | 5.44 | 7.5556 | PM45SC 160 | 910 | 1263.8889 | 0.56875 | 10.72 | 14.8889 | PM45DC 160 | 1160 | 1611.1111 | 0.725 | 10.72 | 14.8889
450 | 1800 | PM45SC 180 | 702 | 866.6667 | 0.39 | 6.12 | 7.5556 | PM45SC 180 | 1025 | 1265.4321 | 0.56944 | 12.06 | 14.8889 | PM45DC 180 | 1306 | 1612.3457 | 0.72556 | 12.06 | 14.8889
450 | 2000 | PM45SC 200 | 781 | 867.7778 | 0.3905 | 6.8 | 7.5556 | PM45SC 200 | 1140 | 1266.6667 | 0.57 | 13.4 | 14.8889 | PM45DC 200 | 1453 | 1614.4444 | 0.7265 | 13.4 | 14.8889
600 | 400 | PM60SC 40 | 190 | 791.6667 | 0.475 | 1.64 | 6.8333 | PM60SC 40 | 277 | 1154.1667 | 0.6925 | 3.32 | 13.8333 | PM60DC 40 | 351 | 1462.5 | 0.8775 | 3.32 | 13.8333
600 | 500 | PM60SC 50 | 241 | 803.3333 | 0.482 | 2.05 | 6.8333 | PM60SC 50 | 350 | 1166.6667 | 0.7 | 4.15 | 13.8333 | PM60DC 50 | 444 | 1480 | 0.888 | 4.15 | 13.8333
600 | 600 | PM60SC 60 | 291 | 808.3333 | 0.485 | 2.46 | 6.8333 | PM60SC 60 | 423 | 1175 | 0.705 | 4.98 | 13.8333 | PM60DC 60 | 536 | 1488.8889 | 0.89333 | 4.98 | 13.8333
600 | 700 | PM60SC 70 | 341 | 811.9048 | 0.48714 | 2.87 | 6.8333 | PM60SC 70 | 495 | 1178.5714 | 0.70714 | 5.81 | 13.8333 | PM60DC 70 | 628 | 1495.2381 | 0.89714 | 5.81 | 13.8333
600 | 800 | PM60SC 80 | 391 | 814.5833 | 0.48875 | 3.28 | 6.8333 | PM60SC 80 | 568 | 1183.3333 | 0.71 | 6.64 | 13.8333 | PM60DC 80 | 721 | 1502.0833 | 0.90125 | 6.64 | 13.8333
600 | 900 | PM60SC 90 | 441 | 816.6667 | 0.49 | 3.69 | 6.8333 | PM60SC 90 | 640 | 1185.1852 | 0.71111 | 7.47 | 13.8333 | PM60DC 90 | 812 | 1503.7037 | 0.90222 | 7.47 | 13.8333
600 | 1000 | PM60SC 100 | 491 | 818.3333 | 0.491 | 4.1 | 6.8333 | PM60SC 100 | 713 | 1188.3333 | 0.713 | 8.3 | 13.8333 | PM60DC 100 | 905 | 1508.3333 | 0.905 | 8.3 | 13.8333
600 | 1100 | PM60SC 110 | 541 | 819.697 | 0.49182 | 4.51 | 6.8333 | PM60SC 110 | 786 | 1190.9091 | 0.71455 | 9.13 | 13.8333 | PM60DC 110 | 997 | 1510.6061 | 0.90636 | 9.13 | 13.8333
600 | 1200 | PM60SC 120 | 591 | 820.8333 | 0.4925 | 4.92 | 6.8333 | PM60SC 120 | 858 | 1191.6667 | 0.715 | 9.96 | 13.8333 | PM60DC 120 | 1089 | 1512.5 | 0.9075 | 9.96 | 13.8333
600 | 1400 | PM60SC 140 | 691 | 822.619 | 0.49357 | 5.74 | 6.8333 | PM60SC 140 | 1003 | 1194.0476 | 0.71643 | 11.62 | 13.8333 | PM60DC 140 | 1273 | 1515.4762 | 0.90929 | 11.62 | 13.8333
600 | 1600 | PM60SC 160 | 791 | 823.9583 | 0.49438 | 6.56 | 6.8333 | PM60SC 160 | 1149 | 1196.875 | 0.71813 | 13.28 | 13.8333 | PM60DC 160 | 1458 | 1518.75 | 0.91125 | 13.28 | 13.8333
600 | 1800 | PM60SC 180 | 891 | 825 | 0.495 | 7.38 | 6.8333 | PM60SC 180 | 1294 | 1198.1481 | 0.71889 | 14.94 | 13.8333 | PM60DC 180 | 1643 | 1521.2963 | 0.91278 | 14.94 | 13.8333
600 | 2000 | PM60SC 200 | 991 | 825.8333 | 0.4955 | 8.2 | 6.8333 | PM60SC 200 | 1439 | 1199.1667 | 0.7195 | 16.6 | 13.8333 | PM60DC 200 | 1827 | 1522.5 | 0.9135 | 16.6 | 13.8333
700 | 400 | PM70SC 40 | 214 | 764.2857 | 0.535 | 1.96 | 7 | PM70SC 40 | 314 | 1121.4286 | 0.785 | 3.96 | 14.1429 | PM70DC 40 | 398 | 1421.4286 | 0.995 | 3.96 | 14.1429
700 | 500 | PM70SC 50 | 270 | 771.4286 | 0.54 | 2.45 | 7 | PM70SC 50 | 397 | 1134.2857 | 0.794 | 4.95 | 14.1429 | PM70DC 50 | 503 | 1437.1429 | 1.006 | 4.95 | 14.1429
700 | 600 | PM70SC 60 | 327 | 778.5714 | 0.545 | 2.94 | 7 | PM70SC 60 | 480 | 1142.8571 | 0.8 | 5.94 | 14.1429 | PM70DC 60 | 607 | 1445.2381 | 1.0117 | 5.94 | 14.1429
700 | 700 | PM70SC 70 | 383 | 781.6327 | 0.54714 | 3.43 | 7 | PM70SC 70 | 561 | 1144.898 | 0.80143 | 6.93 | 14.1429 | PM70DC 70 | 711 | 1451.0204 | 1.0157 | 6.93 | 14.1429
700 | 800 | PM70SC 80 | 439 | 783.9286 | 0.54875 | 3.92 | 7 | PM70SC 80 | 644 | 1150 | 0.805 | 7.92 | 14.1429 | PM70DC 80 | 816 | 1457.1429 | 1.02 | 7.92 | 14.1429
700 | 900 | PM70SC 90 | 495 | 785.7143 | 0.55 | 4.41 | 7 | PM70SC 90 | 726 | 1152.381 | 0.80667 | 8.91 | 14.1429 | PM70DC 90 | 920 | 1460.3175 | 1.0222 | 8.91 | 14.1429
700 | 1000 | PM70SC 100 | 551 | 787.1429 | 0.551 | 4.9 | 7 | PM70SC 100 | 809 | 1155.7143 | 0.809 | 9.9 | 14.1429 | PM70DC 100 | 1025 | 1464.2857 | 1.025 | 9.9 | 14.1429
700 | 1100 | PM70SC 110 | 608 | 789.6104 | 0.55273 | 5.39 | 7 | PM70SC 110 | 892 | 1158.4416 | 0.81091 | 10.89 | 14.1429 | PM70DC 110 | 1130 | 1467.5325 | 1.0273 | 10.89 | 14.1429 | http://www.myson.co.uk/static_files/my/media/downloads/26531_Panel_Tech_Guide_WEB_WITH_DATES.pdf
700 | 1200 | PM70SC 120 | 664 | 790.4762 | 0.55333 | 5.88 | 7 | PM70SC 120 | 974 | 1159.5238 | 0.81167 | 11.88 | 14.1429 | PM70DC 120 | 1233 | 1467.8571 | 1.0275 | 11.88 | 14.1429
700 | 1400 | PM70SC 140 | 776 | 791.8367 | 0.55429 | 6.86 | 7 | PM70SC 140 | 1138 | 1161.2245 | 0.81286 | 13.86 | 14.1429 | PM70DC 140 | 1442 | 1471.4286 | 1.03 | 13.86 | 14.1429
700 | 1600 | PM70SC 160 | 889 | 793.75 | 0.55563 | 7.84 | 7 | PM70SC 160 | 1304 | 1164.2857 | 0.815 | 15.84 | 14.1429 | PM70DC 160 | 1652 | 1475 | 1.0325 | 15.84 | 14.1429
700 | 1800 | PM70SC 180 | 1001 | 794.4444 | 0.55611 | 8.82 | 7 | PM70SC 180 | 1469 | 1165.873 | 0.81611 | 17.82 | 14.1429 | PM70DC 180 | 1860 | 1476.1905 | 1.0333 | 17.82 | 14.1429
700 | 2000 | PM70SC 200 | 1113 | 795 | 0.5565 | 9.8 | 7 | PM70SC 200 | 1633 | 1166.4286 | 0.8165 | 19.8 | 14.1429 | PM70DC 200 | 2069 | 1477.8571 | 1.0345 | 19.8 | 14.1429
at 50C delta T
height | length | model no | type 11 | W/M^2 | kW/m length | model no | type 21 | W/M^2 | kW/m length | model no | type 22 | W/M^2 | kW/m length
mm | mm |  | W |  |  |  | W |  |  |  | W
450 | 400 | PM45SC 40 | 288 | 1600 | 0.72 | PM45DPX 40 | 424 | 2355.5556 | 1.06 | PM45DC 40 | 545 | 3027.7778 | 1.3625
450 | 500 | PM45SC 50 | 364 | 1617.7778 | 0.728 | PM45DPX 50 | 535 | 2377.7778 | 1.07 | PM45DC 50 | 689 | 3062.2222 | 1.378
450 | 600 | PM45SC 60 | 440 | 1629.6296 | 0.73333 | PM45DPX 60 | 647 | 2396.2963 | 1.0783 | PM45DC 60 | 833 | 3085.1852 | 1.3883
450 | 700 | PM45SC 70 | 515 | 1634.9206 | 0.73571 | PM45DPX 70 | 758 | 2406.3492 | 1.0829 | PM45DC 70 | 975 | 3095.2381 | 1.3929
450 | 800 | PM45SC 80 | 591 | 1641.6667 | 0.73875 | PM45DPX 80 | 869 | 2413.8889 | 1.0862 | PM45DC 80 | 1119 | 3108.3333 | 1.3987
450 | 900 | PM45SC 90 | 666 | 1644.4444 | 0.74 | PM45DPX 90 | 980 | 2419.7531 | 1.0889 | PM45DC 90 | 1261 | 3113.5802 | 1.4011
450 | 1000 | PM45SC 100 | 742 | 1648.8889 | 0.742 | PM45SC 100 | 1092 | 2426.6667 | 1.092 | PM45DC 100 | 1405 | 3122.2222 | 1.405
450 | 1100 | PM45SC 110 | 818 | 1652.5253 | 0.74364 | PM45SC 110 | 1203 | 2430.303 | 1.0936 | PM45DC 110 | 1548 | 3127.2727 | 1.4073
450 | 1200 | PM45SC 120 | 893 | 1653.7037 | 0.74417 | PM45SC 120 | 1314 | 2433.3333 | 1.095 | PM45DC 120 | 1691 | 3131.4815 | 1.4092
450 | 1400 | PM45SC 140 | 1044 | 1657.1429 | 0.74571 | PM45SC 140 | 1536 | 2438.0952 | 1.0971 | PM45DC 140 | 1977 | 3138.0952 | 1.4121
450 | 1600 | PM45SC 160 | 1196 | 1661.1111 | 0.7475 | PM45SC 160 | 1760 | 2444.4444 | 1.1 | PM45DC 160 | 2264 | 3144.4444 | 1.415
450 | 1800 | PM45SC 180 | 1347 | 1662.963 | 0.74833 | PM45SC 180 | 1982 | 2446.9136 | 1.1011 | PM45DC 180 | 2550 | 3148.1481 | 1.4167
450 | 2000 | PM45SC 200 | 1498 | 1664.4444 | 0.749 | PM45SC 200 | 2204 | 2448.8889 | 1.102 | PM45DC 200 | 2836 | 3151.1111 | 1.418
600 | 400 | PM60SC 40 | 368 | 1533.3333 | 0.92 | PM60SC 40 | 539 | 2245.8333 | 1.3475 | PM60DC 40 | 691 | 2879.1667 | 1.7275
600 | 500 | PM60SC 50 | 466 | 1553.3333 | 0.932 | PM60SC 50 | 681 | 2270 | 1.362 | PM60DC 50 | 873 | 2910 | 1.746
600 | 600 | PM60SC 60 | 563 | 1563.8889 | 0.93833 | PM60SC 60 | 823 | 2286.1111 | 1.3717 | PM60DC 60 | 1055 | 2930.5556 | 1.7583
600 | 700 | PM60SC 70 | 659 | 1569.0476 | 0.94143 | PM60SC 70 | 964 | 2295.2381 | 1.3771 | PM60DC 70 | 1235 | 2940.4762 | 1.7643
600 | 800 | PM60SC 80 | 756 | 1575 | 0.945 | PM60SC 80 | 1106 | 2304.1667 | 1.3825 | PM60DC 80 | 1417 | 2952.0833 | 1.7712
600 | 900 | PM60SC 90 | 852 | 1577.7778 | 0.94667 | PM60SC 90 | 1247 | 2309.2593 | 1.3856 | PM60DC 90 | 1598 | 2959.2593 | 1.7756
600 | 1000 | PM60SC 100 | 949 | 1581.6667 | 0.949 | PM60SC 100 | 1389 | 2315 | 1.389 | PM60DC 100 | 1780 | 2966.6667 | 1.78
600 | 1100 | PM60SC 110 | 1046 | 1584.8485 | 0.95091 | PM60SC 110 | 1531 | 2319.697 | 1.3918 | PM60DC 110 | 1962 | 2972.7273 | 1.7836
600 | 1200 | PM60SC 120 | 1142 | 1586.1111 | 0.95167 | PM60SC 120 | 1672 | 2322.2222 | 1.3933 | PM60DC 120 | 2142 | 2975 | 1.785
600 | 1400 | PM60SC 140 | 1336 | 1590.4762 | 0.95429 | PM60SC 140 | 1954 | 2326.1905 | 1.3957 | PM60DC 140 | 2504 | 2980.9524 | 1.7886
600 | 1600 | PM60SC 160 | 1530 | 1593.75 | 0.95625 | PM60SC 160 | 2239 | 2332.2917 | 1.3994 | PM60DC 160 | 2868 | 2987.5 | 1.7925
600 | 1800 | PM60SC 180 | 1723 | 1595.3704 | 0.95722 | PM60SC 180 | 2521 | 2334.2593 | 1.4006 | PM60DC 180 | 3231 | 2991.6667 | 1.795
600 | 2000 | PM60SC 200 | 1916 | 1596.6667 | 0.958 | PM60SC 200 | 2804 | 2336.6667 | 1.402 | PM60DC 200 | 3593 | 2994.1667 | 1.7965
700 | 400 | PM70SC 40 | 418 | 1492.8571 | 1.045 | PM70SC 40 | 615 | 2196.4286 | 1.5375 | PM70DC 40 | 783 | 2796.4286 | 1.9575
700 | 500 | PM70SC 50 | 528 | 1508.5714 | 1.056 | PM70SC 50 | 777 | 2220 | 1.554 | PM70DC 50 | 989 | 2825.7143 | 1.978
700 | 600 | PM70SC 60 | 638 | 1519.0476 | 1.0633 | PM70SC 60 | 939 | 2235.7143 | 1.565 | PM70DC 60 | 1195 | 2845.2381 | 1.9917
700 | 700 | PM70SC 70 | 747 | 1524.4898 | 1.0671 | PM70SC 70 | 1099 | 2242.8571 | 1.57 | PM70DC 70 | 1399 | 2855.102 | 1.9986
700 | 800 | PM70SC 80 | 858 | 1532.1429 | 1.0725 | PM70SC 80 | 1261 | 2251.7857 | 1.5762 | PM70DC 80 | 1605 | 2866.0714 | 2.0063
700 | 900 | PM70SC 90 | 967 | 1534.9206 | 1.0744 | PM70SC 90 | 1421 | 2255.5556 | 1.5789 | PM70DC 90 | 1810 | 2873.0159 | 2.0111
700 | 1000 | PM70SC 100 | 1077 | 1538.5714 | 1.077 | PM70SC 100 | 1583 | 2261.4286 | 1.583 | PM70DC 100 | 2016 | 2880 | 2.016
700 | 1100 | PM70SC 110 | 1187 | 1541.5584 | 1.0791 | PM70SC 110 | 1745 | 2266.2338 | 1.5864 | PM70DC 110 | 2222 | 2885.7143 | 2.02
700 | 1200 | PM70SC 120 | 1296 | 1542.8571 | 1.08 | PM70SC 120 | 1906 | 2269.0476 | 1.5883 | PM70DC 120 | 2426 | 2888.0952 | 2.0217
700 | 1400 | PM70SC 140 | 1515 | 1545.9184 | 1.0821 | PM70SC 140 | 2228 | 2273.4694 | 1.5914 | PM70DC 140 | 2837 | 2894.898 | 2.0264
700 | 1600 | PM70SC 160 | 1736 | 1550 | 1.085 | PM70SC 160 | 2552 | 2278.5714 | 1.595 | PM70DC 160 | 3249 | 2900.8929 | 2.0306
700 | 1800 | PM70SC 180 | 1955 | 1551.5873 | 1.0861 | PM70SC 180 | 2874 | 2280.9524 | 1.5967 | PM70DC 180 | 3660 | 2904.7619 | 2.0333
700 | 2000 | PM70SC 200 | 2174 | 1552.8571 | 1.087 | PM70SC 200 | 3197 | 2283.5714 | 1.5985 | PM70DC 200 | 4070 | 2907.1429 | 2.035