## Sheet1
ASHP Heating System Design showing all valves used and general discrption of how they function - DHW used in Hybrid mode.
Thermostat
NOTES
Note 1 | ASHP is setup to take excess solar PV by monitoring PV generation and battery SoC. ASHP will therefore run most sunny days and only use PV power.
Note 2 | Boiler is switched on via UFH Controller, based on average outside temp (over 6 hrs) of below 5 degs
ASHP runs at all other times, only control is thermostat in hall to switch flow temps. Generally locked out by boiler running above start flow temperature permissive for ASHP
Installer Pass code
PSS | 195
Operating Modes
1a. Heating - Runs automatically on Weather Compensated batch floor charging, whole heating system runs as single zone.
1b. Cooling - as above, by selecting summer mode and setting hall thermostat to summer/cooling mode
2. DHW - due to pipe length additional pump required, done via CCT and 3 port valve to provide a return route for water. Cylinder also has 3 port valve activated by cylinder thermostat, this in turn activates a wireless switch to water shed.
3. Hybrid mode works on UFH and DHW.
4. Hydrid heating, this activated by UFH Controller
ASHP
DHW
Cylinder
House Heating - UFH
Plate HE
POD Heating - Fan Coil
Boiler
Boiler Control, via hardwaired connection to UFH Controller. Always on via WC in setback mode. Single from UFH controller moves boiler out of setback - flow temp set to 37 degs via aresistor in wiring centre
2 Port Valve Control
On DHW call for heat, 2 port valve closed.
Summer/Winter switch sets heating / cooling mode on ASHP
3 Port Valve Control - opens and closed in response to DHW call for heat only to give a supply route back to ASHP from CCT
CCT Pump control, on in response to DHW call for heat and gas boiler to UFH. Relay controls ASHP and UFH controller signals
3 Port Valve Control - opens and closed in response to DHW call for heat only, via cylinder thermosat, timing via time switch in UFH controller and wireless switch.
CCT
RF Switch
Radio signal to water shed for DWH demand
PHE, keeps boiler and ASHP Hydraulically seperate
ASHP run WC mode 24/4 - Thermostat in hall switches between two flow temps. Low flow temp keeps circulation pump on, high starts ASHP. Set to 20 degs (+/- 0.1 deg)
UFH Controller
Outside Temp
Room Temp
RF Switch
Relay
UFH Controller.
Wireless outside temp sensor and room sensors. Only hall sensor used to control boiler firing - set to 20.4 degs (+0 / -0.1 deg). No actuators installed on UFH manifold. Controller monitors ouside temperature, only asks for heat when outside temp is below 5 degs for 6 hours or more.
Controls CCT pump and boiler only. Boiler and pump relay hardwired to controller.

## Sheet2
B25 | Restart Hysterisis |  | Original | 2.5 | wasn't restarting at low temperatures
|  |  |  | 2 | Was set here
|  |  |  | 1.4 | Cycling to quickly
|  |  |  | 1.6 | Cycling to quickly
|  |  |  | 1.5 | Current setting but may need increasing????
B05 |  |  | Original | 0.2 | Cycle time too short
|  |  |  | 0.4 | Current setting
Above doesn't allow low enough flow temperatures
7 deg Day on above settings. Target flow temp 29 degs
15 mins running and 25 mins off
On temp average of about 29
Off temp average say 23
Degree hours |  | On | 116
|  | Off | 55.2
|  | Total degree hours | 171.2 | Ratio | 0.47586