## Calculation
Weather Comp simulation | [18 empty] | Summary
Design Ambient |  | -2 | C | [15 empty] | W/C> | None* | Ideal (const DT) | Ideal (const flow) | Linear (const flow) | Lizzie (const flow) | Linear (const flow) + 2C | Lizzie+2C | Add your own
Design Flow |  | 65 | C | [15 empty] | Consumption | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Target temperature |  | 21 | C | [15 empty] | %saving | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Emitter coeff |  | 1.3 | [16 empty] | average COP | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Load @ Design Ambient |  | 10 | kW
Max Heating temp |  | 16 | C | [13 empty] | Note Linear* is a linear best fit to optimum which will result in flow temp a bit too low at some ambient temps
Emitter deltaT |  | 5 | C
Load data |  |  |  | Flow T | [7 empty] | COP | [7 empty] | Annual Consumption
Ambient Temp C | Freq (days/yr) | Load (kW) | Annual load (kWh) | None | Ideal (const DT) | Ideal (const flow) | Linear (const flow) | Lizzie (const flow) | Linear (const flow) + 2C | Lizzie+2C | Add your own | None | Ideal (const DT) | Ideal (const flow) | Linear (const flow) | Lizzie (const flow) | Linear (const flow) + 2C | Lizzie+2C | Add your own | None | Ideal (const DT) | Ideal (const flow) | Linear (const flow) | Lizzie (const flow) | Linear (const flow) + 2C | Lizzie+2C | Add your own
-10 | 0 | 13.4783 | 0 | 65 | 76.3568 | 77.2264 | 79.7636 | 79.7636 | 81.7636 | 81.7636 | 65
-9 | 0 | 13.0435 | 0 | 65 | 74.978 | 75.7389 | 78.0161 | 78.0161 | 80.0161 | 80.0161 | 65
-8 | 0 | 12.6087 | 0 | 65 | 73.5886 | 74.2407 | 76.2685 | 76.2685 | 78.2685 | 78.2685 | 65
-7 | 0 | 12.1739 | 0 | 65 | 72.188 | 72.7315 | 74.521 | 74.521 | 76.521 | 76.521 | 65
-6 | 0 | 11.7391 | 0 | 65 | 70.7759 | 71.2106 | 72.7734 | 72.7734 | 74.7734 | 74.7734 | 65
-5 | 0 | 11.3043 | 0 | 65 | 69.3516 | 69.6777 | 71.0259 | 71.0259 | 73.0259 | 73.0259 | 65
-4 | 1 | 10.8696 | 260.8696 | 65 | 67.9146 | 68.132 | 69.2783 | 69.2783 | 71.2783 | 71.2783 | 65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
-3 | 2 | 10.4348 | 500.8696 | 65 | 66.4643 | 66.573 | 67.5308 | 67.5308 | 69.5308 | 69.5308 | 65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
-2 | 2 | 10 | 480 | 65 | 65 | 65 | 65.7832 | 65.7832 | 67.7832 | 67.7832 | 65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
-1 | 5 | 9.5652 | 1147.8261 | 65 | 63.5209 | 63.4122 | 64.0357 | 64.0357 | 66.0357 | 66.0357 | 65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
0 | 0 | 9.1304 | 0 | 65 | 62.0262 | 61.8088 | 62.2881 | 62.2881 | 64.2881 | 64.2881 | 65
1 | 3 | 8.6957 | 626.087 | 65 | 60.515 | 60.1889 | 60.5406 | 60.5406 | 62.5406 | 62.5406 | 65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
2 | 4 | 8.2609 | 793.0435 | 65 | 58.9862 | 58.5515 | 58.793 | 58.793 | 60.793 | 60.793 | 65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
3 | 7 | 7.8261 | 1314.7826 | 65 | 57.4388 | 56.8953 | 57.0455 | 57.0455 | 59.0455 | 59.0455 | 65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
4 | 17 | 7.3913 | 3015.6522 | 65 | 55.8714 | 55.2192 | 55.2979 | 55.2979 | 57.2979 | 57.2979 | 65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
5 | 21 | 6.9565 | 3506.087 | 65 | 54.2825 | 53.5216 | 53.5504 | 53.5504 | 55.5504 | 55.5504 | 65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
6 | 13 | 6.5217 | 2034.7826 | 65 | 52.6705 | 51.801 | 51.8028 | 51.8028 | 53.8028 | 53.8028 | 65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
7 | 22 | 6.087 | 3213.913 | 65 | 51.0336 | 50.0553 | 50.0553 | 50.0553 | 52.0553 | 52.0553 | 65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
8 | 27 | 5.6522 | 3662.6087 | 65 | 49.3693 | 48.2824 | 48.3077 | 48.3077 | 50.3077 | 50.3077 | 65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
9 | 16 | 5.2174 | 2003.4783 | 65 | 47.6753 | 46.4796 | 46.5602 | 46.5602 | 48.5602 | 48.5602 | 65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
10 | 22 | 4.7826 | 2525.2174 | 65 | 45.9483 | 44.644 | 44.8126 | 44.8126 | 46.8126 | 46.8126 | 65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
11 | 29 | 4.3478 | 3026.087 | 65 | 44.1846 | 42.7716 | 43.0651 | 43.0651 | 45.0651 | 45.0651 | 65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
12 | 20 | 3.913 | 1878.2609 | 65 | 42.3797 | 40.858 | 41.3175 | 41.3175 | 43.3175 | 43.3175 | 65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
13 | 26 | 3.4783 | 2170.4348 | 65 | 40.5278 | 38.8974 | 39.57 | 39.57 | 41.57 | 41.57 | 65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
14 | 25 | 3.0435 | 1826.087 | 65 | 38.6216 | 36.8825 | 37.8224 | 37.8224 | 39.8224 | 39.8224 | 65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
15 | 25 | 2.6087 | 1565.2174 | 65 | 36.6512 | 34.8034 | 36.0749 | 37 | 38.0749 | 38.0749 | 65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
16 | 15 | 2.1739 | 782.6087 | 65 | 34.6031 | 32.6466 | 34.3273 | 37 | 36.3273 | 37 | 65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
17 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
>=21 | 15 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 365 |  | 36333.913
None |  | No weather compensation. Note that this means that below the design temperature the system will deliver inadequate heating
Ideal (const DT) |  | Ideal weather curve where pump modulates to keep DT across emitters constant
Ideal (const flow) |  | Ideal weather curve where pump does not modulate so flow is constant (and thus DT across emitters will vary slightly)
Linear (const flow) |  | Linear best fit to above, offfset so that flow temp is never less than 'ideal flow temp'
Lizzie (const flow)
Linear (const flow) + 2C
Lizzie+2C
Add your own

## Compensation
Temp | Load | None | Ideal (const DT) | Ideal (const flow) | Linear (const flow) | Lizzie (const flow) | Linear (const flow) + 2C | Lizzie+2C | Add your own | Design Ambient | -2 | Linear bestfit | variance to ideal | Linear kissing variance to ideal
-10 | 13.4783 | 65 | 76.3568 | 77.2264 | 79.7636 | 79.7636 | 81.7636 | 81.7636 | 65 | Design Flow | 65 | 78.7425 | 1.5162 | 2.5373
-9 | 13.0435 | 65 | 74.978 | 75.7389 | 78.0161 | 78.0161 | 80.0161 | 80.0161 | 65 | Target temperature | 21 | 76.995 | 1.2561 | 2.2772
-8 | 12.6087 | 65 | 73.5886 | 74.2407 | 76.2685 | 76.2685 | 78.2685 | 78.2685 | 65 | Emitter coeff | 1.3 | 75.2474 | 1.0067 | 2.0278
-7 | 12.1739 | 65 | 72.188 | 72.7315 | 74.521 | 74.521 | 76.521 | 76.521 | 65 | Load @ Design Ambient | 10 | 73.4999 | 0.76839 | 1.7895
-6 | 11.7391 | 65 | 70.7759 | 71.2106 | 72.7734 | 72.7734 | 74.7734 | 74.7734 | 65 | Max Heating temp | 16 | 71.7523 | 0.54168 | 1.5628
-5 | 11.3043 | 65 | 69.3516 | 69.6777 | 71.0259 | 71.0259 | 73.0259 | 73.0259 | 65 | Emitter deltaT | 5 | 70.0048 | 0.3271 | 1.3482
-4 | 10.8696 | 65 | 67.9146 | 68.132 | 69.2783 | 69.2783 | 71.2783 | 71.2783 | 65 | Lizzie floor | 37 | 68.2572 | 0.12521 | 1.1463
-3 | 10.4348 | 65 | 66.4643 | 66.573 | 67.5308 | 67.5308 | 69.5308 | 69.5308 | 65 | Linear Intercept (const DT) | 61.4844 | 66.5097 | -0.063341 | 0.95778
-2 | 10 | 65 | 65 | 65 | 65.7832 | 65.7832 | 67.7832 | 67.7832 | 65 | Linear slope (const DT) | -1.6389 | 64.7621 | -0.23788 | 0.78324
-1 | 9.5652 | 65 | 63.5209 | 63.4122 | 64.0357 | 64.0357 | 66.0357 | 66.0357 | 65 | Linear Intercept const flow | 61.267 | 63.0146 | -0.39764 | 0.62348
0 | 9.1304 | 65 | 62.0262 | 61.8088 | 62.2881 | 62.2881 | 64.2881 | 64.2881 | 65 | Linear Slope const flow | -1.7476 | 61.267 | -0.5418 | 0.47931
1 | 8.6957 | 65 | 60.515 | 60.1889 | 60.5406 | 60.5406 | 62.5406 | 62.5406 | 65 |  |  | 59.5195 | -0.66944 | 0.35167
2 | 8.2609 | 65 | 58.9862 | 58.5515 | 58.793 | 58.793 | 60.793 | 60.793 | 65 |  |  | 57.7719 | -0.77954 | 0.24158
3 | 7.8261 | 65 | 57.4388 | 56.8953 | 57.0455 | 57.0455 | 59.0455 | 59.0455 | 65 |  |  | 56.0244 | -0.87094 | 0.15018
4 | 7.3913 | 65 | 55.8714 | 55.2192 | 55.2979 | 55.2979 | 57.2979 | 57.2979 | 65 |  |  | 54.2768 | -0.94236 | 0.078753
5 | 6.9565 | 65 | 54.2825 | 53.5216 | 53.5504 | 53.5504 | 55.5504 | 55.5504 | 65 |  |  | 52.5293 | -0.99235 | 0.028765
6 | 6.5217 | 65 | 52.6705 | 51.801 | 51.8028 | 51.8028 | 53.8028 | 53.8028 | 65 |  |  | 50.7817 | -1.0192 | 0.0018765
7 | 6.087 | 65 | 51.0336 | 50.0553 | 50.0553 | 50.0553 | 52.0553 | 52.0553 | 65 |  |  | 49.0342 | -1.0211 | 0
8 | 5.6522 | 65 | 49.3693 | 48.2824 | 48.3077 | 48.3077 | 50.3077 | 50.3077 | 65 |  |  | 47.2866 | -0.99576 | 0.025356
9 | 5.2174 | 65 | 47.6753 | 46.4796 | 46.5602 | 46.5602 | 48.5602 | 48.5602 | 65 |  |  | 45.5391 | -0.94057 | 0.080552
10 | 4.7826 | 65 | 45.9483 | 44.644 | 44.8126 | 44.8126 | 46.8126 | 46.8126 | 65 |  |  | 43.7915 | -0.85243 | 0.16868
11 | 4.3478 | 65 | 44.1846 | 42.7716 | 43.0651 | 43.0651 | 45.0651 | 45.0651 | 65 |  |  | 42.044 | -0.72763 | 0.29349
12 | 3.913 | 65 | 42.3797 | 40.858 | 41.3175 | 41.3175 | 43.3175 | 43.3175 | 65 |  |  | 40.2964 | -0.56158 | 0.45954
13 | 3.4783 | 65 | 40.5278 | 38.8974 | 39.57 | 39.57 | 41.57 | 41.57 | 65 |  |  | 38.5489 | -0.34854 | 0.67258
14 | 3.0435 | 65 | 38.6216 | 36.8825 | 37.8224 | 37.8224 | 39.8224 | 39.8224 | 65 |  |  | 36.8013 | -0.08114 | 0.93998
15 | 2.6087 | 65 | 36.6512 | 34.8034 | 36.0749 | 37 | 38.0749 | 38.0749 | 65 |  |  | 35.0538 | 0.2504 | 1.2715
16 | 2.1739 | 65 | 34.6031 | 32.6466 | 34.3273 | 37 | 36.3273 | 37 | 65 |  |  | 33.3062 | 0.65961 | 1.6807
17 | 1.7391 | 65 | 32.4576 | 30.3924 | 32.5798 | 37 | 34.5798 | 37 | 65 |  |  | 31.5587 | 1.1663 | 2.1874
18 | 1.3043 | 65 | 30.183 | 28.0091 | 30.8322 | 37 | 32.8322 | 37 | 65 |  |  | 29.8111 | 1.802 | 2.8231
19 | 0.86957 | 65 | 27.7225 | 25.4399 | 29.0847 | 37 | 31.0847 | 37 | 65 |  |  | 28.0636 | 2.6237 | 3.6448
20 | 0.43478 | 65 | 24.9443 | 22.553 | 27.3371 | 37 | 29.3371 | 37 | 65

## CoP data
COP vs Flow Temp and Ambient
COP (LG 12kW) | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65
-20 | 2.34 | 2.34 | 2.13 | 1.91 | 1.7 | 1.49 | - | - | -
-15 | 2.55 | 2.55 | 2.4 | 2.25 | 2.1 | 1.95 | 1.8 | - | -
-7 | 3.15 | 3.15 | 3 | 2.85 | 2.7 | 2.55 | 2.4 | 2.25 | -
-4 | 3.36 | 3.36 | 3.17 | 2.97 | 2.78 | 2.59 | 2.39 | 2.2 | 2.05 | < These figures are the averages of the figures below
-2 | 3.47 | 3.47 | 3.28 | 3.09 | 2.9 | 2.71 | 2.53 | 2.34 | 2.15 | This is a chart of these figures->
2 | 3.69 | 3.69 | 3.5 | 3.31 | 3.12 | 2.93 | 2.73 | 2.54 | 2.35
7 | 4.93 | 4.93 | 4.6 | 4.27 | 3.93 | 3.6 | 2.8 | 2.6 | 2.6
10 | 5.22 | 5.22 | 4.87 | 4.51 | 4.16 | 3.81 | 3.46 | 3.1 | 2.75
15 | 5.99 | 5.99 | 5.56 | 5.13 | 4.71 | 4.28 | 3.85 | 3.43 | 3
18 | 6.29 | 6.29 | 5.84 | 5.39 | 4.94 | 4.49 | 4.05 | 3.6 | 3.15
20 | 6.49 | 6.49 | 6.02 | 5.56 | 5.1 | 4.64 | 4.17 | 3.71 | 3.25
35 | 7.98 | 7.98 | 7.41 | 6.84 | 6.28 | 5.71 | 5.14 | 4.57 | 4

## CET - Mean
MEAN CET FOR 2022 12 MONTHS HAVE DATA 01/01/2023 11:10:36
2022 | 0.8 | 3.1 | 2.3 | 1.3 | 1.9 | 0.8 | 2.2 | 2.9 | 0.9 | 2.3 | 2.7 | -1.1
2022 | 4.7 | 6.9 | 8 | 9.2 | 13.1 | 14.9 | 18.2 | 18.7 | 14.4 | 12.8 | 9.2 | 3.4
1 | 12.7 | 8.4 | 5.8 | 3.9 | 10.3 | 12 | 14.4 | 18.6 | 17.5 | 14 | 12.2 | 3.8
2 | 9.9 | 9.6 | 5.7 | 4.3 | 12 | 12.4 | 14.9 | 21 | 18.2 | 13.5 | 9.9 | 4
3 | 8.7 | 8.7 | 7.5 | 3.8 | 11.7 | 14.7 | 14.3 | 20.8 | 18.1 | 11.4 | 10.1 | 4.8
4 | 3.2 | 4.9 | 6.6 | 8.8 | 12.2 | 13.1 | 14.7 | 17 | 19.4 | 13.9 | 7.2 | 3.6
5 | 3 | 5.6 | 5.3 | 10.4 | 12.1 | 10.9 | 14.6 | 15.2 | 18.6 | 15.1 | 8.4 | 5.3
6 | 1.3 | 6.6 | 5.1 | 9.9 | 13.1 | 13.1 | 16.4 | 14.7 | 17.5 | 12.6 | 8.8 | 3.5
7 | 3.4 | 5.9 | 4.3 | 8.4 | 13.4 | 14.8 | 17.9 | 16.6 | 17.4 | 14.3 | 10.7 | 1.3
8 | 5 | 7.8 | 5.4 | 5.1 | 13.1 | 16 | 17.8 | 19 | 16 | 11.3 | 12 | -1.1
9 | 4.8 | 9 | 8.1 | 5.3 | 13.3 | 14.3 | 17.9 | 18.8 | 16.4 | 10.7 | 11.2 | -0.8
10 | 5.4 | 5.7 | 11.3 | 5.2 | 15 | 16.8 | 19 | 20.5 | 16.5 | 11 | 11.8 | -0.5
11 | 6.8 | 4.1 | 9.9 | 10 | 13 | 15.7 | 20.6 | 21.9 | 16.6 | 8.7 | 14.3 | -1.4
12 | 3.6 | 5.2 | 9.3 | 11.2 | 11.2 | 14.5 | 21.6 | 23 | 18.1 | 9.6 | 11.9 | -1.9
13 | 3.9 | 7.5 | 9.8 | 12.6 | 13.6 | 13.9 | 18.5 | 23.4 | 14.7 | 11.7 | 12 | -2.3
14 | 2.1 | 6.6 | 7.8 | 10.8 | 13.9 | 13.9 | 15.8 | 23.6 | 14.2 | 11.1 | 10.6 | -2.5
15 | 1.7 | 7 | 7.9 | 13.4 | 15.1 | 15.6 | 16 | 21.4 | 13.4 | 11.9 | 10.2 | -4.4
16 | 3.9 | 10.5 | 8.3 | 13.1 | 16 | 17.5 | 17.3 | 18.7 | 11.8 | 11.6 | 8.3 | -2.6
17 | 4.6 | 8.3 | 7.3 | 12.9 | 16.2 | 21 | 21.9 | 17.7 | 9.9 | 14.1 | 9.1 | -1.3
18 | 2.1 | 6.7 | 8.5 | 10.7 | 15 | 15.1 | 24.4 | 18.9 | 12.6 | 10.2 | 9.1 | 5.4
19 | 3.6 | 6.2 | 9.7 | 9 | 14.5 | 12.4 | 28.1 | 18 | 13.3 | 11.9 | 7.7 | 7
20 | 2.2 | 7.1 | 6.6 | 11.2 | 13.7 | 13.7 | 19.8 | 17.7 | 13.3 | 13.3 | 7.4 | 8.1
21 | 1.2 | 7.2 | 6.5 | 11.1 | 13.6 | 15.1 | 17.1 | 17.3 | 15 | 13.3 | 5.1 | 6.8
22 | 3.5 | 8.2 | 11.2 | 10.9 | 14.6 | 16.9 | 18 | 17 | 14.3 | 14 | 6.9 | 6.5
23 | 4.5 | 6.6 | 11.2 | 11.2 | 13.2 | 17.2 | 17.6 | 19.9 | 14.2 | 14.8 | 7.7 | 7.8
24 | 3.7 | 4.8 | 10.2 | 11.3 | 12.4 | 17.4 | 21.1 | 20.6 | 11.8 | 13 | 8.3 | 7.2
25 | 3 | 6.4 | 10.8 | 9.1 | 12.9 | 15.3 | 18 | 17.2 | 10 | 13.4 | 8.2 | 8
26 | 5 | 5.8 | 10.7 | 9.3 | 13.9 | 14.7 | 16.3 | 15.9 | 12.3 | 15 | 9.1 | 4.2
27 | 7.9 | 6.5 | 9.6 | 6.8 | 13.1 | 14.1 | 15.3 | 17.8 | 10.9 | 15 | 10.1 | 5.5
28 | 6.1 | 7.6 | 9.7 | 8.1 | 11.5 | 13.8 | 17 | 17.1 | 9.5 | 15.4 | 7.7 | 7.5
29 | 8.2 | -99.9 | 8.3 | 8.6 | 10.8 | 16.1 | 18.6 | 17.2 | 11.4 | 14.9 | 3.7 | 7.4
30 | 4.1 | -99.9 | 5.9 | 8.4 | 9.9 | 15.2 | 18.1 | 16.3 | 10.6 | 14.1 | 4.8 | 7.9
31 | 5.4 | -99.9 | 3.2 | -99.9 | 10.8 | -99.9 | 20.4 | 17.2 | -99.9 | 13.4 | -99.9 | 9.3

## Mitsubishi COP
Ambient/Flow Temp | 25 | 35 | 40 | 45 | 50 | 55 | 60
-25 |  | 1.7125 | 1.55 | 1.4
-20 |  | 2.3 | 2.0625 | 1.85
-15 |  | 2.525 | 2.2625 | 2.0125 | 1.725 | 1.475
-10 | 2.9625 | 2.725 | 2.4875 | 2.2625 | 1.9375 | 1.625
-7 | 3.1625 | 2.925 | 2.6875 | 2.4625 | 2.15 | 1.85
2 | 3.9675 | 3.5275 | 3.0875 | 2.695 | 2.3375 | 2.02 | 1.7225
7 | 5.1125 | 4.625 | 4.1375 | 3.6625 | 3.2375 | 2.825 | 2.3125
12 | 6.3625 | 5.85 | 5.3375 | 4.8375 | 4.2 | 3.575 | 3.0275
15 | 7.075 | 6.45 | 5.825 | 5.2375 | 4.55 | 3.8875 | 3.28
20 | 9.15 | 8.1125 | 7.075 | 6.075 | 5.2375 | 4.45 | 3.8
max | 25 | 35 | 40 | 45 | 50 | 55 | 60
-25 | - | 1.7 | 1.55 | 1.4 | - | - | -
-20 | - | 2.35 | 2.1 | 1.9 | - | - | -
-15 | - | 2.55 | 2.3 | 2.05 | 1.75 | 1.5 | -
-10 | 2.8 | 2.6 | 2.4 | 2.25 | 1.9 | 1.55 | -
-7 | 2.95 | 2.8 | 2.65 | 2.5 | 2.2 | 1.9 | -
2 | 3.54 | 3.17 | 2.8 | 2.49 | 2.2 | 1.93 | 1.69
7 | 5.05 | 4.55 | 4.05 | 3.55 | 3.1 | 2.7 | 2.4
12 | 5.65 | 5.25 | 4.85 | 4.5 | 3.95 | 3.45 | 2.96
15 | 5.65 | 5.35 | 5.05 | 4.8 | 4.25 | 3.75 | 3.22
20 | 7.8 | 6.95 | 6.1 | 5.3 | 4.65 | 4.05 | 3.55
Nominal
-25 | - | 1.7 | 1.55 | 1.4 | - | - | -
-20 | - | 2.35 | 2.1 | 1.9 | - | - | -
-15 | - | 2.55 | 2.3 | 2.05 | 1.75 | 1.5 | -
-10 | 3 | 2.75 | 2.5 | 2.25 | 1.9 | 1.55 | -
-7 | 3.25 | 3 | 2.75 | 2.5 | 2.2 | 1.9 | -
2 | 3.83 | 3.44 | 3.05 | 2.74 | 2.3 | 1.95 | 1.7
7 | 5.2 | 4.7 | 4.2 | 3.7 | 3.35 | 3 | 2.4
12 | 6.65 | 6.05 | 5.45 | 4.85 | 4.2 | 3.55 | 3
15 | 7.55 | 6.85 | 6.15 | 5.5 | 4.75 | 4 | 3.35
20 | 9.7 | 8.65 | 7.6 | 6.6 | 5.65 | 4.75 | 3.95
Mid
-25 | - | 1.75 | 1.6 | 1.45 | - | - | -
-20 | - | 2.25 | 2.05 | 1.85 | - | - | -
-15 | - | 2.5 | 2.25 | 2 | 1.75 | 1.5 | -
-10 | 3.05 | 2.8 | 2.55 | 2.3 | 2 | 1.7 | -
-7 | 3.3 | 3.05 | 2.8 | 2.55 | 2.2 | 1.9 | -
2 | 4.25 | 3.75 | 3.25 | 2.8 | 2.45 | 2.1 | 1.8
7 | 5.25 | 4.8 | 4.35 | 3.9 | 3.45 | 3 | 2.4
12 | 6.85 | 6.25 | 5.65 | 5.05 | 4.35 | 3.65 | 3.1
15 | 7.8 | 7.05 | 6.3 | 5.6 | 4.8 | 4.05 | 3.4
20 | 9.85 | 8.75 | 7.65 | 6.6 | 5.65 | 4.75 | 4
Min
-25 | - | 1.7 | 1.5 | 1.35 | - | - | -
-20 | - | 2.25 | 2 | 1.75 | - | - | -
-15 | - | 2.5 | 2.2 | 1.95 | 1.65 | 1.4 | -
-10 | 3 | 2.75 | 2.5 | 2.25 | 1.95 | 1.7 | -
-7 | 3.15 | 2.85 | 2.55 | 2.3 | 2 | 1.7 | -
2 | 4.25 | 3.75 | 3.25 | 2.75 | 2.4 | 2.1 | 1.7
7 | 4.95 | 4.45 | 3.95 | 3.5 | 3.05 | 2.6 | 2.05
12 | 6.3 | 5.85 | 5.4 | 4.95 | 4.3 | 3.65 | 3.05
15 | 7.3 | 6.55 | 5.8 | 5.05 | 4.4 | 3.75 | 3.15
20 | 9.25 | 8.1 | 6.95 | 5.8 | 5 | 4.25 | 3.7

## LG
| 30 |  | 35 |  | 40 |  | 45 |  | 50 |  | 55 |  | 60 |  | 65 |  | COP | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65
-20 | 10.13 | 2.34 | 10 | 2.13 | 9.88 | 1.91 | 9.75 | 1.7 | 9.63 | 1.49 | - | - | - | - | - | - | -20 | 2.34 | 2.13 | 1.91 | 1.7 | 1.49 | - | - | -
-15 | 11.5 | 2.55 | 11.5 | 2.4 | 11.5 | 2.25 | 11.5 | 2.1 | 11.5 | 1.95 | 11.5 | 1.8 | - | - | - | - | -15 | 2.55 | 2.4 | 2.25 | 2.1 | 1.95 | 1.8 | - | -
-7 | 12 | 3.15 | 12 | 3 | 12 | 2.85 | 12 | 2.7 | 12 | 2.55 | 12 | 2.4 | 12 | 2.25 | - | - | -7 | 3.15 | 3 | 2.85 | 2.7 | 2.55 | 2.4 | 2.25 | -
-4 | 12 | 3.36 | 12 | 3.17 | 12 | 2.97 | 12 | 2.78 | 12 | 2.59 | 12 | 2.39 | 12 | 2.2 | 12 | 2.05 | -4 | 3.36 | 3.17 | 2.97 | 2.78 | 2.59 | 2.39 | 2.2 | 2.05
-2 | 12 | 3.47 | 12 | 3.28 | 12 | 3.09 | 12 | 2.9 | 12 | 2.71 | 12 | 2.53 | 12 | 2.34 | 12 | 2.15 | -2 | 3.47 | 3.28 | 3.09 | 2.9 | 2.71 | 2.53 | 2.34 | 2.15
2 | 12 | 3.69 | 12 | 3.5 | 12 | 3.31 | 12 | 3.12 | 12 | 2.93 | 12 | 2.73 | 12 | 2.54 | 12 | 2.35 | 2 | 3.69 | 3.5 | 3.31 | 3.12 | 2.93 | 2.73 | 2.54 | 2.35
7 | 12 | 4.93 | 12 | 4.6 | 12 | 4.27 | 12 | 3.93 | 12 | 3.6 | 12 | 2.8 | 12 | 2.6 | 12 | 2.6 | 7 | 4.93 | 4.6 | 4.27 | 3.93 | 3.6 | 2.8 | 2.6 | 2.6
10 | 12 | 5.22 | 12 | 4.87 | 12 | 4.51 | 12 | 4.16 | 12 | 3.81 | 12 | 3.46 | 12 | 3.1 | 12 | 2.75 | 10 | 5.22 | 4.87 | 4.51 | 4.16 | 3.81 | 3.46 | 3.1 | 2.75
15 | 12 | 5.99 | 12 | 5.56 | 12 | 5.13 | 12 | 4.71 | 12 | 4.28 | 12 | 3.85 | 12 | 3.43 | 12 | 3 | 15 | 5.99 | 5.56 | 5.13 | 4.71 | 4.28 | 3.85 | 3.43 | 3
18 | 12 | 6.29 | 12 | 5.84 | 12 | 5.39 | 12 | 4.94 | 12 | 4.49 | 12 | 4.05 | 12 | 3.6 | 12 | 3.15 | 18 | 6.29 | 5.84 | 5.39 | 4.94 | 4.49 | 4.05 | 3.6 | 3.15
20 | 12 | 6.49 | 12 | 6.02 | 12 | 5.56 | 12 | 5.1 | 12 | 4.64 | 12 | 4.17 | 12 | 3.71 | 12 | 3.25 | 20 | 6.49 | 6.02 | 5.56 | 5.1 | 4.64 | 4.17 | 3.71 | 3.25
35 | 12 | 7.98 | 12 | 7.41 | 12 | 6.84 | 12 | 6.28 | 12 | 5.71 | 12 | 5.14 | 12 | 4.57 | 12 | 4 | 35 | 7.98 | 7.41 | 6.84 | 6.28 | 5.71 | 5.14 | 4.57 | 4

## Samsung HT
Samsung 12kW HT heat pump
| 25 |  | 30 |  | 35 |  | 40 |  | 45 |  | 50 |  | 55 |  | 60 |  | 65 |  | 70 |  |  | COP
TAMB | HC(kW) | PI(kW) | HC(kW) | PI(kW) | HC(kW) | PI(kW) | HC(kW) | PI(kW) | HC(kW) | PI(kW) | HC(kW) | PI(kW) | HC(kW) | PI(kW) | HC(kW) | PI(kW) | HC(kW) | PI(kW) | HC(kW) | PI(kW) |  | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70
-15 | 12 | 4.23 | 12 | 4.53 | 12 | 4.83 | 12 | 5.23 | 12 | 5.63 | 12 | 5.93 | 12 | 6.28 | 12 | 6.57 | 11.53 | 6.66 | 11 | 6.67 | -15 | 2.8369 | 2.649 | 2.4845 | 2.2945 | 2.1314 | 2.0236 | 1.9108 | 1.8265 | 1.7312 | 1.6492
-10 | 11.43 | 3.96 | 11.96 | 4.43 | 11.94 | 4.77 | 11.94 | 5.14 | 11.94 | 5.57 | 11.94 | 5.9 | 11.94 | 6.15 | 11.72 | 6.33 | 10.94 | 6.26 | 10.71 | 6.42 | -10 | 2.8864 | 2.6998 | 2.5031 | 2.323 | 2.1436 | 2.0237 | 1.9415 | 1.8515 | 1.7476 | 1.6682
-7 | 11.93 | 3.85 | 11.85 | 4.1 | 11.95 | 4.47 | 11.95 | 4.86 | 11.95 | 5.32 | 11.95 | 5.75 | 11.95 | 6.07 | 11.65 | 6.13 | 11.18 | 6.16 | 11.06 | 6.4 | -7 | 3.0987 | 2.8902 | 2.6734 | 2.4588 | 2.2462 | 2.0783 | 1.9687 | 1.9005 | 1.8149 | 1.7281
-2 | 11.26 | 3.45 | 11.53 | 3.79 | 11.97 | 4.23 | 11.97 | 4.62 | 11.97 | 5.1 | 11.97 | 5.26 | 11.97 | 5.37 | 12.62 | 6.1 | 11.54 | 6.17 | 11.45 | 6.4 | -2 | 3.2638 | 3.0422 | 2.8298 | 2.5909 | 2.3471 | 2.2757 | 2.2291 | 2.0689 | 1.8703 | 1.7891
2 | 10.63 | 2.5 | 10.81 | 2.83 | 11.96 | 3.53 | 11.96 | 3.9 | 11.96 | 4.36 | 11.96 | 4.62 | 11.96 | 4.84 | 12.55 | 5.47 | 12.37 | 5.99 | 11.92 | 6.02 | 2 | 4.252 | 3.8198 | 3.3881 | 3.0667 | 2.7431 | 2.5887 | 2.4711 | 2.2943 | 2.0651 | 1.9801
7 | 12 | 1.9 | 12 | 2.1 | 12 | 2.35 | 12 | 2.64 | 12 | 3 | 12 | 3.26 | 12 | 3.53 | 13.66 | 4.46 | 14.49 | 5.35 | 15.05 | 6.17 | 7 | 6.3158 | 5.7143 | 5.1064 | 4.5455 | 4 | 3.681 | 3.3994 | 3.0628 | 2.7084 | 2.4392
12 | 13.38 | 1.73 | 13.42 | 1.98 | 13.47 | 2.3 | 13.52 | 2.64 | 13.57 | 3.08 | 13.62 | 3.48 | 13.67 | 3.83 | 14.35 | 4.4 | 15.12 | 5.25 | 15.65 | 6.01 | 12 | 7.7341 | 6.7778 | 5.8565 | 5.1212 | 4.4058 | 3.9138 | 3.5692 | 3.2614 | 2.88 | 2.604
15 | 13.64 | 1.61 | 13.72 | 1.85 | 13.8 | 2.18 | 13.88 | 2.51 | 13.96 | 2.94 | 14.04 | 3.35 | 14.12 | 3.7 | 14.78 | 4.25 | 15.5 | 5.07 | 16.01 | 5.78 | 15 | 8.472 | 7.4162 | 6.3303 | 5.5299 | 4.7483 | 4.191 | 3.8162 | 3.4776 | 3.0572 | 2.7699
20 | 14.09 | 1.45 | 14.22 | 1.67 | 14.35 | 1.96 | 14.48 | 2.21 | 14.61 | 2.59 | 14.74 | 3.04 | 14.87 | 3.47 | 15.47 | 3.98 | 16.14 | 4.77 | 16.62 | 5.71 | 20 | 9.7172 | 8.515 | 7.3214 | 6.552 | 5.6409 | 4.8487 | 4.2853 | 3.8869 | 3.3836 | 2.9107

## DHW
This is what you need to do.
The overall heat transfer coefficient (h) for coils in water is 0.4 - 0.57 kW/m2.k. Source - Perry's Chemical Engineering Handbook
If you have a 22mm coil, 10metres long, thats a heat transfer area of 0.69m2.
The heat transferred will be given by
Q = h * A * DeltaT.
Delta T is a bit tricky, as you need to a) average it, and b) iterate it.
As has been pointed out, to heat 20l/min by 20C needs 27kW.
Doing it the other way round, A delta T of 30C on this coil, will transfer about 10kW, So that would heat your 20 l/min by about 7.5C.
Which isn't much!
Heat transfer rate | 0.4 | kW/sqmK
Volume | 140 | l
Initial temperature | 10 | C
Final temperature | 48 | C
Area | 0.8
Flow | 65
Water SHC | 4.2 | kJ/kgK
Max power | 12 | kW
Idela DT | 37.5
Outside temp | 12
Min | Temp | Power (kW) | Energy (kJ) | Temp rise
1 | 10 | 12 | 720 | 1.2245
2 | 11.2245 | 12 | 720 | 1.2245
3 | 12.449 | 12 | 720 | 1.2245
4 | 13.6735 | 12 | 720 | 1.2245
5 | 14.898 | 12 | 720 | 1.2245
6 | 16.1224 | 12 | 720 | 1.2245
7 | 17.3469 | 12 | 720 | 1.2245
8 | 18.5714 | 12 | 720 | 1.2245
9 | 19.7959 | 12 | 720 | 1.2245
10 | 21.0204 | 12 | 720 | 1.2245
11 | 22.2449 | 12 | 720 | 1.2245
12 | 23.4694 | 12 | 720 | 1.2245
13 | 24.6939 | 12 | 720 | 1.2245
14 | 25.9184 | 12 | 720 | 1.2245
15 | 27.1429 | 12 | 720 | 1.2245
16 | 28.3673 | 11.7224 | 703.3469 | 1.1962
17 | 29.5635 | 11.3397 | 680.3805 | 1.1571
18 | 30.7206 | 10.9694 | 658.164 | 1.1193
19 | 31.84 | 10.6112 | 636.6729 | 1.0828
20 | 32.9227 | 10.2647 | 615.8836 | 1.0474
21 | 33.9701 | 9.9296 | 595.7731 | 1.0132
22 | 34.9834 | 9.6053 | 576.3193 | 0.98013
23 | 35.9635 | 9.2917 | 557.5007 | 0.94813
24 | 36.9116 | 8.9883 | 539.2966 | 0.91717
25 | 37.8288 | 8.6948 | 521.6869 | 0.88722
26 | 38.716 | 8.4109 | 504.6523 | 0.85825
27 | 39.5743 | 8.1362 | 488.1738 | 0.83023
28 | 40.4045 | 7.8706 | 472.2334 | 0.80312
29 | 41.2076 | 7.6136 | 456.8136 | 0.77689
30 | 41.9845 | 7.365 | 441.8972 | 0.75153
31 | 42.736 | 7.1245 | 427.4679 | 0.72699
32 | 43.463 | 6.8918 | 413.5098 | 0.70325
33 | 44.1663 | 6.6668 | 400.0074 | 0.68028
34 | 44.8466 | 6.4491 | 386.946 | 0.65807
35 | 45.5046 | 6.2385 | 374.311 | 0.63658
36 | 46.1412 | 6.0348 | 362.0886 | 0.6158
37 | 46.757 | 5.8378 | 350.2653 | 0.59569
38 | 47.3527 | 5.6471 | 338.8281 | 0.57624
39 | 47.9289 | 5.4627 | 327.7643 | 0.55742
40 | 48.4864 | 5.2844 | 317.0618 | 0.53922
41 | 49.0256 | 5.1118 | 306.7087 | 0.52161
42 | 49.5472 | 4.9449 | 296.6938 | 0.50458
43 | 50.0518 | 4.7834 | 287.0058 | 0.48811
44 | 50.5399 | 4.6272 | 277.6342 | 0.47217
45 | 51.0121 | 4.4761 | 268.5686 | 0.45675
46 | 51.4688 | 4.33 | 259.799 | 0.44184
47 | 51.9106 | 4.1886 | 251.3158 | 0.42741
48 | 52.338 | 4.0518 | 243.1095 | 0.41345
49 | 52.7515 | 3.9195 | 235.1713 | 0.39995
50 | 53.1514 | 3.7915 | 227.4922 | 0.38689
51 | 53.5383 | 3.6677 | 220.0639 | 0.37426
52 | 53.9126 | 3.548 | 212.8781 | 0.36204
53 | 54.2746 | 3.4321 | 205.927 | 0.35022
54 | 54.6249 | 3.32 | 199.2028 | 0.33878
55 | 54.9636 | 3.2116 | 192.6983 | 0.32772
56 | 55.2914 | 3.1068 | 186.4061 | 0.31702
57 | 55.6084 | 3.0053 | 180.3193 | 0.30667
58 | 55.915 | 2.9072 | 174.4314 | 0.29665
59 | 56.2117 | 2.8123 | 168.7357 | 0.28697
60 | 56.4987 | 2.7204 | 163.2259 | 0.2776
61 | 56.7762 | 2.6316 | 157.8961 | 0.26853
62 | 57.0448 | 2.5457 | 152.7403 | 0.25976
63 | 57.3045 | 2.4625 | 147.7529 | 0.25128
64 | 57.5558 | 2.3821 | 142.9283 | 0.24308
65 | 57.7989 | 2.3044 | 138.2612 | 0.23514
66 | 58.034 | 2.2291 | 133.7466 | 0.22746
67 | 58.2615 | 2.1563 | 129.3793 | 0.22003
68 | 58.4815 | 2.0859 | 125.1547 | 0.21285
69 | 58.6944 | 2.0178 | 121.068 | 0.2059
70 | 58.9003 | 1.9519 | 117.1148 | 0.19917
71 | 59.0994 | 1.8882 | 113.2906 | 0.19267
72 | 59.2921 | 1.8265 | 109.5913 | 0.18638
73 | 59.4785 | 1.7669 | 106.0129 | 0.18029
74 | 59.6588 | 1.7092 | 102.5512 | 0.17441
75 | 59.8332 | 1.6534 | 99.2026 | 0.16871
76 | 60.0019 | 1.5994 | 95.9633 | 0.1632
77 | 60.1651 | 1.5472 | 92.8298 | 0.15787
78 | 60.323 | 1.4966 | 89.7987 | 0.15272
79 | 60.4757 | 1.4478 | 86.8665 | 0.14773
80 | 60.6234 | 1.4005 | 84.03 | 0.14291
81 | 60.7663 | 1.3548 | 81.2862 | 0.13824
82 | 60.9046 | 1.3105 | 78.6319 | 0.13373
83 | 61.0383 | 1.2677 | 76.0643 | 0.12936
84 | 61.1677 | 1.2263 | 73.5806 | 0.12514
85 | 61.2928 | 1.1863 | 71.178 | 0.12105
86 | 61.4139 | 1.1476 | 68.8538 | 0.1171
87 | 61.531 | 1.1101 | 66.6055 | 0.11327
88 | 61.6442 | 1.0738 | 64.4306 | 0.10958
89 | 61.7538 | 1.0388 | 62.3268 | 0.106
90 | 61.8598 | 1.0049 | 60.2916 | 0.10254
91 | 61.9623 | 0.97205 | 58.3229 | 0.099189
92 | 62.0615 | 0.94031 | 56.4185 | 0.09595
93 | 62.1575 | 0.9096 | 54.5763 | 0.092817
94 | 62.2503 | 0.8799 | 52.7942 | 0.089786
95 | 62.3401 | 0.85117 | 51.0703 | 0.086854
96 | 62.4269 | 0.82338 | 49.4027 | 0.084018
97 | 62.511 | 0.79649 | 47.7895 | 0.081275
98 | 62.5922 | 0.77048 | 46.2291 | 0.078621
99 | 62.6709 | 0.74533 | 44.7195 | 0.076054
100 | 62.7469 | 0.72099 | 43.2593 | 0.07357
101 | 62.8205 | 0.69745 | 41.8468 | 0.071168
102 | 62.8916 | 0.67467 | 40.4803 | 0.068844
103 | 62.9605 | 0.65264 | 39.1585 | 0.066596
104 | 63.0271 | 0.63133 | 37.8799 | 0.064422
105 | 63.0915 | 0.61072 | 36.643 | 0.062318
106 | 63.1538 | 0.59077 | 35.4465 | 0.060283
107 | 63.2141 | 0.57148 | 34.289 | 0.058315
108 | 63.2724 | 0.55282 | 33.1694 | 0.056411
109 | 63.3288 | 0.53477 | 32.0863 | 0.054569
110 | 63.3834 | 0.51731 | 31.0386 | 0.052787
111 | 63.4362 | 0.50042 | 30.0251 | 0.051063
112 | 63.4873 | 0.48408 | 29.0447 | 0.049396
113 | 63.5367 | 0.46827 | 28.0963 | 0.047783
114 | 63.5844 | 0.45298 | 27.1789 | 0.046223
115 | 63.6307 | 0.43819 | 26.2914 | 0.044713
116 | 63.6754 | 0.42388 | 25.4329 | 0.043253
117 | 63.7186 | 0.41004 | 24.6024 | 0.041841
118 | 63.7605 | 0.39665 | 23.7991 | 0.040475
119 | 63.8009 | 0.3837 | 23.022 | 0.039153
120 | 63.8401 | 0.37117 | 22.2702 | 0.037875
121 | 63.878 | 0.35905 | 21.543 | 0.036638
122 | 63.9146 | 0.34733 | 20.8396 | 0.035441
123 | 63.95 | 0.33599 | 20.1591 | 0.034284
124 | 63.9843 | 0.32501 | 19.5009 | 0.033165
125 | 64.0175 | 0.3144 | 18.8641 | 0.032082
126 | 64.0496 | 0.30414 | 18.2481 | 0.031034
127 | 64.0806 | 0.2942 | 17.6523 | 0.030021
128 | 64.1106 | 0.2846 | 17.0759 | 0.029041
129 | 64.1397 | 0.2753 | 16.5183 | 0.028092
130 | 64.1678 | 0.26632 | 15.9789 | 0.027175
131 | 64.1949 | 0.25762 | 15.4572 | 0.026288
132 | 64.2212 | 0.24921 | 14.9524 | 0.025429
133 | 64.2467 | 0.24107 | 14.4642 | 0.024599
134 | 64.2713 | 0.2332 | 13.9919 | 0.023796
135 | 64.2951 | 0.22558 | 13.535 | 0.023019
136 | 64.3181 | 0.21822 | 13.0931 | 0.022267
137 | 64.3403 | 0.21109 | 12.6655 | 0.02154
138 | 64.3619 | 0.2042 | 12.252 | 0.020837
139 | 64.3827 | 0.19753 | 11.8519 | 0.020156
140 | 64.4029 | 0.19108 | 11.4649 | 0.019498
141 | 64.4224 | 0.18484 | 11.0905 | 0.018861
142 | 64.4412 | 0.17881 | 10.7284 | 0.018246
143 | 64.4595 | 0.17297 | 10.3781 | 0.01765
144 | 64.4771 | 0.16732 | 10.0392 | 0.017073
145 | 64.4942 | 0.16186 | 9.7114 | 0.016516
146 | 64.5107 | 0.15657 | 9.3943 | 0.015977
147 | 64.5267 | 0.15146 | 9.0875 | 0.015455
148 | 64.5421 | 0.14651 | 8.7908 | 0.01495
149 | 64.5571 | 0.14173 | 8.5037 | 0.014462
150 | 64.5716 | 0.1371 | 8.2261 | 0.01399
151 | 64.5855 | 0.13262 | 7.9575 | 0.013533
152 | 64.5991 | 0.12829 | 7.6976 | 0.013091
153 | 64.6122 | 0.1241 | 7.4463 | 0.012664
154 | 64.6248 | 0.12005 | 7.2031 | 0.01225
155 | 64.6371 | 0.11613 | 6.9679 | 0.01185
156 | 64.6489 | 0.11234 | 6.7404 | 0.011463
157 | 64.6604 | 0.10867 | 6.5203 | 0.011089

## CET - Min (hidden)
MIN CET FOR 2022 12 MONTHS HAVE DATA 01/01/2023 11:10:34
2022 | 0.1 | 2.6 | 1.3 | 0.3 | 1.9 | 0.3 | 1.3 | 1.9 | 0.6 | 2.1 | 2.9 | -1.7
2022 | 1.3 | 3.6 | 3.6 | 4.3 | 8.6 | 10 | 12.9 | 13.3 | 10.2 | 9.2 | 6.4 | 0.2
1 | 10.9 | 4 | 3.2 | -0.3 | 7.6 | 7.1 | 9.7 | 12.8 | 12.3 | 10.1 | 10.1 | 1.7
2 | 8.5 | 7.7 | 4.1 | -0.8 | 8.7 | 5.4 | 10.9 | 17.6 | 14.4 | 10.2 | 6.3 | 2.1
3 | 7.3 | 6.8 | 5.1 | -2.4 | 8.7 | 9.3 | 9.4 | 17.4 | 14 | 5.8 | 8.1 | 2.4
4 | 1.8 | 2.4 | 4.7 | 4.5 | 8.8 | 9.7 | 10.2 | 13.3 | 15.4 | 10.3 | 2.4 | 1.4
5 | 0.2 | 1.9 | 2.7 | 8.4 | 5.9 | 9 | 9.2 | 10.2 | 14.2 | 13.5 | 4.1 | 3.3
6 | -3.7 | 3.9 | 2.1 | 7.7 | 8.2 | 10 | 11.4 | 7.9 | 14 | 7.5 | 5.4 | 1
7 | 0 | 0.9 | 1 | 6.1 | 8.8 | 9.1 | 14.3 | 9.5 | 13.3 | 11.8 | 7.3 | -1.9
8 | 0.7 | 3.9 | -0.5 | -0.4 | 8.1 | 12.9 | 11.7 | 12.4 | 12.9 | 7 | 10 | -5.1
9 | 1.8 | 7.2 | 3.7 | -0.3 | 7.2 | 10.3 | 12.6 | 10.3 | 12.8 | 4.6 | 8.7 | -5.1
10 | 1.6 | 3.8 | 8.1 | -1.9 | 11.7 | 12.6 | 11.5 | 12 | 12.9 | 7.5 | 8.6 | -4.1
11 | 4.2 | 0.1 | 7.6 | 4.4 | 10.3 | 11.5 | 12.2 | 12.9 | 11.3 | 2.6 | 12.7 | -3.4
12 | -0.8 | 1.1 | 6.3 | 7.5 | 6.2 | 10.8 | 16.9 | 14.6 | 14.1 | 4.4 | 8.7 | -3.9
13 | 0.1 | 5.3 | 7.4 | 8.9 | 9.4 | 9.5 | 13.9 | 15.3 | 10.8 | 7.1 | 9.5 | -4.1
14 | -0.7 | 4.8 | 2.7 | 4.9 | 7 | 6.9 | 10.4 | 15.6 | 9.3 | 7.3 | 7.9 | -5.5
15 | -2.1 | 1.8 | 1.7 | 6.9 | 11 | 7.7 | 9.6 | 16.9 | 9.7 | 8.6 | 8.1 | -9.3
16 | -0.9 | 5.9 | 5.9 | 6.7 | 11.6 | 9.2 | 9.6 | 14.6 | 7.9 | 7.5 | 5.5 | -8
17 | 0.7 | 6.3 | 1.6 | 7 | 9.7 | 13.8 | 13.7 | 14.6 | 3.7 | 10.9 | 7.7 | -6.6
18 | -2.9 | 5.1 | 1.6 | 6.4 | 9.5 | 13.6 | 13.9 | 15 | 7.9 | 3.9 | 7.2 | -2.1
19 | -1.8 | 1.6 | 4.9 | 3.7 | 10.3 | 7.3 | 18.9 | 14.2 | 9.5 | 8.6 | 4.9 | 0.5
20 | -0.8 | 2 | 2.2 | 5.5 | 10.1 | 7.7 | 17.2 | 12.2 | 8.1 | 11.5 | 4.1 | 6.5
21 | -3.1 | 3.6 | -1.1 | 4.9 | 8.8 | 6.9 | 13.2 | 12.4 | 11 | 9.6 | 1.9 | 4.3
22 | 0.2 | 4.4 | 4.3 | 5.9 | 8.5 | 9.8 | 15 | 12.2 | 10 | 11.2 | 4.1 | 4
23 | 3.8 | 3.1 | 3.7 | 6.6 | 9.8 | 10.1 | 12.3 | 16 | 10.3 | 12.4 | 4.2 | 5.4
24 | 2.9 | 2.9 | 2.2 | 6.3 | 8.6 | 14.4 | 16.8 | 18.1 | 6.1 | 10.2 | 5.2 | 4.4
25 | 0.9 | 2.3 | 3.8 | 4.4 | 8.4 | 10.8 | 15.3 | 15.2 | 5 | 10 | 4.9 | 5.4
26 | 0.8 | 1.2 | 3.2 | 4.2 | 9.8 | 10 | 12.8 | 9.9 | 10 | 12.3 | 6 | 1
27 | 4.1 | 2 | 4.6 | 2.8 | 9.3 | 10.4 | 8.7 | 12.2 | 7.3 | 11.6 | 8.8 | 1.2
28 | 1.1 | 4.3 | 4 | 5 | 5.9 | 9.1 | 13.6 | 11.2 | 4.7 | 13.8 | 4.7 | 3.8
29 | 3.5 | -99.9 | 6.5 | 4.4 | 7.2 | 12.9 | 13.3 | 13.9 | 6.1 | 10.2 | 2.4 | 6.1
30 | -0.2 | -99.9 | 3.8 | 0.8 | 6 | 11.4 | 14.8 | 11.1 | 6.3 | 12 | 2.8 | 4.1
31 | 1.4 | -99.9 | -0.4 | -99.9 | 6.9 | -99.9 | 17 | 12 | -99.9 | 11 | -99.9 | 7.3

## CET - Max (hidden)
MAX CET FOR 2022 12 MONTHS HAVE DATA 01/01/2023 11:10:34
2022 | 1.6 | 3.7 | 3.3 | 2.2 | 1.9 | 1.3 | 3.1 | 4 | 1.2 | 2.5 | 2.5 | -0.5
2022 | 8 | 10.3 | 12.4 | 14.1 | 17.5 | 19.8 | 23.4 | 24.1 | 18.7 | 16.5 | 11.9 | 6.6
1 | 14.5 | 12.9 | 8.4 | 8.2 | 12.9 | 16.9 | 19.1 | 24.4 | 22.7 | 17.8 | 14.3 | 5.9
2 | 11.3 | 11.4 | 7.3 | 9.4 | 15.2 | 19.4 | 19 | 24.4 | 21.9 | 16.9 | 13.5 | 5.9
3 | 10 | 10.6 | 9.9 | 9.9 | 14.7 | 20 | 19.3 | 24.1 | 22.1 | 17 | 12.2 | 7.3
4 | 4.5 | 7.5 | 8.6 | 13.2 | 15.6 | 16.5 | 19.2 | 20.8 | 23.3 | 17.4 | 12 | 5.8
5 | 5.8 | 9.3 | 8 | 12.5 | 18.3 | 12.8 | 20 | 20.3 | 23 | 16.6 | 12.7 | 7.2
6 | 6.4 | 9.3 | 8.2 | 12.1 | 17.9 | 16.2 | 21.5 | 21.5 | 21 | 17.7 | 12.2 | 6
7 | 6.7 | 10.9 | 7.5 | 10.6 | 18 | 20.4 | 21.4 | 23.7 | 21.5 | 16.7 | 14.2 | 4.5
8 | 9.3 | 11.8 | 11.2 | 10.7 | 18.1 | 19.1 | 23.8 | 25.7 | 19 | 15.5 | 13.9 | 3
9 | 7.8 | 10.8 | 12.6 | 11 | 19.4 | 18.3 | 23.2 | 27.4 | 20.1 | 16.9 | 13.7 | 3.5
10 | 9.2 | 7.7 | 14.5 | 12.4 | 18.2 | 20.9 | 26.4 | 28.9 | 20.1 | 14.5 | 15 | 3.2
11 | 9.4 | 8.1 | 12.2 | 15.6 | 15.6 | 19.9 | 29 | 30.9 | 21.8 | 14.8 | 15.9 | 0.7
12 | 7.9 | 9.2 | 12.4 | 15 | 16.3 | 18.3 | 26.4 | 31.4 | 22.1 | 14.9 | 15.2 | 0.1
13 | 7.7 | 9.8 | 12.3 | 16.2 | 17.9 | 18.2 | 23.1 | 31.4 | 18.7 | 16.2 | 14.5 | -0.4
14 | 4.9 | 8.4 | 12.8 | 16.7 | 20.7 | 21 | 21.2 | 31.7 | 19 | 14.9 | 13.4 | 0.4
15 | 5.6 | 12.2 | 14.1 | 19.9 | 19.2 | 23.5 | 22.4 | 25.9 | 17 | 15.1 | 12.2 | 0.5
16 | 8.6 | 15 | 10.7 | 19.5 | 20.4 | 25.7 | 25 | 22.8 | 15.7 | 15.6 | 11.1 | 2.8
17 | 8.5 | 10.4 | 13.1 | 18.8 | 22.8 | 28.2 | 30 | 20.9 | 16.2 | 17.2 | 10.4 | 4
18 | 7 | 8.2 | 15.4 | 14.9 | 20.4 | 16.6 | 34.8 | 22.9 | 17.3 | 16.5 | 11 | 13
19 | 8.9 | 10.7 | 14.6 | 14.3 | 18.8 | 17.6 | 37.3 | 21.8 | 17 | 15.2 | 10.6 | 13.5
20 | 5.2 | 12.2 | 11.1 | 17 | 17.4 | 19.7 | 22.4 | 23.1 | 18.4 | 15 | 10.8 | 9.8
21 | 5.5 | 10.8 | 14.2 | 17.4 | 18.3 | 23.2 | 20.9 | 22.2 | 18.9 | 16.9 | 8.2 | 9.4
22 | 6.9 | 12 | 18.1 | 15.9 | 20.7 | 24 | 20.9 | 21.7 | 18.5 | 16.7 | 9.7 | 9
23 | 5.2 | 10.1 | 18.7 | 15.8 | 16.6 | 24.2 | 22.9 | 23.8 | 18 | 17.2 | 11.1 | 10.2
24 | 4.4 | 6.6 | 18.3 | 16.2 | 16.1 | 20.3 | 25.4 | 23.2 | 17.5 | 15.7 | 11.4 | 9.9
25 | 5.1 | 10.5 | 17.7 | 13.8 | 17.4 | 19.7 | 20.7 | 19.3 | 15.1 | 16.7 | 11.5 | 10.6
26 | 9.2 | 10.4 | 18.1 | 14.5 | 17.9 | 19.5 | 19.9 | 21.9 | 14.5 | 17.7 | 12.1 | 7.4
27 | 11.6 | 10.9 | 14.7 | 10.9 | 16.9 | 17.7 | 21.9 | 23.5 | 14.4 | 18.3 | 11.4 | 9.9
28 | 11 | 11 | 15.5 | 11.3 | 17 | 18.6 | 20.5 | 23 | 14.2 | 17 | 10.6 | 11.1
29 | 12.9 | -99.9 | 10.1 | 12.8 | 14.5 | 19.4 | 23.9 | 20.6 | 16.7 | 19.5 | 5.1 | 8.8
30 | 8.4 | -99.9 | 8 | 16.1 | 13.8 | 18.9 | 21.5 | 21.4 | 14.8 | 16.2 | 6.8 | 11.8
31 | 9.5 | -99.9 | 6.9 | -99.9 | 14.6 | -99.9 | 23.7 | 22.4 | -99.9 | 15.8 | -99.9 | 11.3