## Notes
Modelling Tool for Home Heating System with 14kW Mitsubishi Ecodan ASHP Models PUZ-HWM140VHA(-BS) and PUZ-HWM140YHA(-BS).
The initial data used in the accompanying tables was obtained from document Mitsubishi Ecodan Data Book Vol.5.3 R32, the Performance Data
having been obtained from testing carried out to the requirements of EN14511-2013.
How to use the Modelling Tool.
1. Open the Initial Data sheet and set the operating parameters for the particular system under investigation. (The cells that require setting are highlighted in green).
a) In cell C1 set the the Heat Demand as derived from Heat Loss calculations carried out at the specified Ambient Air Temperature (cell E1).
b) In cell H1 set a desired Indoor Temperature.
c) In cell P1 set the value for the Total Heating Elements Output. (If the required information is not available, measure the size and type of all radiators etc. and
obtain the data from a suitable source).
Once the initial operating parameters have been set the table below will show the anticipated operating characteristics for the system.
Of particular interest may be the following:-
Column B shows various Ambient Air Temperatures.
Column C shows the corresponding calculated Heating Demand.
Column D shows the following:-
Calculated Coefficient of Performance (COP).
Calculated Leaving (Flow) Water Temperature (LWT).
Calculated Duty Cycle (Duty (%)). At higher ambient air temperatures the ASHP will not operate continuoiusly, but will cycle.
Calculated Power Input (PI). The electrical energy drawn from the power supply.
Using the Initial Data sheet it should be possible to compare the performance of a working heating system against the manufacturers specified operating criteria.
Any large discrepancies should become obvious and may lead to further investigation becoming necessary.
It will also be possible to carry out 'what if' scenarious, to investigate the effect of possible improvements that could be made to improve overall efficiency.
To see what effect lowering the Heating Demand by improved insulation would have on system operation.
To see what effect varying the Indoor Temperature would have on system operation.
To see what effect installing larger Heat Emitters would have on system operation.
Using the Playroom sheet will allow more detailed investigation of system operation over specific 24 hours periods.
The Play Area table allows hourly variations to be made to the Outdoor Temperature and Indoor Temperature experienced by the system.
This in turn allows the calculation of the following parameters:-
COP
LWT
PI
Heat Energy
It should therefore be possible to see the effects of making changes to the desired indoor temperature throughout the day.
The Lookup Table contains the data necessary for the calculations to be made and should not be changed.
The Data for Graph table contains the data necessary for the production of the graph and should not be changed.
The Pretty Graph shows the calculated Input Power, Output Power and COP, for Indoor Temperatures of 19C, 21C and 23C.
The Detailed Data sheet contains 6 tables which calculate the various parameters at Indoor Temperatures from 18C to 23C.
The data within the tables has been extrapolated from the manufaturers data, to provide ambient air increments of 1C.
Cells containing Bold text or highlighted in Yellow contain formulas, and should not be changed.
Two further parameters have been added to the Detailed Data sheet, Water Temp Hyst. (C.) in cell C2 and Buffer Tank Effect (%) in cell N2.
The Water Temp Hyst. (C.) allows investigation of the possible effect of changing the point at which the ASHP would start and stop operating as the water flowing heat up and cools down.
The Buffer Tank Effect (%) allows investigation of the possible effect of changing of flow rates as pumps stop and start and valves open and close
Both of these paramaters have been set at zero for the moment.
The modelling tool deals solely with heating demand and makes no allowance for hot water production and usage.
It is also impossible to take any account of changes in operation due to solar gain, human activity, wind chill and rain effect.

## Initial Data
Heating Demand (W) |  | 12400 | at Amb. | -2 | Indoor Temp. |  | 19 |  | Total Heating Elements Output (W) | [5 empty] | 23000 | at Delta T of 50C
LWT |  |  |  |  | 25 |  |  |  | 35 |  |  |  | 40 |  |  |  | 45 |  |  |  | 50 |  |  |  | 55
Outdoor air temperature[℃] |  | Heating Demand | COP | CL | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP
|  |  | LWT |  |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI
Duty (%)
PI
12kW-Maximum heating CAP | -15 |  | -1.9651 | max | - | - | - | - | 14000 | 1.85 | 7567.5676 | 0.93857 | 13500 | 1.7 | 7941.1765 | 0.64781 | 13100 | 1.55 | 8451.6129 | 0.3873 | 12600 | 1.45 | 8689.6552 | 0.048214 | 12200 | 1.3 | 9384.6154 | -0.66905
|  | 20076.1905 | 64.0349 | nom | - | - | - | - | 11000 | 2.3 | 4782.6087 | 21390.1573 | 11000 | 2.1 | 5238.0952 | 30990.885 | 11000 | 1.9 | 5789.4737 | 51836.0656 | 11000 | 1.75 | 6285.7143 | 416395.0617 | 11000 | 1.6 | 6875 | -30007.1174
|  |  | 100 | mid | - | - | - | - | 8800 | 2.5 | 3520 | 3 | 8800 | 2.3 | 3826.087 | 3 | 8800 | 2.1 | 4190.4762 | 3 | 8800 | 1.9 | 4631.5789 | 3 | 8800 | 1.7 | 5176.4706 | 3
|  |  | -10216.2076 | min | - | - | - | - | 7800 | 2.35 | 3319.1489 | 3.0254 | 7200 | 2 | 3600 | 3.6305 | 6500 | 1.6 | 4062.5 | 4.322 | 5700 | 1.3 | 4384.6154 | 5.6726 | 4800 | 1 | 4800 | 7.5635
| -10 |  | #DIV/0! | max | 14600 | 2.4 | 6083.3333 | 0.71746 | 14400 | 2.25 | 6400 | 0.54762 | 14200 | 2.1 | 6761.9048 | 0.6381 | 14000 | 1.9 | 7368.4211 | #DIV/0! | 14000 | 1.85 | 7567.5676 | #DIV/0! | 14000 | 1.75 | 8000 | #DIV/0!
|  | 17123.8095 | 58.8484 | nom | 14000 | 2.8 | 5000 | 23867.2566 | 14000 | 2.5 | 5600 | 31269.5652 | 14000 | 2.2 | 6363.6364 | 26835.8209 | 14000 | 1.9 | 7368.4211 | #DIV/0! | 14000 | 1.85 | 7567.5676 | #DIV/0! | 14000 | 1.75 | 8000 | #DIV/0!
|  |  | 100 | mid | 11200 | 2.85 | 3929.8246 | 3 | 11200 | 2.7 | 4148.1481 | 3 | 11200 | 2.55 | 4392.1569 | 3 | 11200 | 2.35 | 4765.9574 | 3 | 11200 | 2.1 | 5333.3333 | 3 | 11200 | 1.85 | 6054.0541 | 3
|  |  | #DIV/0! | min | 6200 | 2.55 | 2431.3725 | 5.2063 | 5900 | 2.3 | 2565.2174 | 7.8095 | 5600 | 2.05 | 2731.7073 | 15.619 | 5300 | 1.75 | 3028.5714 | #DIV/0! | 4600 | 1.45 | 3172.4138 | #DIV/0! | 4000 | 1.1 | 3636.3636 | #DIV/0!
| -7 |  | #DIV/0! | max | 16100 | 2.7 | 5962.963 | 2.8246 | 15900 | 2.5 | 6360 | 2.5865 | 15700 | 2.3 | 6826.087 | 2.3511 | 15500 | 2.1 | 7380.9524 | 2.1197 | 14700 | 2.05 | 7170.7317 | 1.9568 | 14000 | 1.95 | 7179.4872 | #DIV/0!
|  | 15352.381 | 55.6378 | nom | 14000 | 3.05 | 4590.1639 | 5435.2346 | 14000 | 2.8 | 5000 | 5935.6589 | 14000 | 2.55 | 5490.1961 | 6529.8147 | 14000 | 2.3 | 6086.9565 | 7242.7737 | 14000 | 2.15 | 6511.6279 | 7845.6458 | 14000 | 1.95 | 7179.4872 | #DIV/0!
|  |  | 100 | mid | 11200 | 3.25 | 3446.1538 | 3 | 11200 | 3 | 3733.3333 | 3 | 11200 | 2.75 | 4072.7273 | 3 | 11200 | 2.5 | 4480 | 3 | 11200 | 2.3 | 4869.5652 | 3 | 11200 | 2.1 | 5333.3333 | 3
|  |  | #DIV/0! | min | 5100 | 3.65 | 1397.2603 | 0.64399 | 4000 | 2.25 | 1777.7778 | 0.71178 | 4000 | 2.05 | 1951.2195 | 0.79552 | 4000 | 1.85 | 2162.1622 | 0.90159 | 3600 | 1.5 | 2400 | 1.932 | 3100 | 1.15 | 2695.6522 | #DIV/0!
| 2 |  | 2.8173 | max | 16500 | 3.25 | 5076.9231 | 3.7641 | 16300 | 3 | 5433.3333 | 3.4476 | 16000 | 2.75 | 5818.1818 | 3.1411 | 15800 | 2.5 | 6320 | 2.8336 | 15100 | 2.45 | 6163.2653 | 2.6416 | 14300 | 2.35 | 6085.1064 | 2.4048
|  | 10038.0952 | 45.4234 | nom | 14000 | 3.4 | 4117.6471 | 2666.7872 | 14000 | 3.15 | 4444.4444 | 2911.6022 | 14000 | 2.9 | 4827.5862 | 3195.7645 | 14000 | 2.65 | 5283.0189 | 3542.5169 | 14000 | 2.55 | 5490.1961 | 3800.0697 | 14000 | 2.4 | 5833.3333 | 4174.2574
|  |  | 100 | mid | 11200 | 3.65 | 3068.4932 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 3.15 | 3555.5556 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.55 | 4392.1569 | 1
|  |  | 3562.9638 | min | 5600 | 4.2 | 1333.3333 | 0.79252 | 5100 | 3.65 | 1397.2603 | 0.80952 | 4700 | 3.1 | 1516.129 | 0.82125 | 4200 | 2.5 | 1680 | 0.83401 | 3700 | 2.05 | 1804.878 | 0.84508 | 3200 | 1.55 | 2064.5161 | 0.85476
| 7 |  | 3.9956 | max | 16800 | 4.7 | 3574.4681 | 6.079 | 16600 | 4.25 | 3905.8824 | 4.5943 | 16400 | 3.8 | 4315.7895 | 3.8837 | 16100 | 3.3 | 4878.7879 | 3.1814 | 15400 | 2.9 | 5310.3448 | 2.7224 | 14600 | 2.5 | 5840 | 2.2371
|  | 7085.7143 | 39.2129 | nom | 14000 | 4.9 | 2857.1429 | 1165.6057 | 14000 | 4.45 | 3146.0674 | 1542.2886 | 14000 | 4 | 3500 | 1824.4685 | 14000 | 3.5 | 4000 | 2227.2115 | 14000 | 3.15 | 4444.4444 | 2602.7905 | 14000 | 2.75 | 5090.9091 | 3167.3052
|  |  | 100 | mid | 11200 | 5.25 | 2133.3333 | 1 | 11200 | 4.8 | 2333.3333 | 1 | 11200 | 4.35 | 2574.7126 | 1 | 11200 | 3.85 | 2909.0909 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 2.9 | 3862.069 | 1
|  |  | 1773.3906 | min | 4500 | 6.6 | 681.8182 | 0.38593 | 4200 | 4.45 | 943.8202 | 0.41224 | 3700 | 3.5 | 1057.1429 | 0.45143 | 3200 | 2.55 | 1254.902 | 0.48571 | 2700 | 2 | 1350 | 0.51597 | 2200 | 1.45 | 1517.2414 | 0.54286
| 12 |  | 4.9662 | max | 17100 | 5.25 | 3257.1429 | 5.15 | 16800 | 4.9 | 3428.5714 | 4.9 | 16600 | 4.45 | 3730.3371 | 4.65 | 16400 | 4.2 | 3904.7619 | 4.35 | 15600 | 3.7 | 4216.2162 | 3.7 | 14800 | 3.2 | 4625 | 3.05
|  | 4133.3333 | 32.3526 | nom | 14000 | 5.5 | 2545.4545 | 802.589 | 14000 | 5.15 | 2718.4466 | 843.5374 | 14000 | 4.8 | 2916.6667 | 888.8889 | 14000 | 4.45 | 3146.0674 | 950.1916 | 14000 | 4 | 3500 | 1117.1171 | 14000 | 3.5 | 4000 | 1355.1913
|  |  | 65.5471 | mid | 11200 | 5.85 | 1914.5299 | 0 | 11200 | 5.55 | 2018.018 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.9 | 2285.7143 | 0 | 11200 | 4.3 | 2604.6512 | 0 | 11200 | 3.7 | 3027.027 | 0
|  |  | 832.2953 | min | 6600 | 5.15 | 1281.5534 | 0 | 6200 | 4.9 | 1265.3061 | 0 | 5800 | 4.65 | 1247.3118 | 0 | 5400 | 4.35 | 1241.3793 | 0 | 5200 | 3.7 | 1405.4054 | 0 | 5000 | 3.05 | 1639.3443 | 0
| 15 |  | 5.1366 | max | 18500 | 5.35 | 3457.9439 | 5.15 | 18200 | 5 | 3640 | 5.1 | 17900 | 4.75 | 3768.4211 | 5.05 | 17700 | 4.5 | 3933.3333 | 4.95 | 16900 | 4 | 4225 | 4.35 | 16000 | 3.5 | 4571.4286 | 3.7
|  | 2361.9048 | 27.6818 | nom | 14000 | 5.5 | 2545.4545 | 458.6223 | 14000 | 5.25 | 2666.6667 | 463.1186 | 14000 | 5 | 2800 | 467.7039 | 14000 | 4.75 | 2947.3684 | 477.1525 | 14000 | 4.3 | 3255.814 | 542.9666 | 14000 | 3.85 | 3636.3636 | 638.3526
|  |  | 34.9089 | mid | 11200 | 6 | 1866.6667 | 0 | 11200 | 5.65 | 1982.3009 | 0 | 11200 | 5.45 | 2055.0459 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.65 | 2408.6022 | 0 | 11200 | 4.05 | 2765.4321 | 0
|  |  | 459.8195 | min | 6900 | 5.15 | 1339.8058 | 0 | 6400 | 5.1 | 1254.902 | 0 | 5900 | 5.05 | 1168.3168 | 0 | 5400 | 4.95 | 1090.9091 | 0 | 5300 | 4.35 | 1218.3908 | 0 | 5200 | 3.7 | 1405.4054 | 0
| 20 |  | #NUM! | max | 21100 | 7.25 | 2910.3448 | 14 | 20800 | 6.5 | 3200 | 8 | 20500 | 5.75 | 3565.2174 | 6.65 | 20200 | 4.95 | 4080.8081 | 5.3 | 19300 | 4.4 | 4386.3636 | 4.4 | 18300 | 3.8 | 4815.7895 | 3.45
|  | -590.4762 | #NUM! | nom | 14000 | 7.65 | 1830.0654 | -42.1769 | 14000 | 6.85 | 2043.7956 | -73.8095 | 14000 | 6.05 | 2314.0496 | -88.7934 | 14000 | 5.25 | 2666.6667 | -111.4106 | 14000 | 4.75 | 2947.3684 | -134.1991 | 14000 | 4.2 | 3333.3333 | -171.1525
|  |  | #NUM! | mid | 11200 | 8.1 | 1382.716 | 0 | 11200 | 7.35 | 1523.8095 | 0 | 11200 | 6.6 | 1696.9697 | 0 | 11200 | 5.8 | 1931.0345 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.4 | 2545.4545 | 0
|  |  | #NUM! | min | 7300 | 14 | 521.4286 | 0 | 6700 | 8 | 837.5 | 0 | 6400 | 6.65 | 962.406 | 0 | 6000 | 5.3 | 1132.0755 | 0 | 5600 | 4.4 | 1272.7273 | 0 | 5100 | 3.45 | 1478.2609 | 0
Abbreviations:
LWT: Leaving water temperature (°C )
CL: Capacity level
CAP: Total heating capacity (W)
PI: Power input (W)

## Playroom
Initial Conditions
Heating Demand (W) = |  | 12400
Heating Elements (W) = |  | 23000
Play Area.
Hour |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Indoor Temp. (18 to 23) |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
Outside Temp (-15 to 20) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | Ave COP
COP |  | 3.4061 | 3.4061 | 3.4061 | 3.4061 | 3.4061 | 3.4061 | 3.4061 | 3.4061 | 3.4061 | 3.4061 | 3.4061 | 3.4061 | 3.4061 | 3.4061 | 3.4061 | 3.4061 | 3.4061 | 3.4061 | 3.4061 | 3.4061 | 3.4061 | 3.4061 | 3.4061 | 3.4061 | 3.4061
LWT |  | 38.3796 | 38.3796 | 38.3796 | 38.3796 | 38.3796 | 38.3796 | 38.3796 | 38.3796 | 38.3796 | 38.3796 | 38.3796 | 38.3796 | 38.3796 | 38.3796 | 38.3796 | 38.3796 | 38.3796 | 38.3796 | 38.3796 | 38.3796 | 38.3796 | 38.3796 | 38.3796 | 38.3796 | Totals
PI (W/h) |  | 1709.4456 | 1709.4456 | 1709.4456 | 1709.4456 | 1709.4456 | 1709.4456 | 1709.4456 | 1709.4456 | 1709.4456 | 1709.4456 | 1709.4456 | 1709.4456 | 1709.4456 | 1709.4456 | 1709.4456 | 1709.4456 | 1709.4456 | 1709.4456 | 1709.4456 | 1709.4456 | 1709.4456 | 1709.4456 | 1709.4456 | 1709.4456 | 41026.695
Heat Energy (W/h) |  | 5822.6087 | 5822.6087 | 5822.6087 | 5822.6087 | 5822.6087 | 5822.6087 | 5822.6087 | 5822.6087 | 5822.6087 | 5822.6087 | 5822.6087 | 5822.6087 | 5822.6087 | 5822.6087 | 5822.6087 | 5822.6087 | 5822.6087 | 5822.6087 | 5822.6087 | 5822.6087 | 5822.6087 | 5822.6087 | 5822.6087 | 5822.6087 | 139742.6087
104806.9565
|  | 6149 | 6149 | 6149 | 6149 | 6149 | 6149 | 6149 | 6149 | 6149 | 6149 | 6149 | 6149 | 6149 | 6149 | 6149 | 6149 | 6149 | 6149 | 6149 | 6149 | 6149 | 6149 | 6149 | 6149 | 147576
Lookup Table.
|  | Indoor | 18 |  |  | 19 |  |  | 20 |  |  | 21 |  |  | 22 |  |  | 23
|  | Amb. | COP | LWT | PI | COP | LWT | PI | COP | LWT | PI | COP | LWT | PI | COP | LWT | PI | COP | LWT | PI
|  | -15 | 1.9074 | 45.7034 | 5596.4375 | 1.8297 | 47.3469 | 6010.8568 | 1.7215 | 48.9861 | 6576.859 | 1.6054 | 50.6211 | 7253.8654 | 1.4735 | 52.252 | 8122.4014 | 1.3287 | 53.879 | 9251.3208
|  | -14 | 2.0583 | 45.0553 | 5028.9876 | 2.0229 | 46.7034 | 5276.9026 | 1.988 | 48.3469 | 5532.3015 | 1.9332 | 49.9861 | 5856.5253 | 1.8485 | 51.6211 | 6299.8437 | 1.7692 | 53.252 | 6764.8611
|  | -13 | 2.1048 | 44.4026 | 4764.193 | 2.0651 | 46.0553 | 5012.5706 | 2.0263 | 47.7034 | 5268.2123 | 1.9877 | 49.3469 | 5533.2067 | 1.9291 | 50.9861 | 5868.8518 | 1.842 | 52.6211 | 6322.1744
|  | -12 | 2.1527 | 43.7449 | 4508.0534 | 2.1105 | 45.4026 | 4751.4642 | 2.0681 | 47.0553 | 5005.1435 | 2.0258 | 48.7034 | 5269.4492 | 1.9834 | 50.3469 | 5545.2763 | 1.9214 | 51.9861 | 5892.4129
|  | -11 | 2.201 | 43.0822 | 4262.0761 | 2.1581 | 44.7449 | 4496.6906 | 2.1133 | 46.4026 | 4745.1696 | 2.0675 | 48.0553 | 5006.6852 | 2.0215 | 49.7034 | 5280.6639 | 1.9749 | 51.3469 | 5569.1601
|  | -10 | 2.2493 | 42.4142 | 4026.7818 | 2.2059 | 44.0822 | 4252.7088 | 2.1614 | 45.7449 | 4489.9102 | 2.1125 | 47.4026 | 4746.9546 | 2.0631 | 49.0553 | 5017.2667 | 2.0127 | 50.7034 | 5303.7491
|  | -9 | 2.3091 | 41.7407 | 3782.3599 | 2.2635 | 43.4142 | 4001.5412 | 2.2189 | 45.0822 | 4227.6571 | 2.1711 | 46.7449 | 4469.8569 | 2.1242 | 48.4026 | 4720.7215 | 2.0783 | 50.0553 | 4980.5982
|  | -8 | 2.3696 | 41.0614 | 3549.2704 | 2.3231 | 42.7407 | 3759.6707 | 2.2764 | 44.4142 | 3978.7471 | 2.2291 | 46.0822 | 4208.4542 | 2.1832 | 47.7449 | 4445.071 | 2.1396 | 49.4026 | 4686.8033
|  | -7 | 2.4302 | 40.376 | 3327.7373 | 2.3837 | 42.0614 | 3528.2984 | 2.336 | 43.7407 | 3738.8038 | 2.2873 | 45.4142 | 3959.7921 | 2.2411 | 47.0822 | 4185.7753 | 2.1984 | 48.7449 | 4414.2955
|  | -6 | 2.5069 | 39.6843 | 3096.8926 | 2.4525 | 41.376 | 3297.4402 | 2.398 | 43.0614 | 3507.3012 | 2.3434 | 44.7407 | 3726.9564 | 2.2932 | 46.4142 | 3949.5954 | 2.2475 | 48.0822 | 4173.8721
|  | -5 | 2.5953 | 38.9859 | 2866.676 | 2.5317 | 40.6843 | 3066.5398 | 2.4684 | 42.376 | 3276.2597 | 2.4063 | 44.0614 | 3495.2003 | 2.3489 | 45.7407 | 3718.3159 | 2.2994 | 47.4142 | 3938.9433
|  | -4 | 2.6978 | 38.2805 | 2637.8913 | 2.6233 | 39.9859 | 2836.1595 | 2.5491 | 41.6843 | 3045.6346 | 2.4774 | 43.376 | 3264.2837 | 2.4087 | 45.0614 | 3491.6456 | 2.3548 | 46.7407 | 3708.9582
|  | -3 | 2.8167 | 37.5676 | 2411.6723 | 2.7284 | 39.2805 | 2608.3347 | 2.6422 | 40.9859 | 2815.8824 | 2.5588 | 42.6843 | 3034.0683 | 2.4793 | 44.376 | 3261.7622 | 2.4143 | 46.0614 | 3483.591
|  | -2 | 2.9549 | 36.8468 | 2189.427 | 2.8501 | 38.5676 | 2383.4117 | 2.7499 | 40.2805 | 2587.9137 | 2.6525 | 41.9859 | 2804.9256 | 2.5604 | 43.6843 | 3032.0899 | 2.4786 | 45.376 | 3262.7161
|  | -1 | 3.1155 | 36.1176 | 1972.7607 | 2.9914 | 37.8468 | 2162.7138 | 2.8739 | 39.5676 | 2363.6698 | 2.7608 | 41.2805 | 2577.6907 | 2.6538 | 42.9859 | 2803.5163 | 2.5537 | 44.6843 | 3040.1465
|  | 0 | 3.302 | 35.3796 | 1763.3781 | 3.1555 | 37.1176 | 1947.7682 | 3.0172 | 38.8468 | 2144.2117 | 2.8862 | 40.5676 | 2353.5902 | 2.7618 | 42.2805 | 2576.8082 | 2.6457 | 43.9859 | 2812.1126
|  | 1 | 3.507 | 34.632 | 1568.0654 | 3.3459 | 36.3796 | 1740.211 | 3.1836 | 38.1176 | 1930.552 | 3.0312 | 39.8468 | 2134.29 | 2.8868 | 41.5676 | 2353.1411 | 2.7522 | 43.2805 | 2585.7274
|  | 2 | 3.7092 | 33.8742 | 1395.3669 | 3.567 | 35.632 | 1541.6817 | 3.3768 | 37.3796 | 1724.2794 | 3.1987 | 39.1176 | 1921.4596 | 3.0317 | 40.8468 | 2134.003 | 2.8758 | 42.5676 | 2362.1282
|  | 3 | 3.9748 | 33.1053 | 1220.7231 | 3.8157 | 34.8742 | 1356.4019 | 3.6065 | 36.632 | 1524.7762 | 3.4061 | 38.3796 | 1709.4456 | 3.2187 | 40.1176 | 1909.5028 | 3.0449 | 41.8468 | 2124.6927
|  | 4 | 4.2884 | 32.3246 | 1056.0399 | 4.0763 | 34.1053 | 1190.3358 | 3.8535 | 35.8742 | 1343.0969 | 3.6295 | 37.632 | 1515.0998 | 3.4194 | 39.3796 | 1702.8115 | 3.2253 | 41.1176 | 1905.5776
|  | 5 | 4.6538 | 31.5308 | 903.6006 | 4.383 | 33.3246 | 1033.2437 | 4.1193 | 35.1053 | 1177.9185 | 3.8704 | 36.8742 | 1337.2552 | 3.6363 | 38.632 | 1512.2998 | 3.4182 | 40.3796 | 1703.4108
|  | 6 | 5.0727 | 30.7228 | 765.2186 | 4.7419 | 32.5308 | 886.8289 | 4.4183 | 34.3246 | 1024.991 | 4.13 | 36.1053 | 1174.8688 | 3.8706 | 37.8742 | 1337.1657 | 3.6268 | 39.632 | 1516.2325
|  | 7 | 5.5467 | 29.8992 | 641.5116 | 5.1546 | 31.7228 | 753.0648 | 4.7661 | 33.5308 | 882.3193 | 4.4098 | 35.3246 | 1026.9628 | 4.1238 | 37.1053 | 1176.6134 | 3.8545 | 38.8742 | 1342.7642
|  | 8 | 5.5917 | 29.058 | 578.4932 | 5.2658 | 30.8992 | 675.724 | 4.9431 | 32.7228 | 785.2913 | 4.623 | 34.5308 | 909.6209 | 4.3377 | 36.3246 | 1044.043 | 4.0943 | 38.1053 | 1185.1181
|  | 9 | 5.5756 | 28.1971 | 522.1508 | 5.3169 | 30.058 | 608.3916 | 5.061 | 31.8992 | 703.0722 | 4.8075 | 33.7228 | 807.4299 | 4.5589 | 35.5308 | 922.4255 | 4.3185 | 37.3246 | 1048.6716
|  | 10 | 5.4963 | 27.3139 | 470.8305 | 5.3061 | 29.1971 | 548.6722 | 5.1181 | 31.058 | 632.0225 | 4.9322 | 32.8992 | 721.437 | 4.748 | 34.7228 | 817.5537 | 4.5577 | 36.5308 | 922.6556
|  | 11 | 5.3515 | 26.4047 | 423.1235 | 5.2312 | 28.3139 | 494.6881 | 5.1126 | 30.1971 | 569.4392 | 4.9953 | 32.058 | 647.5591 | 4.8794 | 33.8992 | 729.2485 | 4.7536 | 35.7228 | 816.5862
|  | 12 | 5.1384 | 25.4649 | 377.7203 | 5.0899 | 27.4047 | 444.8722 | 5.0422 | 29.3139 | 513.2382 | 4.9951 | 31.1971 | 582.8353 | 4.9486 | 33.058 | 653.6828 | 4.9025 | 34.8992 | 725.8023
|  | 13 | 5.15 | 24.488 | 314.0566 | 5.1231 | 26.4649 | 378.8435 | 5.0876 | 28.4047 | 445.0735 | 5.0526 | 30.3139 | 512.1792 | 5.0181 | 32.1971 | 580.1661 | 4.9839 | 34.058 | 649.0416
|  | 14 | 5.15 | 23.4647 | 251.2453 | 5.1443 | 25.488 | 314.4042 | 5.1212 | 27.4649 | 378.9841 | 5.0986 | 29.4047 | 444.1106 | 5.0763 | 31.3139 | 509.782 | 5.0544 | 33.1971 | 575.9978
|  | 15 | 5.15 | 22.3799 | 188.4339 | 5.15 | 24.4647 | 251.2453 | 5.1426 | 26.488 | 314.5109 | 5.1327 | 28.4649 | 378.1399 | 5.123 | 30.4047 | 441.9985 | 5.1134 | 32.3139 | 506.0841
|  | 16 | 6.92 | 21.2063 | 93.4908 | 6.92 | 23.3799 | 140.2362 | 6.8624 | 25.4647 | 188.5518 | 6.6115 | 27.488 | 244.6337 | 6.3664 | 29.4649 | 304.8635 | 6.1258 | 31.4047 | 369.6398
|  | 17 | 8.69 | 19.8812 | 37.2242 | 8.69 | 22.2063 | 74.4484 | 8.69 | 24.3799 | 111.6726 | 8.3341 | 26.4647 | 155.2558 | 7.8424 | 28.488 | 206.2367 | 7.362 | 30.4649 | 263.6322
|  | 18 | 10.46 | 18 | 0 | 10.46 | 20.8812 | 30.9253 | 10.46 | 23.2063 | 61.8505 | 10.3225 | 25.3799 | 94.0117 | 9.5678 | 27.4647 | 135.2366 | 8.8353 | 29.488 | 183.0596
|  | 19 |  |  |  | 12.23 | 19 | 0 | 12.23 | 21.8812 | 26.4496 | 12.23 | 24.2063 | 52.8991 | 11.5663 | 26.3799 | 83.902 | 10.5635 | 28.4647 | 122.4894
|  | 20 | [6 empty] | 14 | 20 | 0 | 14 | 22.8812 | 23.1056 | 13.8762 | 25.2063 | 46.6234 | 12.5721 | 27.3799 | 77.1897
Data for Graph.
|  | Indoor | 19 |  |  | 21 |  |  | 23
|  | Amb. | PI (kW) | PO (kW) | COP (%) | PI (kW) | PO (kW) | COP (%) | PI (kW) | PO (kW) | COP (%)
|  | -15 | 6.0109 | 10.6748 | 1.8297 | 7.2539 | 11.6452 | 1.6054 | 9.2513 | 12.2922 | 1.3287
|  | -14 | 5.2769 | 10.3513 | 2.0229 | 5.8565 | 11.3217 | 1.9332 | 6.7649 | 11.9687 | 1.7692
|  | -13 | 5.0126 | 10.0278 | 2.0651 | 5.5332 | 10.9983 | 1.9877 | 6.3222 | 11.6452 | 1.842
|  | -12 | 4.7515 | 9.7043 | 2.1105 | 5.2694 | 10.6748 | 2.0258 | 5.8924 | 11.3217 | 1.9214
|  | -11 | 4.4967 | 9.3809 | 2.1581 | 5.0067 | 10.3513 | 2.0675 | 5.5692 | 10.9983 | 1.9749
|  | -10 | 4.2527 | 9.0574 | 2.2059 | 4.747 | 10.0278 | 2.1125 | 5.3037 | 10.6748 | 2.0127
|  | -9 | 4.0015 | 8.7339 | 2.2635 | 4.4699 | 9.7043 | 2.1711 | 4.9806 | 10.3513 | 2.0783
|  | -8 | 3.7597 | 8.4104 | 2.3231 | 4.2085 | 9.3809 | 2.2291 | 4.6868 | 10.0278 | 2.1396
|  | -7 | 3.5283 | 8.087 | 2.3837 | 3.9598 | 9.0574 | 2.2873 | 4.4143 | 9.7043 | 2.1984
|  | -6 | 3.2974 | 7.7635 | 2.4525 | 3.727 | 8.7339 | 2.3434 | 4.1739 | 9.3809 | 2.2475
|  | -5 | 3.0665 | 7.44 | 2.5317 | 3.4952 | 8.4104 | 2.4063 | 3.9389 | 9.0574 | 2.2994
|  | -4 | 2.8362 | 7.1165 | 2.6233 | 3.2643 | 8.087 | 2.4774 | 3.709 | 8.7339 | 2.3548
|  | -3 | 2.6083 | 6.793 | 2.7284 | 3.0341 | 7.7635 | 2.5588 | 3.4836 | 8.4104 | 2.4143
|  | -2 | 2.3834 | 6.4696 | 2.8501 | 2.8049 | 7.44 | 2.6525 | 3.2627 | 8.087 | 2.4786
|  | -1 | 2.1627 | 6.1461 | 2.9914 | 2.5777 | 7.1165 | 2.7608 | 3.0401 | 7.7635 | 2.5537
|  | 0 | 1.9478 | 5.8226 | 3.1555 | 2.3536 | 6.793 | 2.8862 | 2.8121 | 7.44 | 2.6457
|  | 1 | 1.7402 | 5.4991 | 3.3459 | 2.1343 | 6.4696 | 3.0312 | 2.5857 | 7.1165 | 2.7522
|  | 2 | 1.5417 | 5.1757 | 3.567 | 1.9215 | 6.1461 | 3.1987 | 2.3621 | 6.793 | 2.8758
|  | 3 | 1.3564 | 4.8522 | 3.8157 | 1.7094 | 5.8226 | 3.4061 | 2.1247 | 6.4696 | 3.0449
|  | 4 | 1.1903 | 4.5287 | 4.0763 | 1.5151 | 5.4991 | 3.6295 | 1.9056 | 6.1461 | 3.2253
|  | 5 | 1.0332 | 4.2052 | 4.383 | 1.3373 | 5.1757 | 3.8704 | 1.7034 | 5.8226 | 3.4182
|  | 6 | 0.88683 | 3.8817 | 4.7419 | 1.1749 | 4.8522 | 4.13 | 1.5162 | 5.4991 | 3.6268
|  | 7 | 0.75306 | 3.5583 | 5.1546 | 1.027 | 4.5287 | 4.4098 | 1.3428 | 5.1757 | 3.8545
|  | 8 | 0.67572 | 3.2348 | 5.2658 | 0.90962 | 4.2052 | 4.623 | 1.1851 | 4.8522 | 4.0943
|  | 9 | 0.60839 | 2.9113 | 5.3169 | 0.80743 | 3.8817 | 4.8075 | 1.0487 | 4.5287 | 4.3185
|  | 10 | 0.54867 | 2.5878 | 5.3061 | 0.72144 | 3.5583 | 4.9322 | 0.92266 | 4.2052 | 4.5577
|  | 11 | 0.49469 | 2.2643 | 5.2312 | 0.64756 | 3.2348 | 4.9953 | 0.81659 | 3.8817 | 4.7536
|  | 12 | 0.44487 | 1.9409 | 5.0899 | 0.58284 | 2.9113 | 4.9951 | 0.7258 | 3.5583 | 4.9025
|  | 13 | 0.37884 | 1.6174 | 5.1231 | 0.51218 | 2.5878 | 5.0526 | 0.64904 | 3.2348 | 4.9839
|  | 14 | 0.3144 | 1.2939 | 5.1443 | 0.44411 | 2.2643 | 5.0986 | 0.576 | 2.9113 | 5.0544
|  | 15 | 0.25125 | 0.97043 | 5.15 | 0.37814 | 1.9409 | 5.1327 | 0.50608 | 2.5878 | 5.1134
|  | 16 | 0.14024 | 0.64696 | 6.92 | 0.24463 | 1.6174 | 6.6115 | 0.36964 | 2.2643 | 6.1258
|  | 17 | 0.074448 | 0.32348 | 8.69 | 0.15526 | 1.2939 | 8.3341 | 0.26363 | 1.9409 | 7.362
|  | 18 | 0.030925 | 0 | 10.46 | 0.094012 | 0.97043 | 10.3225 | 0.18306 | 1.6174 | 8.8353
|  | 19 | 0 | 0 | 12.23 | 0.052899 | 0.64696 | 12.23 | 0.12249 | 1.2939 | 10.5635
|  | 20 | 0 | 0 | 0 | 0.023106 | 0.32348 | 14 | 0.07719 | 0.97043 | 12.5721
Pretty Graph.

## Detailed Data
Heating Demand (W) |  | 7440 | at Amb. | -2 |  |  |  |  | Total Heating Elements Output (W) | [5 empty] | 23000 | at Delta T of 50C
Water Temp Hyst. (C.) |  | 0 | [6 empty] | Buffer Tank Effect (%) |  |  |  | 0
Indoor Temp. |  | 18
LWT |  |  |  |  | 25 |  |  |  | 35 |  |  |  | 40 |  |  |  | 45 |  |  |  | 50 |  |  |  | 55
Outdoor air temperature[℃] |  | Heating Demand | COP | CL | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP
|  |  | LWT |  |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI
| -15 |  | 1.9074 | max | - | - | - | - | 14000 | 1.85 | 7567.5676 | 2.3296 | 13500 | 1.7 | 7941.1765 | 2.1296 | 13100 | 1.55 | 8451.6129 | 1.9296 | 12600 | 1.45 | 8689.6552 | 1.7722 | 12200 | 1.3 | 9384.6154 | 1.6148
|  | 10674.7826 | 45.7034 | nom | - | - | - | - | 11000 | 2.3 | 4782.6087 | 4582.3068 | 11000 | 2.1 | 5238.0952 | 5012.6582 | 11000 | 1.9 | 5789.4737 | 5532.2217 | 11000 | 1.75 | 6285.7143 | 6023.5525 | 11000 | 1.6 | 6875 | 6610.6624
|  |  | 100 | mid | - | - | - | - | 8800 | 2.5 | 3520 | 2 | 8800 | 2.3 | 3826.087 | 2 | 8800 | 2.1 | 4190.4762 | 2 | 8800 | 1.9 | 4631.5789 | 2 | 8800 | 1.7 | 5176.4706 | 2
|  |  | 5596.4375 | min | - | - | - | - | 7800 | 2.35 | 3319.1489 | 0.85217 | 7200 | 2 | 3600 | 0.85217 | 6500 | 1.6 | 4062.5 | 0.85217 | 5700 | 1.3 | 4384.6154 | 0.85217 | 4800 | 1 | 4800 | 0.85217
| -14 |  | 2.0583 | max | 14280 | 2.08 | 6865.3846 | 2.6656 | 14080 | 1.93 | 7295.3368 | 2.4951 | 13640 | 1.78 | 7662.9213 | 2.2832 | 13280 | 1.62 | 8197.5309 | 2.0607 | 12880 | 1.53 | 8418.3007 | 1.8495 | 12560 | 1.39 | 9035.9712 | 1.6381
|  | 10351.3043 | 45.0553 | nom | 14000 | 2.64 | 5303.0303 | 3883.2747 | 14000 | 2.34 | 5982.906 | 4148.6606 | 14000 | 2.12 | 6603.7736 | 4533.6738 | 14000 | 1.9 | 7368.4211 | 5023.2868 | 14000 | 1.77 | 7909.6045 | 5596.8358 | 14000 | 1.63 | 8588.9571 | 6318.9213
|  |  | 100 | mid | 11200 | 2.69 | 4163.5688 | 1 | 11200 | 2.54 | 4409.4488 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.15 | 5209.3023 | 1 | 11200 | 1.94 | 5773.1959 | 1 | 11200 | 1.73 | 6473.9884 | 1
|  |  | 5028.9876 | min | 7720 | 2.59 | 2980.695 | 0.75612 | 7420 | 2.34 | 3170.9402 | 0.77548 | 6880 | 2.01 | 3422.8856 | 0.80354 | 6260 | 1.63 | 3840.4908 | 0.8282 | 5480 | 1.33 | 4120.3008 | 0.85163 | 4640 | 1.02 | 4549.0196 | 0.87063
| -13 |  | 2.1048 | max | 14360 | 2.16 | 6648.1481 | 2.6844 | 14160 | 2.01 | 7044.7761 | 2.5096 | 13780 | 1.86 | 7408.6022 | 2.304 | 13460 | 1.69 | 7964.497 | 2.0778 | 13160 | 1.61 | 8173.913 | 1.8577 | 12920 | 1.48 | 8729.7297 | 1.6344
|  | 10027.8261 | 44.4026 | nom | 14000 | 2.68 | 5223.8806 | 3735.5246 | 14000 | 2.38 | 5882.3529 | 3995.8553 | 14000 | 2.14 | 6542.0561 | 4352.3494 | 14000 | 1.9 | 7368.4211 | 4826.1649 | 14000 | 1.79 | 7821.2291 | 5398.1191 | 14000 | 1.66 | 8433.7349 | 6135.4412
|  |  | 100 | mid | 11200 | 2.73 | 4102.5641 | 1 | 11200 | 2.58 | 4341.0853 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.2 | 5090.9091 | 1 | 11200 | 1.98 | 5656.5657 | 1 | 11200 | 1.76 | 6363.6364 | 1
|  |  | 4764.193 | min | 7340 | 2.58 | 2844.9612 | 0.69633 | 7040 | 2.33 | 3021.4592 | 0.71823 | 6560 | 2.02 | 3247.5248 | 0.74738 | 6020 | 1.66 | 3626.506 | 0.77371 | 5260 | 1.36 | 3867.6471 | 0.80266 | 4480 | 1.04 | 4307.6923 | 0.82557
| -12 |  | 2.1527 | max | 14440 | 2.24 | 6446.4286 | 2.6995 | 14240 | 2.09 | 6813.3971 | 2.5212 | 13920 | 1.94 | 7175.2577 | 2.3234 | 13640 | 1.76 | 7750 | 2.0955 | 13440 | 1.69 | 7952.6627 | 1.867 | 13280 | 1.57 | 8458.5987 | 1.6313
|  | 9704.3478 | 43.7449 | nom | 14000 | 2.72 | 5147.0588 | 3594.9347 | 14000 | 2.42 | 5785.124 | 3849.1471 | 14000 | 2.16 | 6481.4815 | 4176.8736 | 14000 | 1.9 | 7368.4211 | 4631.1131 | 14000 | 1.81 | 7734.8066 | 5197.7305 | 14000 | 1.69 | 8284.0237 | 5948.8273
|  |  | 100 | mid | 11200 | 2.77 | 4043.3213 | 1 | 11200 | 2.62 | 4274.8092 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.25 | 4977.7778 | 1 | 11200 | 2.02 | 5544.5545 | 1 | 11200 | 1.79 | 6256.9832 | 1
|  |  | 4508.0534 | min | 6960 | 2.57 | 2708.1712 | 0.64725 | 6660 | 2.32 | 2870.6897 | 0.67056 | 6240 | 2.03 | 3073.8916 | 0.69846 | 5780 | 1.69 | 3420.1183 | 0.72405 | 5040 | 1.39 | 3625.8993 | 0.7572 | 4320 | 1.06 | 4075.4717 | 0.78261
| -11 |  | 2.201 | max | 14520 | 2.32 | 6258.6207 | 2.7116 | 14320 | 2.17 | 6599.0783 | 2.5306 | 14060 | 2.02 | 6960.396 | 2.3415 | 13820 | 1.83 | 7551.9126 | 2.1136 | 13720 | 1.77 | 7751.4124 | 1.8775 | 13640 | 1.66 | 8216.8675 | 1.6288
|  | 9380.8696 | 43.0822 | nom | 14000 | 2.76 | 5072.4638 | 3459.5812 | 14000 | 2.46 | 5691.0569 | 3706.9886 | 14000 | 2.18 | 6422.0183 | 4006.3245 | 14000 | 1.9 | 7368.4211 | 4438.3638 | 14000 | 1.83 | 7650.2732 | 4996.424 | 14000 | 1.72 | 8139.5349 | 5759.4292
|  |  | 100 | mid | 11200 | 2.81 | 3985.7651 | 1 | 11200 | 2.66 | 4210.5263 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1 | 11200 | 2.06 | 5436.8932 | 1 | 11200 | 1.82 | 6153.8462 | 1
|  |  | 4262.0761 | min | 6580 | 2.56 | 2570.3125 | 0.60625 | 6280 | 2.31 | 2718.6147 | 0.63026 | 5920 | 2.04 | 2901.9608 | 0.65547 | 5540 | 1.72 | 3220.9302 | 0.6786 | 4820 | 1.42 | 3394.3662 | 0.71487 | 4160 | 1.08 | 3851.8519 | 0.7416
| -10 |  | 2.2493 | max | 14600 | 2.4 | 6083.3333 | 2.7214 | 14400 | 2.25 | 6400 | 2.5383 | 14200 | 2.1 | 6761.9048 | 2.3587 | 14000 | 1.9 | 7368.4211 | 2.1321 | 14000 | 1.85 | 7567.5676 | 1.889 | 14000 | 1.75 | 8000 | 1.6268
|  | 9057.3913 | 42.4142 | nom | 14000 | 2.8 | 5000 | 3328.1571 | 14000 | 2.5 | 5600 | 3568.2992 | 14000 | 2.2 | 6363.6364 | 3840 | 14000 | 1.9 | 7368.4211 | 4248.093 | 14000 | 1.85 | 7567.5676 | 4794.8443 | 14000 | 1.75 | 8000 | 5567.5724
|  |  | 100 | mid | 11200 | 2.85 | 3929.8246 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.1 | 5333.3333 | 1 | 11200 | 1.85 | 6054.0541 | 1
|  |  | 4026.7818 | min | 6200 | 2.55 | 2431.3725 | 0.57148 | 5900 | 2.3 | 2565.2174 | 0.59573 | 5600 | 2.05 | 2731.7073 | 0.61739 | 5300 | 1.75 | 3028.5714 | 0.63685 | 4600 | 1.45 | 3172.4138 | 0.67536 | 4000 | 1.1 | 3636.3636 | 0.70242
| -9 |  | 2.3091 | max | 15100 | 2.5 | 6040 | 2.9527 | 14900 | 2.3333 | 6385.7143 | 2.5853 | 14700 | 2.1667 | 6784.6154 | 2.3888 | 14500 | 1.9667 | 7372.8814 | 2.1599 | 14233.3333 | 1.9167 | 7426.087 | 1.9177 | 14000 | 1.8167 | 7706.422 | 1.6648
|  | 8733.913 | 41.7407 | nom | 14000 | 2.8833 | 4855.4913 | 2957.9425 | 14000 | 2.6 | 5384.6154 | 3378.3546 | 14000 | 2.3167 | 6043.1655 | 3656.1595 | 14000 | 2.0333 | 6885.2459 | 4043.701 | 14000 | 1.95 | 7179.4872 | 4554.4003 | 14000 | 1.8167 | 7706.422 | 5246.2114
|  |  | 100 | mid | 11200 | 2.9833 | 3754.1899 | 1 | 11200 | 2.8 | 4000 | 1 | 11200 | 2.6167 | 4280.2548 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.1667 | 5169.2308 | 1 | 11200 | 1.9333 | 5793.1034 | 1
|  |  | 3782.3599 | min | 5833.3333 | 2.9167 | 2000 | 0.54048 | 5266.6667 | 2.2833 | 2306.5693 | 0.58437 | 5066.6667 | 2.05 | 2471.5447 | 0.59792 | 4866.6667 | 1.7833 | 2728.972 | 0.61062 | 4266.6667 | 1.4667 | 2909.0909 | 0.64431 | 3700 | 1.1167 | 3313.4328 | 0.67119
| -8 |  | 2.3696 | max | 15600 | 2.6 | 6000 | 3.1978 | 15400 | 2.4167 | 6372.4138 | 2.631 | 15200 | 2.2333 | 6805.9701 | 2.4183 | 15000 | 2.0333 | 7377.0492 | 2.1889 | 14466.6667 | 1.9833 | 7294.1176 | 1.9454 | 14000 | 1.8833 | 7433.6283 | 1.7008
|  | 8410.4348 | 41.0614 | nom | 14000 | 2.9667 | 4719.1011 | 2630.103 | 14000 | 2.7 | 5185.1852 | 3196.7224 | 14000 | 2.4333 | 5753.4247 | 3477.7939 | 14000 | 2.1667 | 6461.5385 | 3842.2976 | 14000 | 2.05 | 6829.2683 | 4323.1986 | 14000 | 1.8833 | 7433.6283 | 4945.1202
|  |  | 100 | mid | 11200 | 3.1167 | 3593.5829 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.6833 | 4173.913 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.2333 | 5014.9254 | 1 | 11200 | 2.0167 | 5553.719 | 1
|  |  | 3549.2704 | min | 5466.6667 | 3.2833 | 1664.9746 | 0.51345 | 4633.3333 | 2.2667 | 2044.1176 | 0.57519 | 4533.3333 | 2.05 | 2211.3821 | 0.58157 | 4433.3333 | 1.8167 | 2440.367 | 0.58775 | 3933.3333 | 1.4833 | 2651.6854 | 0.61611 | 3400 | 1.1333 | 3000 | 0.64236
| -7 |  | 2.4302 | max | 16100 | 2.7 | 5962.963 | 3.4541 | 15900 | 2.5 | 6360 | 2.6757 | 15700 | 2.3 | 6826.087 | 2.4473 | 15500 | 2.1 | 7380.9524 | 2.219 | 14700 | 2.05 | 7170.7317 | 1.9723 | 14000 | 1.95 | 7179.4872 | 1.7349
|  | 8086.9565 | 40.376 | nom | 14000 | 3.05 | 4590.1639 | 2341.24 | 14000 | 2.8 | 5000 | 3022.3426 | 14000 | 2.55 | 5490.1961 | 3304.3822 | 14000 | 2.3 | 6086.9565 | 3644.4783 | 14000 | 2.15 | 6511.6279 | 4100.2436 | 14000 | 1.95 | 7179.4872 | 4661.3657
|  |  | 100 | mid | 11200 | 3.25 | 3446.1538 | 1 | 11200 | 3 | 3733.3333 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1 | 11200 | 2.1 | 5333.3333 | 1
|  |  | 3327.7373 | min | 5100 | 3.65 | 1397.2603 | 0.48967 | 4000 | 2.25 | 1777.7778 | 0.56763 | 4000 | 2.05 | 1951.2195 | 0.56763 | 4000 | 1.85 | 2162.1622 | 0.56763 | 3600 | 1.5 | 2400 | 0.59039 | 3100 | 1.15 | 2695.6522 | 0.61567
| -6 |  | 2.5069 | max | 16144.4444 | 2.7611 | 5847.0825 | 3.5313 | 15944.4444 | 2.5556 | 6239.1304 | 2.7342 | 15733.3333 | 2.35 | 6695.0355 | 2.4915 | 15533.3333 | 2.1444 | 7243.5233 | 2.2465 | 14744.4444 | 2.0944 | 7039.7878 | 1.9928 | 14033.3333 | 1.9944 | 7036.2117 | 1.744
|  | 7763.4783 | 39.6843 | nom | 14000 | 3.0889 | 4532.3741 | 2198.4529 | 14000 | 2.8389 | 4931.5068 | 2839.3547 | 14000 | 2.5889 | 5407.7253 | 3115.939 | 14000 | 2.3389 | 5985.7482 | 3455.7464 | 14000 | 2.1944 | 6379.7468 | 3895.8367 | 14000 | 2 | 7000 | 4451.4406
|  |  | 100 | mid | 11200 | 3.2944 | 3399.6627 | 1 | 11200 | 3.0444 | 3678.8321 | 1 | 11200 | 2.7944 | 4007.9523 | 1 | 11200 | 2.5444 | 4401.7467 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.15 | 5209.3023 | 1
|  |  | 3096.8926 | min | 5155.5556 | 3.7111 | 1389.2216 | 0.43146 | 4122.2222 | 2.4056 | 1713.6259 | 0.51446 | 4077.7778 | 2.1667 | 1882.0513 | 0.51749 | 4022.2222 | 1.9222 | 2092.4855 | 0.52123 | 3611.1111 | 1.5611 | 2313.1673 | 0.54716 | 3111.1111 | 1.1944 | 2604.6512 | 0.57516
| -5 |  | 2.5953 | max | 16188.8889 | 2.8222 | 5736.2205 | 3.6109 | 15988.8889 | 2.6111 | 6123.4043 | 2.8036 | 15766.6667 | 2.4 | 6569.4444 | 2.5424 | 15566.6667 | 2.1889 | 7111.6751 | 2.2765 | 14788.8889 | 2.1389 | 6914.2857 | 2.0141 | 14066.6667 | 2.0389 | 6899.1826 | 1.7526
|  | 7440 | 38.9859 | nom | 14000 | 3.1278 | 4476.0213 | 2060.4006 | 14000 | 2.8778 | 4864.8649 | 2653.7448 | 14000 | 2.6278 | 5327.6956 | 2926.4161 | 14000 | 2.3778 | 5887.8505 | 3268.1337 | 14000 | 2.2389 | 6253.1017 | 3694.0012 | 14000 | 2.05 | 6829.2683 | 4245.0556
|  |  | 100 | mid | 11200 | 3.3389 | 3354.4093 | 1 | 11200 | 3.0889 | 3625.8993 | 1 | 11200 | 2.8389 | 3945.2055 | 1 | 11200 | 2.5889 | 4326.1803 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.2 | 5090.9091 | 1
|  |  | 2866.676 | min | 5211.1111 | 3.7722 | 1381.4433 | 0.37217 | 4244.4444 | 2.5611 | 1657.2668 | 0.45942 | 4155.5556 | 2.2833 | 1819.9513 | 0.46625 | 4044.4444 | 1.9944 | 2027.8552 | 0.47453 | 3622.2222 | 1.6222 | 2232.8767 | 0.50381 | 3122.2222 | 1.2389 | 2520.1794 | 0.53453
| -4 |  | 2.6978 | max | 16233.3333 | 2.8833 | 5630.0578 | 3.693 | 16033.3333 | 2.6667 | 6012.5 | 2.8843 | 15800 | 2.45 | 6448.9796 | 2.6 | 15600 | 2.2333 | 6985.0746 | 2.3089 | 14833.3333 | 2.1833 | 6793.8931 | 2.0363 | 14100 | 2.0833 | 6768 | 1.7607
|  | 7116.5217 | 38.2805 | nom | 14000 | 3.1667 | 4421.0526 | 1927.0115 | 14000 | 2.9167 | 4800 | 2467.2958 | 14000 | 2.6667 | 5250 | 2737.0924 | 14000 | 2.4167 | 5793.1034 | 3082.1532 | 14000 | 2.2833 | 6131.3869 | 3494.9061 | 14000 | 2.1 | 6666.6667 | 4041.9681
|  |  | 100 | mid | 11200 | 3.3833 | 3310.3448 | 1 | 11200 | 3.1333 | 3574.4681 | 1 | 11200 | 2.8833 | 3884.3931 | 1 | 11200 | 2.6333 | 4253.1646 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.25 | 4977.7778 | 1
|  |  | 2637.8913 | min | 5266.6667 | 3.8333 | 1373.913 | 0.31177 | 4366.6667 | 2.7167 | 1607.362 | 0.40242 | 4233.3333 | 2.4 | 1763.8889 | 0.41385 | 4066.6667 | 2.0667 | 1967.7419 | 0.42755 | 3633.3333 | 1.6833 | 2158.4158 | 0.46033 | 3133.3333 | 1.2833 | 2441.5584 | 0.49378
| -3 |  | 2.8167 | max | 16277.7778 | 2.9444 | 5528.3019 | 3.7777 | 16077.7778 | 2.7222 | 5906.1224 | 2.9771 | 15833.3333 | 2.5 | 6333.3333 | 2.6648 | 15633.3333 | 2.2778 | 6863.4146 | 2.3438 | 14877.7778 | 2.2278 | 6678.3042 | 2.0593 | 14133.3333 | 2.1278 | 6642.2977 | 1.7681
|  | 6793.0435 | 37.5676 | nom | 14000 | 3.2056 | 4367.4177 | 1798.2106 | 14000 | 2.9556 | 4736.8421 | 2281.7424 | 14000 | 2.7056 | 5174.538 | 2549.193 | 14000 | 2.4556 | 5701.3575 | 2898.2872 | 14000 | 2.3278 | 6014.3198 | 3298.7079 | 14000 | 2.15 | 6511.6279 | 3841.9455
|  |  | 100 | mid | 11200 | 3.4278 | 3267.423 | 1 | 11200 | 3.1778 | 3524.4755 | 1 | 11200 | 2.9278 | 3825.4269 | 1 | 11200 | 2.6778 | 4182.5726 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1
|  |  | 2411.6723 | min | 5322.2222 | 3.8944 | 1366.6191 | 0.25023 | 4488.8889 | 2.8722 | 1562.8627 | 0.34333 | 4311.1111 | 2.5167 | 1713.0243 | 0.36028 | 4088.8889 | 2.1389 | 1911.6883 | 0.38027 | 3644.4444 | 1.7444 | 2089.172 | 0.41673 | 3144.4444 | 1.3278 | 2368.2008 | 0.45293
| -2 |  | 2.9549 | max | 16322.2222 | 3.0056 | 5430.6839 | 3.8649 | 16122.2222 | 2.7778 | 5804 | 3.0826 | 15866.6667 | 2.55 | 6222.2222 | 2.7369 | 15666.6667 | 2.3222 | 6746.4115 | 2.3812 | 14922.2222 | 2.2722 | 6567.2372 | 2.0832 | 14166.6667 | 2.1722 | 6521.7391 | 1.775
|  | 6469.5652 | 36.8468 | nom | 14000 | 3.2444 | 4315.0685 | 1673.9193 | 14000 | 2.9944 | 4675.3247 | 2098.7212 | 14000 | 2.7444 | 5101.2146 | 2363.8659 | 14000 | 2.4944 | 5612.4722 | 2716.9846 | 14000 | 2.3722 | 5901.6393 | 3105.5504 | 14000 | 2.2 | 6363.6364 | 3644.7638
|  |  | 100 | mid | 11200 | 3.4722 | 3225.6 | 1 | 11200 | 3.2222 | 3475.8621 | 1 | 11200 | 2.9722 | 3768.2243 | 1 | 11200 | 2.7222 | 4114.2857 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1
|  |  | 2189.427 | min | 5377.7778 | 3.9556 | 1359.5506 | 0.18752 | 4611.1111 | 3.0278 | 1522.9358 | 0.28206 | 4388.8889 | 2.6333 | 1666.6667 | 0.30548 | 4111.1111 | 2.2111 | 1859.2965 | 0.3327 | 3655.5556 | 1.8056 | 2024.6154 | 0.37299 | 3155.5556 | 1.3722 | 2299.5951 | 0.41196
| -1 |  | 3.1155 | max | 16366.6667 | 3.0667 | 5336.9565 | 3.9549 | 16166.6667 | 2.8333 | 5705.8824 | 3.2015 | 15900 | 2.6 | 6115.3846 | 2.8165 | 15700 | 2.3667 | 6633.8028 | 2.421 | 14966.6667 | 2.3167 | 6460.4317 | 2.108 | 14200 | 2.2167 | 6406.015 | 1.7814
|  | 6146.087 | 36.1176 | nom | 14000 | 3.2833 | 4263.9594 | 1554.0565 | 14000 | 3.0333 | 4615.3846 | 1919.729 | 14000 | 2.7833 | 5029.9401 | 2182.1628 | 14000 | 2.5333 | 5526.3158 | 2538.6583 | 14000 | 2.4167 | 5793.1034 | 2915.5648 | 14000 | 2.25 | 6222.2222 | 3450.2072
|  |  | 100 | mid | 11200 | 3.5167 | 3184.8341 | 1 | 11200 | 3.2667 | 3428.5714 | 1 | 11200 | 3.0167 | 3712.7072 | 1 | 11200 | 2.7667 | 4048.1928 | 1 | 11200 | 2.6 | 4307.6923 | 1 | 11200 | 2.4 | 4666.6667 | 1
|  |  | 1972.7607 | min | 5433.3333 | 4.0167 | 1352.6971 | 0.1236 | 4733.3333 | 3.1833 | 1486.911 | 0.21847 | 4466.6667 | 2.75 | 1624.2424 | 0.24942 | 4133.3333 | 2.2833 | 1810.219 | 0.28482 | 3666.6667 | 1.8667 | 1964.2857 | 0.32913 | 3166.6667 | 1.4167 | 2235.2941 | 0.37088
| 0 |  | 3.302 | max | 16411.1111 | 3.1278 | 5246.8917 | 4.0476 | 16211.1111 | 2.8889 | 5611.5385 | 3.3347 | 15933.3333 | 2.65 | 6012.5786 | 2.904 | 15733.3333 | 2.4111 | 6525.3456 | 2.4634 | 15011.1111 | 2.3611 | 6357.6471 | 2.1337 | 14233.3333 | 2.2611 | 6294.8403 | 1.7871
|  | 5822.6087 | 35.3796 | nom | 14000 | 3.3222 | 4214.0468 | 1438.5382 | 14000 | 3.0722 | 4556.962 | 1746.0904 | 14000 | 2.8222 | 4960.6299 | 2005.0245 | 14000 | 2.5722 | 5442.7646 | 2363.6839 | 14000 | 2.4611 | 5688.4876 | 2728.87 | 14000 | 2.3 | 6086.9565 | 3258.067
|  |  | 100 | mid | 11200 | 3.5611 | 3145.0858 | 1 | 11200 | 3.3111 | 3382.5503 | 1 | 11200 | 3.0611 | 3658.8022 | 1 | 11200 | 2.8111 | 3984.1897 | 1 | 11200 | 2.65 | 4226.4151 | 1 | 11200 | 2.45 | 4571.4286 | 1
|  |  | 1763.3781 | min | 5488.8889 | 4.0778 | 1346.049 | 0.058433 | 4855.5556 | 3.3389 | 1454.2429 | 0.15243 | 4544.4444 | 2.8667 | 1585.2713 | 0.19204 | 4155.5556 | 2.3556 | 1764.1509 | 0.23665 | 3677.7778 | 1.9278 | 1907.781 | 0.28513 | 3177.7778 | 1.4611 | 2174.9049 | 0.32969
| 1 |  | 3.507 | max | 16455.5556 | 3.1889 | 5160.2787 | 4.1389 | 16255.5556 | 2.9444 | 5520.7547 | 3.4828 | 15966.6667 | 2.7 | 5913.5802 | 2.9996 | 15766.6667 | 2.4556 | 6420.8145 | 2.5083 | 15055.5556 | 2.4056 | 6258.6605 | 2.1603 | 14266.6667 | 2.3056 | 6187.9518 | 1.7923
|  | 5499.1304 | 34.632 | nom | 14000 | 3.3611 | 4165.2893 | 1328.649 | 14000 | 3.1111 | 4500 | 1578.9363 | 14000 | 2.8611 | 4893.2039 | 1833.2713 | 14000 | 2.6111 | 5361.7021 | 2192.3983 | 14000 | 2.5056 | 5587.5831 | 2545.5723 | 14000 | 2.35 | 5957.4468 | 3068.1408
|  |  | 100 | mid | 11200 | 3.6056 | 3106.3174 | 0 | 11200 | 3.3556 | 3337.7483 | 1 | 11200 | 3.1056 | 3606.4401 | 1 | 11200 | 2.8556 | 3922.179 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.5 | 4480 | 1
|  |  | 1568.0654 | min | 5544.4444 | 4.1389 | 1339.5973 | 0 | 4977.7778 | 3.4944 | 1424.4833 | 0.083789 | 4622.2222 | 2.9833 | 1549.3482 | 0.13331 | 4177.7778 | 2.4278 | 1720.8238 | 0.18817 | 3688.8889 | 1.9889 | 1854.7486 | 0.24101 | 3188.8889 | 1.5056 | 2118.0812 | 0.28838
14kW-Maximum heating CAP | 2 |  | 3.7092 | max | 16500 | 3.25 | 5076.9231 | 4.2 | 16300 | 3 | 5433.3333 | 3.6469 | 16000 | 2.75 | 5818.1818 | 3.1037 | 15800 | 2.5 | 6320 | 2.5558 | 15100 | 2.45 | 6163.2653 | 2.1877 | 14300 | 2.35 | 6085.1064 | 1.797
|  | 5175.6522 | 33.8742 | nom | 14000 | 3.4 | 4117.6471 | 1232.2981 | 14000 | 3.15 | 4444.4444 | 1419.1924 | 14000 | 2.9 | 4827.5862 | 1667.597 | 14000 | 2.65 | 5283.0189 | 2025.0999 | 14000 | 2.55 | 5490.1961 | 2365.7663 | 14000 | 2.4 | 5833.3333 | 2880.2323
|  |  | 100 | mid | 11200 | 3.65 | 3068.4932 | 0 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 3.15 | 3555.5556 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.55 | 4392.1569 | 1
|  |  | 1395.3669 | min | 5600 | 4.2 | 1333.3333 | 0 | 5100 | 3.65 | 1397.2603 | 0.012402 | 4700 | 3.1 | 1516.129 | 0.073177 | 4200 | 2.5 | 1680 | 0.13938 | 3700 | 2.05 | 1804.878 | 0.19675 | 3200 | 1.55 | 2064.5161 | 0.24696
| 3 |  | 3.9748 | max | 16560 | 3.54 | 4677.9661 | 4.68 | 16360 | 3.25 | 5033.8462 | 3.81 | 16080 | 2.96 | 5432.4324 | 3.191 | 15860 | 2.66 | 5962.406 | 2.5786 | 15160 | 2.54 | 5968.5039 | 2.1875 | 14360 | 2.38 | 6033.6134 | 1.7762
|  | 4852.1739 | 33.1053 | nom | 14000 | 3.7 | 3783.7838 | 1036.7893 | 14000 | 3.41 | 4105.5718 | 1273.5365 | 14000 | 3.12 | 4487.1795 | 1520.5627 | 14000 | 2.82 | 4964.539 | 1881.6741 | 14000 | 2.67 | 5243.4457 | 2218.1266 | 14000 | 2.47 | 5668.0162 | 2731.7667
|  |  | 96.9048 | mid | 11200 | 3.97 | 2821.1587 | 0 | 11200 | 3.68 | 3043.4783 | 0 | 11200 | 3.39 | 3303.8348 | 1 | 11200 | 3.09 | 3624.5955 | 1 | 11200 | 2.88 | 3888.8889 | 1 | 11200 | 2.62 | 4274.8092 | 1
|  |  | 1220.7231 | min | 5380 | 4.68 | 1149.5726 | 0 | 4920 | 3.81 | 1291.3386 | 0 | 4500 | 3.18 | 1415.0943 | 0.052563 | 4000 | 2.51 | 1593.6255 | 0.11836 | 3500 | 2.04 | 1715.6863 | 0.17561 | 3000 | 1.53 | 1960.7843 | 0.22587
| 4 |  | 4.2884 | max | 16620 | 3.83 | 4339.4256 | 5.16 | 16420 | 3.5 | 4691.4286 | 3.97 | 16160 | 3.17 | 5097.7918 | 3.2723 | 15920 | 2.82 | 5645.3901 | 2.5948 | 15220 | 2.63 | 5787.0722 | 2.1824 | 14420 | 2.41 | 5983.4025 | 1.7528
|  | 4528.6957 | 32.3246 | nom | 14000 | 4 | 3500 | 877.6542 | 14000 | 3.67 | 3814.7139 | 1140.7294 | 14000 | 3.34 | 4191.6168 | 1383.9643 | 14000 | 2.99 | 4682.2742 | 1745.2704 | 14000 | 2.79 | 5017.9211 | 2075.0793 | 14000 | 2.54 | 5511.811 | 2583.6324
|  |  | 93.3296 | mid | 11200 | 4.29 | 2610.7226 | 0 | 11200 | 3.96 | 2828.2828 | 0 | 11200 | 3.63 | 3085.3994 | 1 | 11200 | 3.28 | 3414.6341 | 1 | 11200 | 3.01 | 3720.9302 | 1 | 11200 | 2.69 | 4163.5688 | 1
|  |  | 1056.0399 | min | 5160 | 5.16 | 1000 | 0 | 4740 | 3.97 | 1193.9547 | 0 | 4300 | 3.26 | 1319.0184 | 0.033144 | 3800 | 2.52 | 1507.9365 | 0.098472 | 3300 | 2.03 | 1625.6158 | 0.15553 | 2800 | 1.51 | 1854.3046 | 0.2058
| 5 |  | 4.6538 | max | 16680 | 4.12 | 4048.5437 | 5.64 | 16480 | 3.75 | 4394.6667 | 4.13 | 16240 | 3.38 | 4804.7337 | 3.3479 | 15980 | 2.98 | 5362.4161 | 2.6049 | 15280 | 2.72 | 5617.6471 | 2.1728 | 14480 | 2.44 | 5934.4262 | 1.727
|  | 4205.2174 | 31.5308 | nom | 14000 | 4.3 | 3255.814 | 745.6059 | 14000 | 3.93 | 3562.341 | 1018.2124 | 14000 | 3.56 | 3932.5843 | 1256.0933 | 14000 | 3.16 | 4430.3797 | 1614.3762 | 14000 | 2.91 | 4810.9966 | 1935.3729 | 14000 | 2.61 | 5363.9847 | 2434.9142
|  |  | 89.6285 | mid | 11200 | 4.61 | 2429.5011 | 0 | 11200 | 4.24 | 2641.5094 | 0 | 11200 | 3.87 | 2894.0568 | 1 | 11200 | 3.47 | 3227.6657 | 1 | 11200 | 3.14 | 3566.879 | 1 | 11200 | 2.76 | 4057.971 | 1
|  |  | 903.6006 | min | 4940 | 5.64 | 875.8865 | 0 | 4560 | 4.13 | 1104.1162 | 0 | 4100 | 3.34 | 1227.5449 | 0.014819 | 3600 | 2.53 | 1422.9249 | 0.079634 | 3100 | 2.02 | 1534.6535 | 0.13645 | 2600 | 1.49 | 1744.9664 | 0.18665
| 6 |  | 5.0727 | max | 16740 | 4.41 | 3795.9184 | 6.12 | 16540 | 4 | 4135 | 4.29 | 16320 | 3.59 | 4545.961 | 3.42 | 16040 | 3.14 | 5108.2803 | 2.6092 | 15340 | 2.81 | 5459.0747 | 2.159 | 14540 | 2.47 | 5886.6397 | 1.699
|  | 3881.7391 | 30.7228 | nom | 14000 | 4.6 | 3043.4783 | 634.2711 | 14000 | 4.19 | 3341.2888 | 904.8343 | 14000 | 3.78 | 3703.7037 | 1135.0114 | 14000 | 3.33 | 4204.2042 | 1487.7279 | 14000 | 3.03 | 4620.462 | 1797.9046 | 14000 | 2.68 | 5223.8806 | 2284.7252
|  |  | 85.7763 | mid | 11200 | 4.93 | 2271.8053 | 0 | 11200 | 4.52 | 2477.8761 | 0 | 11200 | 4.11 | 2725.0608 | 0 | 11200 | 3.66 | 3060.1093 | 1 | 11200 | 3.27 | 3425.0765 | 1 | 11200 | 2.83 | 3957.5972 | 1
|  |  | 765.2186 | min | 4720 | 6.12 | 771.2418 | 0 | 4380 | 4.29 | 1020.979 | 0 | 3900 | 3.42 | 1140.3509 | 0 | 3400 | 2.54 | 1338.5827 | 0.061761 | 2900 | 2.01 | 1442.7861 | 0.11828 | 2400 | 1.47 | 1632.6531 | 0.16838
| 7 |  | 5.5467 | max | 16800 | 4.7 | 3574.4681 | 6.6 | 16600 | 4.25 | 3905.8824 | 4.45 | 16400 | 3.8 | 4315.7895 | 3.5 | 16100 | 3.3 | 4878.7879 | 2.6082 | 15400 | 2.9 | 5310.3448 | 2.1414 | 14600 | 2.5 | 5840 | 1.6688
|  | 3558.2609 | 29.8992 | nom | 14000 | 4.9 | 2857.1429 | 539.1304 | 14000 | 4.45 | 3146.0674 | 799.6092 | 14000 | 4 | 3500 | 1016.646 | 14000 | 3.5 | 4000 | 1364.2501 | 14000 | 3.15 | 4444.4444 | 1661.6822 | 14000 | 2.75 | 5090.9091 | 2132.1878
|  |  | 81.7423 | mid | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.8 | 2333.3333 | 0 | 11200 | 4.35 | 2574.7126 | 0 | 11200 | 3.85 | 2909.0909 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 2.9 | 3862.069 | 1
|  |  | 641.5116 | min | 4500 | 6.6 | 681.8182 | 0 | 4200 | 4.45 | 943.8202 | 0 | 3700 | 3.5 | 1057.1429 | 0 | 3200 | 2.55 | 1254.902 | 0.044783 | 2700 | 2 | 1350 | 0.10097 | 2200 | 1.45 | 1517.2414 | 0.15092
| 8 |  | 5.5917 | max | 16860 | 4.81 | 3505.1975 | 6.31 | 16640 | 4.38 | 3799.0868 | 4.54 | 16440 | 3.93 | 4183.2061 | 3.73 | 16160 | 3.48 | 4643.6782 | 2.91 | 15440 | 3.06 | 5045.7516 | 2.3454 | 14640 | 2.64 | 5545.4545 | 1.8426
|  | 3234.7826 | 29.058 | nom | 14000 | 5.02 | 2788.8446 | 512.6438 | 14000 | 4.59 | 3050.1089 | 712.5072 | 14000 | 4.16 | 3365.3846 | 867.2339 | 14000 | 3.69 | 3794.0379 | 1111.6091 | 14000 | 3.32 | 4216.8675 | 1379.2081 | 14000 | 2.9 | 4827.5862 | 1755.5843
|  |  | 67.53 | mid | 11200 | 5.37 | 2085.6611 | 0 | 11200 | 4.95 | 2262.6263 | 0 | 11200 | 4.53 | 2472.4062 | 0 | 11200 | 4.06 | 2758.6207 | 0 | 11200 | 3.58 | 3128.4916 | 1 | 11200 | 3.06 | 3660.1307 | 1
|  |  | 578.4932 | min | 4920 | 6.31 | 779.7147 | 0 | 4600 | 4.54 | 1013.2159 | 0 | 4120 | 3.73 | 1104.5576 | 0 | 3640 | 2.91 | 1250.8591 | 0 | 3200 | 2.34 | 1367.5214 | 0.0043478 | 2760 | 1.77 | 1559.322 | 0.056254
| 9 |  | 5.5756 | max | 16920 | 4.92 | 3439.0244 | 6.02 | 16680 | 4.51 | 3698.4479 | 4.63 | 16480 | 4.06 | 4059.1133 | 3.96 | 16220 | 3.66 | 4431.694 | 3.27 | 15480 | 3.22 | 4807.4534 | 2.68 | 14680 | 2.78 | 5280.5755 | 2.09
|  | 2911.3043 | 28.1971 | nom | 14000 | 5.14 | 2723.7354 | 483.6054 | 14000 | 4.73 | 2959.8309 | 628.7914 | 14000 | 4.32 | 3240.7407 | 735.1779 | 14000 | 3.88 | 3608.2474 | 890.3071 | 14000 | 3.49 | 4011.4613 | 1086.3076 | 14000 | 3.05 | 4590.1639 | 1392.9686
|  |  | 55.6517 | mid | 11200 | 5.49 | 2040.0729 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.71 | 2377.9193 | 0 | 11200 | 4.27 | 2622.9508 | 0 | 11200 | 3.76 | 2978.7234 | 0 | 11200 | 3.22 | 3478.2609 | 0
|  |  | 522.1508 | min | 5340 | 6.02 | 887.0432 | 0 | 5000 | 4.63 | 1079.9136 | 0 | 4540 | 3.96 | 1146.4646 | 0 | 4080 | 3.27 | 1247.7064 | 0 | 3700 | 2.68 | 1380.597 | 0 | 3320 | 2.09 | 1588.5167 | 0
| 10 |  | 5.4963 | max | 16980 | 5.03 | 3375.7455 | 5.73 | 16720 | 4.64 | 3603.4483 | 4.72 | 16520 | 4.19 | 3942.7208 | 4.19 | 16280 | 3.84 | 4239.5833 | 3.63 | 15520 | 3.38 | 4591.716 | 3.02 | 14720 | 2.92 | 5041.0959 | 2.41
|  | 2587.8261 | 27.3139 | nom | 14000 | 5.26 | 2661.597 | 451.6276 | 14000 | 4.87 | 2874.7433 | 548.2682 | 14000 | 4.48 | 3125 | 617.6196 | 14000 | 4.07 | 3439.8034 | 712.8997 | 14000 | 3.66 | 3825.1366 | 856.8961 | 14000 | 3.2 | 4375 | 1073.7868
|  |  | 45.5868 | mid | 11200 | 5.61 | 1996.4349 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.89 | 2290.3885 | 0 | 11200 | 4.48 | 2500 | 0 | 11200 | 3.94 | 2842.6396 | 0 | 11200 | 3.38 | 3313.6095 | 0
|  |  | 470.8305 | min | 5760 | 5.73 | 1005.2356 | 0 | 5400 | 4.72 | 1144.0678 | 0 | 4960 | 4.19 | 1183.7709 | 0 | 4520 | 3.63 | 1245.1791 | 0 | 4200 | 3.02 | 1390.7285 | 0 | 3880 | 2.41 | 1609.9585 | 0
| 11 |  | 5.3515 | max | 17040 | 5.14 | 3315.1751 | 5.44 | 16760 | 4.77 | 3513.6268 | 4.81 | 16560 | 4.32 | 3833.3333 | 4.42 | 16340 | 4.02 | 4064.6766 | 3.99 | 15560 | 3.54 | 4395.4802 | 3.36 | 14760 | 3.06 | 4823.5294 | 2.73
|  | 2264.3478 | 26.4047 | nom | 14000 | 5.38 | 2602.2305 | 416.2404 | 14000 | 5.01 | 2794.4112 | 470.7584 | 14000 | 4.64 | 3017.2414 | 512.2959 | 14000 | 4.26 | 3286.385 | 567.5057 | 14000 | 3.83 | 3655.3525 | 673.913 | 14000 | 3.35 | 4179.1045 | 829.4314
|  |  | 36.9592 | mid | 11200 | 5.73 | 1954.6248 | 0 | 11200 | 5.4 | 2074.0741 | 0 | 11200 | 5.07 | 2209.073 | 0 | 11200 | 4.69 | 2388.0597 | 0 | 11200 | 4.12 | 2718.4466 | 0 | 11200 | 3.54 | 3163.8418 | 0
|  |  | 423.1235 | min | 6180 | 5.44 | 1136.0294 | 0 | 5800 | 4.81 | 1205.8212 | 0 | 5380 | 4.42 | 1217.1946 | 0 | 4960 | 3.99 | 1243.1078 | 0 | 4700 | 3.36 | 1398.8095 | 0 | 4440 | 2.73 | 1626.3736 | 0
| 12 |  | 5.1384 | max | 17100 | 5.25 | 3257.1429 | 5.15 | 16800 | 4.9 | 3428.5714 | 4.9 | 16600 | 4.45 | 3730.3371 | 4.65 | 16400 | 4.2 | 3904.7619 | 4.35 | 15600 | 3.7 | 4216.2162 | 3.7 | 14800 | 3.2 | 4625 | 3.05
|  | 1940.8696 | 25.4649 | nom | 14000 | 5.5 | 2545.4545 | 376.8679 | 14000 | 5.15 | 2718.4466 | 396.0958 | 14000 | 4.8 | 2916.6667 | 417.3913 | 14000 | 4.45 | 3146.0674 | 446.1769 | 14000 | 4 | 3500 | 524.5593 | 14000 | 3.5 | 4000 | 636.3507
|  |  | 29.4902 | mid | 11200 | 5.85 | 1914.5299 | 0 | 11200 | 5.55 | 2018.018 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.9 | 2285.7143 | 0 | 11200 | 4.3 | 2604.6512 | 0 | 11200 | 3.7 | 3027.027 | 0
|  |  | 377.7203 | min | 6600 | 5.15 | 1281.5534 | 0 | 6200 | 4.9 | 1265.3061 | 0 | 5800 | 4.65 | 1247.3118 | 0 | 5400 | 4.35 | 1241.3793 | 0 | 5200 | 3.7 | 1405.4054 | 0 | 5000 | 3.05 | 1639.3443 | 0
| 13 |  | 5.15 | max | 17566.6667 | 5.2833 | 3324.9211 | 5.15 | 17266.6667 | 4.9333 | 3500 | 4.9667 | 17033.3333 | 4.55 | 3743.5897 | 4.7833 | 16833.3333 | 4.3 | 3914.7287 | 4.55 | 16033.3333 | 3.8 | 4219.2982 | 3.9167 | 15200 | 3.3 | 4606.0606 | 3.2667
|  | 1617.3913 | 24.488 | nom | 14000 | 5.5 | 2545.4545 | 314.0566 | 14000 | 5.1833 | 2700.9646 | 325.6493 | 14000 | 4.8667 | 2876.7123 | 338.1306 | 14000 | 4.55 | 3076.9231 | 355.4706 | 14000 | 4.1 | 3414.6341 | 412.951 | 14000 | 3.6167 | 3870.9677 | 495.1198
|  |  | 24.1402 | mid | 11200 | 5.9 | 1898.3051 | 0 | 11200 | 5.5833 | 2005.9701 | 0 | 11200 | 5.3167 | 2106.5831 | 0 | 11200 | 5.0167 | 2232.5581 | 0 | 11200 | 4.4167 | 2535.8491 | 0 | 11200 | 3.8167 | 2934.4978 | 0
|  |  | 314.0566 | min | 6700 | 5.15 | 1300.9709 | 0 | 6266.6667 | 4.9667 | 1261.745 | 0 | 5833.3333 | 4.7833 | 1219.5122 | 0 | 5400 | 4.55 | 1186.8132 | 0 | 5233.3333 | 3.9167 | 1336.1702 | 0 | 5066.6667 | 3.2667 | 1551.0204 | 0
| 14 |  | 5.15 | max | 18033.3333 | 5.3167 | 3391.8495 | 5.15 | 17733.3333 | 4.9667 | 3570.4698 | 5.0333 | 17466.6667 | 4.65 | 3756.2724 | 4.9167 | 17266.6667 | 4.4 | 3924.2424 | 4.75 | 16466.6667 | 3.9 | 4222.2222 | 4.1333 | 15600 | 3.4 | 4588.2353 | 3.4833
|  | 1293.913 | 23.4647 | nom | 14000 | 5.5 | 2545.4545 | 251.2453 | 14000 | 5.2167 | 2683.7061 | 257.0688 | 14000 | 4.9333 | 2837.8378 | 263.1688 | 14000 | 4.65 | 3010.7527 | 272.4027 | 14000 | 4.2 | 3333.3333 | 313.0435 | 14000 | 3.7333 | 3750 | 371.4583
|  |  | 19.0281 | mid | 11200 | 5.95 | 1882.3529 | 0 | 11200 | 5.6167 | 1994.0653 | 0 | 11200 | 5.3833 | 2080.4954 | 0 | 11200 | 5.1333 | 2181.8182 | 0 | 11200 | 4.5333 | 2470.5882 | 0 | 11200 | 3.9333 | 2847.4576 | 0
|  |  | 251.2453 | min | 6800 | 5.15 | 1320.3883 | 0 | 6333.3333 | 5.0333 | 1258.2781 | 0 | 5866.6667 | 4.9167 | 1193.2203 | 0 | 5400 | 4.75 | 1136.8421 | 0 | 5266.6667 | 4.1333 | 1274.1935 | 0 | 5133.3333 | 3.4833 | 1473.6842 | 0
| 15 |  | 5.15 | max | 18500 | 5.35 | 3457.9439 | 5.15 | 18200 | 5 | 3640 | 5.1 | 17900 | 4.75 | 3768.4211 | 5.05 | 17700 | 4.5 | 3933.3333 | 4.95 | 16900 | 4 | 4225 | 4.35 | 16000 | 3.5 | 4571.4286 | 3.7
|  | 970.4348 | 22.3799 | nom | 14000 | 5.5 | 2545.4545 | 188.4339 | 14000 | 5.25 | 2666.6667 | 190.2813 | 14000 | 5 | 2800 | 192.1653 | 14000 | 4.75 | 2947.3684 | 196.0474 | 14000 | 4.3 | 3255.814 | 223.0885 | 14000 | 3.85 | 3636.3636 | 262.2797
|  |  | 14.0643 | mid | 11200 | 6 | 1866.6667 | 0 | 11200 | 5.65 | 1982.3009 | 0 | 11200 | 5.45 | 2055.0459 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.65 | 2408.6022 | 0 | 11200 | 4.05 | 2765.4321 | 0
|  |  | 188.4339 | min | 6900 | 5.15 | 1339.8058 | 0 | 6400 | 5.1 | 1254.902 | 0 | 5900 | 5.05 | 1168.3168 | 0 | 5400 | 4.95 | 1090.9091 | 0 | 5300 | 4.35 | 1218.3908 | 0 | 5200 | 3.7 | 1405.4054 | 0
| 16 |  | 6.92 | max | 19020 | 5.73 | 3319.3717 | 6.92 | 18720 | 5.3 | 3532.0755 | 5.68 | 18420 | 4.95 | 3721.2121 | 5.37 | 18200 | 4.59 | 3965.1416 | 5.02 | 17380 | 4.08 | 4259.8039 | 4.36 | 16460 | 3.56 | 4623.5955 | 3.65
|  | 646.9565 | 21.2063 | nom | 14000 | 5.93 | 2360.8769 | 93.4908 | 14000 | 5.57 | 2513.465 | 113.9008 | 14000 | 5.21 | 2687.1401 | 120.4761 | 14000 | 4.85 | 2886.5979 | 128.8758 | 14000 | 4.39 | 3189.0661 | 148.3845 | 14000 | 3.92 | 3571.4286 | 177.2484
|  |  | 9.2687 | mid | 11200 | 6.42 | 1744.5483 | 0 | 11200 | 5.99 | 1869.783 | 0 | 11200 | 5.68 | 1971.831 | 0 | 11200 | 5.36 | 2089.5522 | 0 | 11200 | 4.74 | 2362.8692 | 0 | 11200 | 4.12 | 2718.4466 | 0
|  |  | 93.4908 | min | 6980 | 6.92 | 1008.6705 | 0 | 6460 | 5.68 | 1137.3239 | 0 | 6000 | 5.37 | 1117.3184 | 0 | 5520 | 5.02 | 1099.6016 | 0 | 5360 | 4.36 | 1229.3578 | 0 | 5180 | 3.65 | 1419.1781 | 0
| 17 |  | 8.69 | max | 19540 | 6.11 | 3198.036 | 8.69 | 19240 | 5.6 | 3435.7143 | 6.26 | 18940 | 5.15 | 3677.6699 | 5.69 | 18700 | 4.68 | 3995.7265 | 5.09 | 17860 | 4.16 | 4293.2692 | 4.37 | 16920 | 3.62 | 4674.0331 | 3.6
|  | 323.4783 | 19.8812 | nom | 14000 | 6.36 | 2201.2579 | 37.2242 | 14000 | 5.89 | 2376.91 | 51.6738 | 14000 | 5.42 | 2583.0258 | 56.8503 | 14000 | 4.95 | 2828.2828 | 63.5517 | 14000 | 4.48 | 3125 | 74.0225 | 14000 | 3.99 | 3508.7719 | 89.8551
|  |  | 4.5818 | mid | 11200 | 6.84 | 1637.4269 | 0 | 11200 | 6.33 | 1769.3523 | 0 | 11200 | 5.91 | 1895.0931 | 0 | 11200 | 5.47 | 2047.532 | 0 | 11200 | 4.83 | 2318.8406 | 0 | 11200 | 4.19 | 2673.031 | 0
|  |  | 37.2242 | min | 7060 | 8.69 | 812.4281 | 0 | 6520 | 6.26 | 1041.5335 | 0 | 6100 | 5.69 | 1072.0562 | 0 | 5640 | 5.09 | 1108.055 | 0 | 5420 | 4.37 | 1240.2746 | 0 | 5160 | 3.6 | 1433.3333 | 0
| 18 |  | 10.46 | max | 20060 | 6.49 | 3090.9091 | 10.46 | 19760 | 5.9 | 3349.1525 | 6.84 | 19460 | 5.35 | 3637.3832 | 6.01 | 19200 | 4.77 | 4025.1572 | 5.16 | 18340 | 4.24 | 4325.4717 | 4.38 | 17380 | 3.68 | 4722.8261 | 3.55
|  | 0 | 18 | nom | 14000 | 6.79 | 2061.8557 | 0 | 14000 | 6.21 | 2254.4283 | 0 | 14000 | 5.63 | 2486.6785 | 0 | 14000 | 5.05 | 2772.2772 | 0 | 14000 | 4.57 | 3063.4573 | 0 | 14000 | 4.06 | 3448.2759 | 0
|  |  | 0 | mid | 11200 | 7.26 | 1542.6997 | 0 | 11200 | 6.67 | 1679.1604 | 0 | 11200 | 6.14 | 1824.1042 | 0 | 11200 | 5.58 | 2007.1685 | 0 | 11200 | 4.92 | 2276.4228 | 0 | 11200 | 4.26 | 2629.108 | 0
|  |  | 0 | min | 7140 | 10.46 | 682.6004 | 0 | 6580 | 6.84 | 961.9883 | 0 | 6200 | 6.01 | 1031.614 | 0 | 5760 | 5.16 | 1116.2791 | 0 | 5480 | 4.38 | 1251.1416 | 0 | 5140 | 3.55 | 1447.8873 | 0
| 19 |  | #NUM! | max | 20580 | 6.87 | 2995.6332 | 12.23 | 20280 | 6.2 | 3270.9677 | 7.42 | 19980 | 5.55 | 3600 | 6.33 | 19700 | 4.86 | 4053.4979 | 5.23 | 18820 | 4.32 | 4356.4815 | 4.39 | 17840 | 3.74 | 4770.0535 | 3.5
|  | -323.4783 | #NUM! | nom | 14000 | 7.22 | 1939.0582 | -26.4496 | 14000 | 6.53 | 2143.951 | -43.5955 | 14000 | 5.84 | 2397.2603 | -51.1024 | 14000 | 5.15 | 2718.4466 | -61.8505 | 14000 | 4.66 | 3004.2918 | -73.6853 | 14000 | 4.13 | 3389.8305 | -92.4224
|  |  |  | mid | 11200 | 7.68 | 1458.3333 | 0 | 11200 | 7.01 | 1597.7175 | 0 | 11200 | 6.37 | 1758.2418 | 0 | 11200 | 5.69 | 1968.3656 | 0 | 11200 | 5.01 | 2235.5289 | 0 | 11200 | 4.33 | 2586.6051 | 0
|  |  | #NUM! | min | 7220 | 12.23 | 590.3516 | 0 | 6640 | 7.42 | 894.8787 | 0 | 6300 | 6.33 | 995.2607 | 0 | 5880 | 5.23 | 1124.283 | 0 | 5540 | 4.39 | 1261.959 | 0 | 5120 | 3.5 | 1462.8571 | 0
| 20 |  | #NUM! | max | 21100 | 7.25 | 2910.3448 | 14 | 20800 | 6.5 | 3200 | 8 | 20500 | 5.75 | 3565.2174 | 6.65 | 20200 | 4.95 | 4080.8081 | 5.3 | 19300 | 4.4 | 4386.3636 | 4.4 | 18300 | 3.8 | 4815.7895 | 3.45
|  | -646.9565 | #NUM! | nom | 14000 | 7.65 | 1830.0654 | -46.2112 | 14000 | 6.85 | 2043.7956 | -80.8696 | 14000 | 6.05 | 2314.0496 | -97.2867 | 14000 | 5.25 | 2666.6667 | -122.0673 | 14000 | 4.75 | 2947.3684 | -147.0356 | 14000 | 4.2 | 3333.3333 | -187.5236
|  |  |  | mid | 11200 | 8.1 | 1382.716 | 0 | 11200 | 7.35 | 1523.8095 | 0 | 11200 | 6.6 | 1696.9697 | 0 | 11200 | 5.8 | 1931.0345 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.4 | 2545.4545 | 0
|  |  | #NUM! | min | 7300 | 14 | 521.4286 | 0 | 6700 | 8 | 837.5 | 0 | 6400 | 6.65 | 962.406 | 0 | 6000 | 5.3 | 1132.0755 | 0 | 5600 | 4.4 | 1272.7273 | 0 | 5100 | 3.45 | 1478.2609 | 0
Indoor Temp. |  | 19
LWT |  |  | 25 CAP: 25; 35 CAP: 35; 40 CAP: 40; 45 CAP: 45; 50 CAP: 50; 55 CAP: 55
Outdoor air temperature[℃] |  | Heating Demand | COP | CL | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP
|  |  | LWT |  |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI
| -15 |  | 1.8297 | max | - | - | - | - | 14000 | 1.85 | 7567.5676 | 2.3002 | 13500 | 1.7 | 7941.1765 | 2.1002 | 13100 | 1.55 | 8451.6129 | 1.9002 | 12600 | 1.45 | 8689.6552 | 1.7501 | 12200 | 1.3 | 9384.6154 | 1.6001
|  | 10998.2609 | 47.3469 | nom | - | - | - | - | 11000 | 2.3 | 4782.6087 | 4781.5239 | 11000 | 2.1 | 5238.0952 | 5236.8728 | 11000 | 1.9 | 5789.4737 | 5788.0767 | 11000 | 1.75 | 6285.7143 | 6284.2947 | 11000 | 1.6 | 6875 | 6873.5734
|  |  | 100 | mid | - | - | - | - | 8800 | 2.5 | 3520 | 2 | 8800 | 2.3 | 3826.087 | 2 | 8800 | 2.1 | 4190.4762 | 2 | 8800 | 1.9 | 4631.5789 | 2 | 8800 | 1.7 | 5176.4706 | 2
|  |  | 6010.8568 | min | - | - | - | - | 7800 | 2.35 | 3319.1489 | 0.99921 | 7200 | 2 | 3600 | 0.99921 | 6500 | 1.6 | 4062.5 | 0.99921 | 5700 | 1.3 | 4384.6154 | 0.99921 | 4800 | 1 | 4800 | 0.99921
| -14 |  | 2.0229 | max | 14280 | 2.08 | 6865.3846 | 2.6749 | 14080 | 1.93 | 7295.3368 | 2.5122 | 13640 | 1.78 | 7662.9213 | 2.3087 | 13280 | 1.62 | 8197.5309 | 2.0947 | 12880 | 1.53 | 8418.3007 | 1.884 | 12560 | 1.39 | 9035.9712 | 1.6732
|  | 10674.7826 | 46.7034 | nom | 14000 | 2.64 | 5303.0303 | 3990.7109 | 14000 | 2.34 | 5982.906 | 4249.1589 | 14000 | 2.12 | 6603.7736 | 4623.7933 | 14000 | 1.9 | 7368.4211 | 5096.0574 | 14000 | 1.77 | 7909.6045 | 5666.0534 | 14000 | 1.63 | 8588.9571 | 6380.0328
|  |  | 100 | mid | 11200 | 2.69 | 4163.5688 | 1 | 11200 | 2.54 | 4409.4488 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.15 | 5209.3023 | 1 | 11200 | 1.94 | 5773.1959 | 1 | 11200 | 1.73 | 6473.9884 | 1
|  |  | 5276.9026 | min | 7720 | 2.59 | 2980.695 | 0.84908 | 7420 | 2.34 | 3170.9402 | 0.86105 | 6880 | 2.01 | 3422.8856 | 0.87842 | 6260 | 1.63 | 3840.4908 | 0.89368 | 5480 | 1.33 | 4120.3008 | 0.90818 | 4640 | 1.02 | 4549.0196 | 0.91994
| -13 |  | 2.0651 | max | 14360 | 2.16 | 6648.1481 | 2.697 | 14160 | 2.01 | 7044.7761 | 2.529 | 13780 | 1.86 | 7408.6022 | 2.3305 | 13460 | 1.69 | 7964.497 | 2.1115 | 13160 | 1.61 | 8173.913 | 1.8914 | 12920 | 1.48 | 8729.7297 | 1.6691
|  | 10351.3043 | 46.0553 | nom | 14000 | 2.68 | 5223.8806 | 3838.0531 | 14000 | 2.38 | 5882.3529 | 4093.0479 | 14000 | 2.14 | 6542.0561 | 4441.6767 | 14000 | 1.9 | 7368.4211 | 4902.2861 | 14000 | 1.79 | 7821.2291 | 5472.7815 | 14000 | 1.66 | 8433.7349 | 6201.8458
|  |  | 100 | mid | 11200 | 2.73 | 4102.5641 | 1 | 11200 | 2.58 | 4341.0853 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.2 | 5090.9091 | 1 | 11200 | 1.98 | 5656.5657 | 1 | 11200 | 1.76 | 6363.6364 | 1
|  |  | 5012.5706 | min | 7340 | 2.58 | 2844.9612 | 0.78013 | 7040 | 2.33 | 3021.4592 | 0.79599 | 6560 | 2.02 | 3247.5248 | 0.81709 | 6020 | 1.66 | 3626.506 | 0.83616 | 5260 | 1.36 | 3867.6471 | 0.85712 | 4480 | 1.04 | 4307.6923 | 0.87371
| -12 |  | 2.1105 | max | 14440 | 2.24 | 6446.4286 | 2.7147 | 14240 | 2.09 | 6813.3971 | 2.5425 | 13920 | 1.94 | 7175.2577 | 2.3507 | 13640 | 1.76 | 7750 | 2.1289 | 13440 | 1.69 | 7952.6627 | 1.9001 | 13280 | 1.57 | 8458.5987 | 1.6656
|  | 10027.8261 | 45.4026 | nom | 14000 | 2.72 | 5147.0588 | 3693.8865 | 14000 | 2.42 | 5785.124 | 3944.0135 | 14000 | 2.16 | 6481.4815 | 4265.8107 | 14000 | 1.9 | 7368.4211 | 4710.3547 | 14000 | 1.81 | 7734.8066 | 5277.4738 | 14000 | 1.69 | 8284.0237 | 6020.4516
|  |  | 100 | mid | 11200 | 2.77 | 4043.3213 | 1 | 11200 | 2.62 | 4274.8092 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.25 | 4977.7778 | 1 | 11200 | 2.02 | 5544.5545 | 1 | 11200 | 1.79 | 6256.9832 | 1
|  |  | 4751.4642 | min | 6960 | 2.57 | 2708.1712 | 0.72354 | 6660 | 2.32 | 2870.6897 | 0.74181 | 6240 | 2.03 | 3073.8916 | 0.76367 | 5780 | 1.69 | 3420.1183 | 0.78373 | 5040 | 1.39 | 3625.8993 | 0.80971 | 4320 | 1.06 | 4075.4717 | 0.82963
| -11 |  | 2.1581 | max | 14520 | 2.32 | 6258.6207 | 2.7291 | 14320 | 2.17 | 6599.0783 | 2.5536 | 14060 | 2.02 | 6960.396 | 2.3697 | 13820 | 1.83 | 7551.9126 | 2.1467 | 13720 | 1.77 | 7751.4124 | 1.91 | 13640 | 1.66 | 8216.8675 | 1.6628
|  | 9704.3478 | 44.7449 | nom | 14000 | 2.76 | 5072.4638 | 3555.9222 | 14000 | 2.46 | 5691.0569 | 3800.2586 | 14000 | 2.18 | 6422.0183 | 4095.1851 | 14000 | 1.9 | 7368.4211 | 4520.5144 | 14000 | 1.83 | 7650.2732 | 5080.901 | 14000 | 1.72 | 8139.5349 | 5836.1957
|  |  | 100 | mid | 11200 | 2.81 | 3985.7651 | 1 | 11200 | 2.66 | 4210.5263 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1 | 11200 | 2.06 | 5436.8932 | 1 | 11200 | 1.82 | 6153.8462 | 1
|  |  | 4496.6906 | min | 6580 | 2.56 | 2570.3125 | 0.67627 | 6280 | 2.31 | 2718.6147 | 0.69601 | 5920 | 2.04 | 2901.9608 | 0.71673 | 5540 | 1.72 | 3220.9302 | 0.73575 | 4820 | 1.42 | 3394.3662 | 0.76557 | 4160 | 1.08 | 3851.8519 | 0.78755
| -10 |  | 2.2059 | max | 14600 | 2.4 | 6083.3333 | 2.7409 | 14400 | 2.25 | 6400 | 2.5627 | 14200 | 2.1 | 6761.9048 | 2.3876 | 14000 | 1.9 | 7368.4211 | 2.165 | 14000 | 1.85 | 7567.5676 | 1.9208 | 14000 | 1.75 | 8000 | 1.6605
|  | 9380.8696 | 44.0822 | nom | 14000 | 2.8 | 5000 | 3422.6105 | 14000 | 2.5 | 5600 | 3660.5313 | 14000 | 2.2 | 6363.6364 | 3929.0323 | 14000 | 1.9 | 7368.4211 | 4332.9578 | 14000 | 1.85 | 7567.5676 | 4883.7248 | 14000 | 1.75 | 8000 | 5649.4
|  |  | 100 | mid | 11200 | 2.85 | 3929.8246 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.1 | 5333.3333 | 1 | 11200 | 1.85 | 6054.0541 | 1
|  |  | 4252.7088 | min | 6200 | 2.55 | 2431.3725 | 0.63617 | 5900 | 2.3 | 2565.2174 | 0.65677 | 5600 | 2.05 | 2731.7073 | 0.67516 | 5300 | 1.75 | 3028.5714 | 0.69167 | 4600 | 1.45 | 3172.4138 | 0.72437 | 4000 | 1.1 | 3636.3636 | 0.74734
| -9 |  | 2.2635 | max | 15100 | 2.5 | 6040 | 2.9567 | 14900 | 2.3333 | 6385.7143 | 2.6134 | 14700 | 2.1667 | 6784.6154 | 2.4187 | 14500 | 1.9667 | 7372.8814 | 2.1914 | 14233.3333 | 1.9167 | 7426.087 | 1.9503 | 14000 | 1.8167 | 7706.422 | 1.7
|  | 9057.3913 | 43.4142 | nom | 14000 | 2.8833 | 4855.4913 | 3063.327 | 14000 | 2.6 | 5384.6154 | 3465.7176 | 14000 | 2.3167 | 6043.1655 | 3744.7225 | 14000 | 2.0333 | 6885.2459 | 4133.1952 | 14000 | 1.95 | 7179.4872 | 4643.993 | 14000 | 1.8167 | 7706.422 | 5327.7925
|  |  | 100 | mid | 11200 | 2.9833 | 3754.1899 | 1 | 11200 | 2.8 | 4000 | 1 | 11200 | 2.6167 | 4280.2548 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.1667 | 5169.2308 | 1 | 11200 | 1.9333 | 5793.1034 | 1
|  |  | 4001.5412 | min | 5833.3333 | 2.9167 | 2000 | 0.60076 | 5266.6667 | 2.2833 | 2306.5693 | 0.63889 | 5066.6667 | 2.05 | 2471.5447 | 0.65066 | 4866.6667 | 1.7833 | 2728.972 | 0.66169 | 4266.6667 | 1.4667 | 2909.0909 | 0.69097 | 3700 | 1.1167 | 3313.4328 | 0.71432
| -8 |  | 2.3231 | max | 15600 | 2.6 | 6000 | 3.1884 | 15400 | 2.4167 | 6372.4138 | 2.6622 | 15200 | 2.2333 | 6805.9701 | 2.4491 | 15000 | 2.0333 | 7377.0492 | 2.2192 | 14466.6667 | 1.9833 | 7294.1176 | 1.9788 | 14000 | 1.8833 | 7433.6283 | 1.7374
|  | 8733.913 | 42.7407 | nom | 14000 | 2.9667 | 4719.1011 | 2739.3162 | 14000 | 2.7 | 5185.1852 | 3280.7692 | 14000 | 2.4333 | 5753.4247 | 3566.2379 | 14000 | 2.1667 | 6461.5385 | 3935.6417 | 14000 | 2.05 | 6829.2683 | 4413.7288 | 14000 | 1.8833 | 7433.6283 | 5027.0378
|  |  | 100 | mid | 11200 | 3.1167 | 3593.5829 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.6833 | 4173.913 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.2333 | 5014.9254 | 1 | 11200 | 2.0167 | 5553.719 | 1
|  |  | 3759.6707 | min | 5466.6667 | 3.2833 | 1664.9746 | 0.56987 | 4633.3333 | 2.2667 | 2044.1176 | 0.62445 | 4533.3333 | 2.05 | 2211.3821 | 0.63009 | 4433.3333 | 1.8167 | 2440.367 | 0.63555 | 3933.3333 | 1.4833 | 2651.6854 | 0.66063 | 3400 | 1.1333 | 3000 | 0.68384
| -7 |  | 2.3837 | max | 16100 | 2.7 | 5962.963 | 3.4329 | 15900 | 2.5 | 6360 | 2.7094 | 15700 | 2.3 | 6826.087 | 2.4788 | 15500 | 2.1 | 7380.9524 | 2.2482 | 14700 | 2.05 | 7170.7317 | 2.0064 | 14000 | 1.95 | 7179.4872 | 1.7728
|  | 8410.4348 | 42.0614 | nom | 14000 | 3.05 | 4590.1639 | 2449.9345 | 14000 | 2.8 | 5000 | 3104.1455 | 14000 | 2.55 | 5490.1961 | 3392.9567 | 14000 | 2.3 | 6086.9565 | 3741.0233 | 14000 | 2.15 | 6511.6279 | 4191.8839 | 14000 | 1.95 | 7179.4872 | 4744.0762
|  |  | 100 | mid | 11200 | 3.25 | 3446.1538 | 1 | 11200 | 3 | 3733.3333 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1 | 11200 | 2.1 | 5333.3333 | 1
|  |  | 3528.2984 | min | 5100 | 3.65 | 1397.2603 | 0.54269 | 4000 | 2.25 | 1777.7778 | 0.61256 | 4000 | 2.05 | 1951.2195 | 0.61256 | 4000 | 1.85 | 2162.1622 | 0.61256 | 3600 | 1.5 | 2400 | 0.63295 | 3100 | 1.15 | 2695.6522 | 0.65561
| -6 |  | 2.4525 | max | 16144.4444 | 2.7611 | 5847.0825 | 3.509 | 15944.4444 | 2.5556 | 6239.1304 | 2.7634 | 15733.3333 | 2.35 | 6695.0355 | 2.52 | 15533.3333 | 2.1444 | 7243.5233 | 2.2746 | 14744.4444 | 2.0944 | 7039.7878 | 2.0264 | 14033.3333 | 1.9944 | 7036.2117 | 1.7823
|  | 8086.9565 | 41.376 | nom | 14000 | 3.0889 | 4532.3741 | 2304.6076 | 14000 | 2.8389 | 4931.5068 | 2926.4096 | 14000 | 2.5889 | 5407.7253 | 3209.0463 | 14000 | 2.3389 | 5985.7482 | 3555.3577 | 14000 | 2.1944 | 6379.7468 | 3990.8207 | 14000 | 2 | 7000 | 4537.4975
|  |  | 100 | mid | 11200 | 3.2944 | 3399.6627 | 1 | 11200 | 3.0444 | 3678.8321 | 1 | 11200 | 2.7944 | 4007.9523 | 1 | 11200 | 2.5444 | 4401.7467 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.15 | 5209.3023 | 1
|  |  | 3297.4402 | min | 5155.5556 | 3.7111 | 1389.2216 | 0.48497 | 4122.2222 | 2.4056 | 1713.6259 | 0.56017 | 4077.7778 | 2.1667 | 1882.0513 | 0.56291 | 4022.2222 | 1.9222 | 2092.4855 | 0.56629 | 3611.1111 | 1.5611 | 2313.1673 | 0.58979 | 3111.1111 | 1.1944 | 2604.6512 | 0.61515
| -5 |  | 2.5317 | max | 16188.8889 | 2.8222 | 5736.2205 | 3.5875 | 15988.8889 | 2.6111 | 6123.4043 | 2.8281 | 15766.6667 | 2.4 | 6569.4444 | 2.5679 | 15566.6667 | 2.1889 | 7111.6751 | 2.3034 | 14788.8889 | 2.1389 | 6914.2857 | 2.0473 | 14066.6667 | 2.0389 | 6899.1826 | 1.7911
|  | 7763.4783 | 40.6843 | nom | 14000 | 3.1278 | 4476.0213 | 2164.0101 | 14000 | 2.8778 | 4864.8649 | 2745.092 | 14000 | 2.6278 | 5327.6956 | 3023.3146 | 14000 | 2.3778 | 5887.8505 | 3370.4408 | 14000 | 2.2389 | 6253.1017 | 3792.0981 | 14000 | 2.05 | 6829.2683 | 4334.4379
|  |  | 100 | mid | 11200 | 3.3389 | 3354.4093 | 1 | 11200 | 3.0889 | 3625.8993 | 1 | 11200 | 2.8389 | 3945.2055 | 1 | 11200 | 2.5889 | 4326.1803 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.2 | 5090.9091 | 1
|  |  | 3066.5398 | min | 5211.1111 | 3.7722 | 1381.4433 | 0.42618 | 4244.4444 | 2.5611 | 1657.2668 | 0.50593 | 4155.5556 | 2.2833 | 1819.9513 | 0.51217 | 4044.4444 | 1.9944 | 2027.8552 | 0.51974 | 3622.2222 | 1.6222 | 2232.8767 | 0.5465 | 3122.2222 | 1.2389 | 2520.1794 | 0.57457
| -4 |  | 2.6233 | max | 16233.3333 | 2.8833 | 5630.0578 | 3.6685 | 16033.3333 | 2.6667 | 6012.5 | 2.9041 | 15800 | 2.45 | 6448.9796 | 2.6225 | 15600 | 2.2333 | 6985.0746 | 2.3346 | 14833.3333 | 2.1833 | 6793.8931 | 2.069 | 14100 | 2.0833 | 6768 | 1.7994
|  | 7440 | 39.9859 | nom | 14000 | 3.1667 | 4421.0526 | 2028.0758 | 14000 | 2.9167 | 4800 | 2561.9261 | 14000 | 2.6667 | 5250 | 2837.0178 | 14000 | 2.4167 | 5793.1034 | 3186.7844 | 14000 | 2.2833 | 6131.3869 | 3595.8865 | 14000 | 2.1 | 6666.6667 | 4134.6622
|  |  | 100 | mid | 11200 | 3.3833 | 3310.3448 | 1 | 11200 | 3.1333 | 3574.4681 | 1 | 11200 | 2.8833 | 3884.3931 | 1 | 11200 | 2.6333 | 4253.1646 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.25 | 4977.7778 | 1
|  |  | 2836.1595 | min | 5266.6667 | 3.8333 | 1373.913 | 0.36629 | 4366.6667 | 2.7167 | 1607.362 | 0.44976 | 4233.3333 | 2.4 | 1763.8889 | 0.46029 | 4066.6667 | 2.0667 | 1967.7419 | 0.4729 | 3633.3333 | 1.6833 | 2158.4158 | 0.50308 | 3133.3333 | 1.2833 | 2441.5584 | 0.53388
| -3 |  | 2.7284 | max | 16277.7778 | 2.9444 | 5528.3019 | 3.752 | 16077.7778 | 2.7222 | 5906.1224 | 2.9919 | 15833.3333 | 2.5 | 6333.3333 | 2.6841 | 15633.3333 | 2.2778 | 6863.4146 | 2.3683 | 14877.7778 | 2.2278 | 6678.3042 | 2.0917 | 14133.3333 | 2.1278 | 6642.2977 | 1.8072
|  | 7116.5217 | 39.2805 | nom | 14000 | 3.2056 | 4367.4177 | 1896.7347 | 14000 | 2.9556 | 4736.8421 | 2378.6297 | 14000 | 2.7056 | 5174.538 | 2651.3759 | 14000 | 2.4556 | 5701.3575 | 3004.8733 | 14000 | 2.3278 | 6014.3198 | 3402.3447 | 14000 | 2.15 | 6511.6279 | 3937.9449
|  |  | 100 | mid | 11200 | 3.4278 | 3267.423 | 1 | 11200 | 3.1778 | 3524.4755 | 1 | 11200 | 2.9278 | 3825.4269 | 1 | 11200 | 2.6778 | 4182.5726 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1
|  |  | 2608.3347 | min | 5322.2222 | 3.8944 | 1366.6191 | 0.30527 | 4488.8889 | 2.8722 | 1562.8627 | 0.39153 | 4311.1111 | 2.5167 | 1713.0243 | 0.40724 | 4088.8889 | 2.1389 | 1911.6883 | 0.42576 | 3644.4444 | 1.7444 | 2089.172 | 0.45954 | 3144.4444 | 1.3278 | 2368.2008 | 0.49309
| -2 |  | 2.8501 | max | 16322.2222 | 3.0056 | 5430.6839 | 3.8381 | 16122.2222 | 2.7778 | 5804 | 3.0922 | 15866.6667 | 2.55 | 6222.2222 | 2.753 | 15666.6667 | 2.3222 | 6746.4115 | 2.4045 | 14922.2222 | 2.2722 | 6567.2372 | 2.1151 | 14166.6667 | 2.1722 | 6521.7391 | 1.8143
|  | 6793.0435 | 38.5676 | nom | 14000 | 3.2444 | 4315.0685 | 1769.9127 | 14000 | 2.9944 | 4675.3247 | 2196.8541 | 14000 | 2.7444 | 5101.2146 | 2467.5481 | 14000 | 2.4944 | 5612.4722 | 2825.162 | 14000 | 2.3722 | 5901.6393 | 3211.6197 | 14000 | 2.2 | 6363.6364 | 3744.069
|  |  | 100 | mid | 11200 | 3.4722 | 3225.6 | 1 | 11200 | 3.2222 | 3475.8621 | 1 | 11200 | 2.9722 | 3768.2243 | 1 | 11200 | 2.7222 | 4114.2857 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1
|  |  | 2383.4117 | min | 5377.7778 | 3.9556 | 1359.5506 | 0.24308 | 4611.1111 | 3.0278 | 1522.9358 | 0.33115 | 4388.8889 | 2.6333 | 1666.6667 | 0.35298 | 4111.1111 | 2.2111 | 1859.2965 | 0.37833 | 3655.5556 | 1.8056 | 2024.6154 | 0.41587 | 3155.5556 | 1.3722 | 2299.5951 | 0.45217
| -1 |  | 2.9914 | max | 16366.6667 | 3.0667 | 5336.9565 | 3.9268 | 16166.6667 | 2.8333 | 5705.8824 | 3.2057 | 15900 | 2.6 | 6115.3846 | 2.8293 | 15700 | 2.3667 | 6633.8028 | 2.4431 | 14966.6667 | 2.3167 | 6460.4317 | 2.1395 | 14200 | 2.2167 | 6406.015 | 1.821
|  | 6469.5652 | 37.8468 | nom | 14000 | 3.2833 | 4263.9594 | 1647.5329 | 14000 | 3.0333 | 4615.3846 | 2018.1396 | 14000 | 2.7833 | 5029.9401 | 2286.6127 | 14000 | 2.5333 | 5526.3158 | 2648.0721 | 14000 | 2.4167 | 5793.1034 | 3023.8463 | 14000 | 2.25 | 6222.2222 | 3552.8256
|  |  | 100 | mid | 11200 | 3.5167 | 3184.8341 | 1 | 11200 | 3.2667 | 3428.5714 | 1 | 11200 | 3.0167 | 3712.7072 | 1 | 11200 | 2.7667 | 4048.1928 | 1 | 11200 | 2.6 | 4307.6923 | 1 | 11200 | 2.4 | 4666.6667 | 1
|  |  | 2162.7138 | min | 5433.3333 | 4.0167 | 1352.6971 | 0.17969 | 4733.3333 | 3.1833 | 1486.911 | 0.26849 | 4466.6667 | 2.75 | 1624.2424 | 0.29746 | 4133.3333 | 2.2833 | 1810.219 | 0.3306 | 3666.6667 | 1.8667 | 1964.2857 | 0.37207 | 3166.6667 | 1.4167 | 2235.2941 | 0.41115
| 0 |  | 3.1555 | max | 16411.1111 | 3.1278 | 5246.8917 | 4.0183 | 16211.1111 | 2.8889 | 5611.5385 | 3.3332 | 15933.3333 | 2.65 | 6012.5786 | 2.9135 | 15733.3333 | 2.4111 | 6525.3456 | 2.4843 | 15011.1111 | 2.3611 | 6357.6471 | 2.1648 | 14233.3333 | 2.2611 | 6294.8403 | 1.827
|  | 6146.087 | 37.1176 | nom | 14000 | 3.3222 | 4214.0468 | 1529.5154 | 14000 | 3.0722 | 4556.962 | 1843.8785 | 14000 | 2.8222 | 4960.6299 | 2109.5497 | 14000 | 2.5722 | 5442.7646 | 2473.9905 | 14000 | 2.4611 | 5688.4876 | 2839.1479 | 14000 | 2.3 | 6086.9565 | 3364.0125
|  |  | 100 | mid | 11200 | 3.5611 | 3145.0858 | 1 | 11200 | 3.3111 | 3382.5503 | 1 | 11200 | 3.0611 | 3658.8022 | 1 | 11200 | 2.8111 | 3984.1897 | 1 | 11200 | 2.65 | 4226.4151 | 1 | 11200 | 2.45 | 4571.4286 | 1
|  |  | 1947.7682 | min | 5488.8889 | 4.0778 | 1346.049 | 0.11507 | 4855.5556 | 3.3389 | 1454.2429 | 0.20341 | 4544.4444 | 2.8667 | 1585.2713 | 0.24065 | 4155.5556 | 2.3556 | 1764.1509 | 0.28257 | 3677.7778 | 1.9278 | 1907.781 | 0.32814 | 3177.7778 | 1.4611 | 2174.9049 | 0.37001
| 1 |  | 3.3459 | max | 16455.5556 | 3.1889 | 5160.2787 | 4.1127 | 16255.5556 | 2.9444 | 5520.7547 | 3.4756 | 15966.6667 | 2.7 | 5913.5802 | 3.0056 | 15766.6667 | 2.4556 | 6420.8145 | 2.528 | 15055.5556 | 2.4056 | 6258.6605 | 2.1909 | 14266.6667 | 2.3056 | 6187.9518 | 1.8325
|  | 5822.6087 | 36.3796 | nom | 14000 | 3.3611 | 4165.2893 | 1415.7778 | 14000 | 3.1111 | 4500 | 1675.288 | 14000 | 2.8611 | 4893.2039 | 1937.229 | 14000 | 2.6111 | 5361.7021 | 2303.2679 | 14000 | 2.5056 | 5587.5831 | 2657.6358 | 14000 | 2.35 | 5957.4468 | 3177.4344
|  |  | 100 | mid | 11200 | 3.6056 | 3106.3174 | 1 | 11200 | 3.3556 | 3337.7483 | 1 | 11200 | 3.1056 | 3606.4401 | 1 | 11200 | 2.8556 | 3922.179 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.5 | 4480 | 1
|  |  | 1740.211 | min | 5544.4444 | 4.1389 | 1339.5973 | 0.049184 | 4977.7778 | 3.4944 | 1424.4833 | 0.13578 | 4622.2222 | 2.9833 | 1549.3482 | 0.18249 | 4177.7778 | 2.4278 | 1720.8238 | 0.23423 | 3688.8889 | 1.9889 | 1854.7486 | 0.28408 | 3188.8889 | 1.5056 | 2118.0812 | 0.32876
14kW-Maximum heating CAP | 2 |  | 3.567 | max | 16500 | 3.25 | 5076.9231 | 4.2 | 16300 | 3 | 5433.3333 | 3.6336 | 16000 | 2.75 | 5818.1818 | 3.1061 | 15800 | 2.5 | 6320 | 2.5742 | 15100 | 2.45 | 6163.2653 | 2.2179 | 14300 | 2.35 | 6085.1064 | 1.8374
|  | 5499.1304 | 35.632 | nom | 14000 | 3.4 | 4117.6471 | 1309.3168 | 14000 | 3.15 | 4444.4444 | 1513.3935 | 14000 | 2.9 | 4827.5862 | 1770.4024 | 14000 | 2.65 | 5283.0189 | 2136.2184 | 14000 | 2.55 | 5490.1961 | 2479.4101 | 14000 | 2.4 | 5833.3333 | 2992.9011
|  |  | 100 | mid | 11200 | 3.65 | 3068.4932 | 0 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 3.15 | 3555.5556 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.55 | 4392.1569 | 1
|  |  | 1541.6817 | min | 5600 | 4.2 | 1333.3333 | 0 | 5100 | 3.65 | 1397.2603 | 0.065431 | 4700 | 3.1 | 1516.129 | 0.12294 | 4200 | 2.5 | 1680 | 0.18559 | 3700 | 2.05 | 1804.878 | 0.23988 | 3200 | 1.55 | 2064.5161 | 0.28739
| 3 |  | 3.8157 | max | 16560 | 3.54 | 4677.9661 | 4.68 | 16360 | 3.25 | 5033.8462 | 3.8047 | 16080 | 2.96 | 5432.4324 | 3.2012 | 15860 | 2.66 | 5962.406 | 2.6047 | 15160 | 2.54 | 5968.5039 | 2.2228 | 14360 | 2.38 | 6033.6134 | 1.8192
|  | 5175.6522 | 34.8742 | nom | 14000 | 3.7 | 3783.7838 | 1105.9086 | 14000 | 3.41 | 4105.5718 | 1360.3284 | 14000 | 3.12 | 4487.1795 | 1616.7965 | 14000 | 2.82 | 4964.539 | 1987.0394 | 14000 | 2.67 | 5243.4457 | 2328.4397 | 14000 | 2.47 | 5668.0162 | 2845.0115
|  |  | 100 | mid | 11200 | 3.97 | 2821.1587 | 0 | 11200 | 3.68 | 3043.4783 | 1 | 11200 | 3.39 | 3303.8348 | 1 | 11200 | 3.09 | 3624.5955 | 1 | 11200 | 2.88 | 3888.8889 | 1 | 11200 | 2.62 | 4274.8092 | 1
|  |  | 1356.4019 | min | 5380 | 4.68 | 1149.5726 | 0 | 4920 | 3.81 | 1291.3386 | 0.040709 | 4500 | 3.18 | 1415.0943 | 0.10084 | 4000 | 2.51 | 1593.6255 | 0.16329 | 3500 | 2.04 | 1715.6863 | 0.21762 | 3000 | 1.53 | 1960.7843 | 0.26532
| 4 |  | 4.0763 | max | 16620 | 3.83 | 4339.4256 | 5.16 | 16420 | 3.5 | 4691.4286 | 3.9698 | 16160 | 3.17 | 5097.7918 | 3.2896 | 15920 | 2.82 | 5645.3901 | 2.6281 | 15220 | 2.63 | 5787.0722 | 2.2225 | 14420 | 2.41 | 5983.4025 | 1.7983
|  | 4852.1739 | 34.1053 | nom | 14000 | 4 | 3500 | 940.3438 | 14000 | 3.67 | 3814.7139 | 1222.2635 | 14000 | 3.34 | 4191.6168 | 1475 | 14000 | 2.99 | 4682.2742 | 1846.2942 | 14000 | 2.79 | 5017.9211 | 2183.1581 | 14000 | 2.54 | 5511.811 | 2698.2281
|  |  | 100 | mid | 11200 | 4.29 | 2610.7226 | 0 | 11200 | 3.96 | 2828.2828 | 1 | 11200 | 3.63 | 3085.3994 | 1 | 11200 | 3.28 | 3414.6341 | 1 | 11200 | 3.01 | 3720.9302 | 1 | 11200 | 2.69 | 4163.5688 | 1
|  |  | 1190.3358 | min | 5160 | 5.16 | 1000 | 0 | 4740 | 3.97 | 1193.9547 | 0.017364 | 4300 | 3.26 | 1319.0184 | 0.080025 | 3800 | 2.52 | 1507.9365 | 0.14219 | 3300 | 2.03 | 1625.6158 | 0.19648 | 2800 | 1.51 | 1854.3046 | 0.24431
| 5 |  | 4.383 | max | 16680 | 4.12 | 4048.5437 | 5.64 | 16480 | 3.75 | 4394.6667 | 4.13 | 16240 | 3.38 | 4804.7337 | 3.372 | 15980 | 2.98 | 5362.4161 | 2.6449 | 15280 | 2.72 | 5617.6471 | 2.2175 | 14480 | 2.44 | 5934.4262 | 1.7748
|  | 4528.6957 | 33.3246 | nom | 14000 | 4.3 | 3255.814 | 802.9602 | 14000 | 3.93 | 3562.341 | 1096.5365 | 14000 | 3.56 | 3932.5843 | 1343.0291 | 14000 | 3.16 | 4430.3797 | 1712.2597 | 14000 | 2.91 | 4810.9966 | 2042.2086 | 14000 | 2.61 | 5363.9847 | 2551.638
|  |  | 97.946 | mid | 11200 | 4.61 | 2429.5011 | 0 | 11200 | 4.24 | 2641.5094 | 0 | 11200 | 3.87 | 2894.0568 | 1 | 11200 | 3.47 | 3227.6657 | 1 | 11200 | 3.14 | 3566.879 | 1 | 11200 | 2.76 | 4057.971 | 1
|  |  | 1033.2437 | min | 4940 | 5.64 | 875.8865 | 0 | 4560 | 4.13 | 1104.1162 | 0 | 4100 | 3.34 | 1227.5449 | 0.06038 | 3600 | 2.53 | 1422.9249 | 0.1222 | 3100 | 2.02 | 1534.6535 | 0.17638 | 2600 | 1.49 | 1744.9664 | 0.22427
| 6 |  | 4.7419 | max | 16740 | 4.41 | 3795.9184 | 6.12 | 16540 | 4 | 4135 | 4.29 | 16320 | 3.59 | 4545.961 | 3.4488 | 16040 | 3.14 | 5108.2803 | 2.6556 | 15340 | 2.81 | 5459.0747 | 2.2081 | 14540 | 2.47 | 5886.6397 | 1.749
|  | 4205.2174 | 32.5308 | nom | 14000 | 4.6 | 3043.4783 | 687.127 | 14000 | 4.19 | 3341.2888 | 980.2372 | 14000 | 3.78 | 3703.7037 | 1219.3103 | 14000 | 3.33 | 4204.2042 | 1583.5157 | 14000 | 3.03 | 4620.462 | 1904.4149 | 14000 | 2.68 | 5223.8806 | 2404.3716
|  |  | 94.2039 | mid | 11200 | 4.93 | 2271.8053 | 0 | 11200 | 4.52 | 2477.8761 | 0 | 11200 | 4.11 | 2725.0608 | 1 | 11200 | 3.66 | 3060.1093 | 1 | 11200 | 3.27 | 3425.0765 | 1 | 11200 | 2.83 | 3957.5972 | 1
|  |  | 886.8289 | min | 4720 | 6.12 | 771.2418 | 0 | 4380 | 4.29 | 1020.979 | 0 | 3900 | 3.42 | 1140.3509 | 0.041811 | 3400 | 2.54 | 1338.5827 | 0.10323 | 2900 | 2.01 | 1442.7861 | 0.15726 | 2400 | 1.47 | 1632.6531 | 0.20514
| 7 |  | 5.1546 | max | 16800 | 4.7 | 3574.4681 | 6.6 | 16600 | 4.25 | 3905.8824 | 4.45 | 16400 | 3.8 | 4315.7895 | 3.5206 | 16100 | 3.3 | 4878.7879 | 2.6608 | 15400 | 2.9 | 5310.3448 | 2.1946 | 14600 | 2.5 | 5840 | 1.7209
|  | 3881.7391 | 31.7228 | nom | 14000 | 4.9 | 2857.1429 | 588.1423 | 14000 | 4.45 | 3146.0674 | 872.3009 | 14000 | 4 | 3500 | 1102.5798 | 14000 | 3.5 | 4000 | 1458.8712 | 14000 | 3.15 | 4444.4444 | 1768.7367 | 14000 | 2.75 | 5090.9091 | 2255.5834
|  |  | 90.3084 | mid | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.8 | 2333.3333 | 0 | 11200 | 4.35 | 2574.7126 | 1 | 11200 | 3.85 | 2909.0909 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 2.9 | 3862.069 | 1
|  |  | 753.0648 | min | 4500 | 6.6 | 681.8182 | 0 | 4200 | 4.45 | 943.8202 | 0 | 3700 | 3.5 | 1057.1429 | 0.024232 | 3200 | 2.55 | 1254.902 | 0.085217 | 2700 | 2 | 1350 | 0.13903 | 2200 | 1.45 | 1517.2414 | 0.18686
| 8 |  | 5.2658 | max | 16860 | 4.81 | 3505.1975 | 6.31 | 16640 | 4.38 | 3799.0868 | 4.54 | 16440 | 3.93 | 4183.2061 | 3.73 | 16160 | 3.48 | 4643.6782 | 2.91 | 15440 | 3.06 | 5045.7516 | 2.3955 | 14640 | 2.64 | 5545.4545 | 1.892
|  | 3558.2609 | 30.8992 | nom | 14000 | 5.02 | 2788.8446 | 563.9082 | 14000 | 4.59 | 3050.1089 | 783.7579 | 14000 | 4.16 | 3365.3846 | 953.9573 | 14000 | 3.69 | 3794.0379 | 1222.7701 | 14000 | 3.32 | 4216.8675 | 1485.3749 | 14000 | 2.9 | 4827.5862 | 1880.6786
|  |  | 75.208 | mid | 11200 | 5.37 | 2085.6611 | 0 | 11200 | 4.95 | 2262.6263 | 0 | 11200 | 4.53 | 2472.4062 | 0 | 11200 | 4.06 | 2758.6207 | 0 | 11200 | 3.58 | 3128.4916 | 1 | 11200 | 3.06 | 3660.1307 | 1
|  |  | 675.724 | min | 4920 | 6.31 | 779.7147 | 0 | 4600 | 4.54 | 1013.2159 | 0 | 4120 | 3.73 | 1104.5576 | 0 | 3640 | 2.91 | 1250.8591 | 0 | 3200 | 2.34 | 1367.5214 | 0.044783 | 2760 | 1.77 | 1559.322 | 0.094581
| 9 |  | 5.3169 | max | 16920 | 4.92 | 3439.0244 | 6.02 | 16680 | 4.51 | 3698.4479 | 4.63 | 16480 | 4.06 | 4059.1133 | 3.96 | 16220 | 3.66 | 4431.694 | 3.27 | 15480 | 3.22 | 4807.4534 | 2.68 | 14680 | 2.78 | 5280.5755 | 2.09
|  | 3234.7826 | 30.058 | nom | 14000 | 5.14 | 2723.7354 | 537.3393 | 14000 | 4.73 | 2959.8309 | 698.6572 | 14000 | 4.32 | 3240.7407 | 816.8643 | 14000 | 3.88 | 3608.2474 | 989.2302 | 14000 | 3.49 | 4011.4613 | 1207.0084 | 14000 | 3.05 | 4590.1639 | 1547.7429
|  |  | 62.5922 | mid | 11200 | 5.49 | 2040.0729 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.71 | 2377.9193 | 0 | 11200 | 4.27 | 2622.9508 | 0 | 11200 | 3.76 | 2978.7234 | 0 | 11200 | 3.22 | 3478.2609 | 0
|  |  | 608.3916 | min | 5340 | 6.02 | 887.0432 | 0 | 5000 | 4.63 | 1079.9136 | 0 | 4540 | 3.96 | 1146.4646 | 0 | 4080 | 3.27 | 1247.7064 | 0 | 3700 | 2.68 | 1380.597 | 0 | 3320 | 2.09 | 1588.5167 | 0
| 10 |  | 5.3061 | max | 16980 | 5.03 | 3375.7455 | 5.73 | 16720 | 4.64 | 3603.4483 | 4.72 | 16520 | 4.19 | 3942.7208 | 4.19 | 16280 | 3.84 | 4239.5833 | 3.63 | 15520 | 3.38 | 4591.716 | 3.02 | 14720 | 2.92 | 5041.0959 | 2.41
|  | 2911.3043 | 29.1971 | nom | 14000 | 5.26 | 2661.597 | 508.081 | 14000 | 4.87 | 2874.7433 | 616.8018 | 14000 | 4.48 | 3125 | 694.822 | 14000 | 4.07 | 3439.8034 | 802.0122 | 14000 | 3.66 | 3825.1366 | 964.0081 | 14000 | 3.2 | 4375 | 1208.0101
|  |  | 51.9051 | mid | 11200 | 5.61 | 1996.4349 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.89 | 2290.3885 | 0 | 11200 | 4.48 | 2500 | 0 | 11200 | 3.94 | 2842.6396 | 0 | 11200 | 3.38 | 3313.6095 | 0
|  |  | 548.6722 | min | 5760 | 5.73 | 1005.2356 | 0 | 5400 | 4.72 | 1144.0678 | 0 | 4960 | 4.19 | 1183.7709 | 0 | 4520 | 3.63 | 1245.1791 | 0 | 4200 | 3.02 | 1390.7285 | 0 | 3880 | 2.41 | 1609.9585 | 0
| 11 |  | 5.2312 | max | 17040 | 5.14 | 3315.1751 | 5.44 | 16760 | 4.77 | 3513.6268 | 4.81 | 16560 | 4.32 | 3833.3333 | 4.42 | 16340 | 4.02 | 4064.6766 | 3.99 | 15560 | 3.54 | 4395.4802 | 3.36 | 14760 | 3.06 | 4823.5294 | 2.73
|  | 2587.8261 | 28.3139 | nom | 14000 | 5.38 | 2602.2305 | 475.7033 | 14000 | 5.01 | 2794.4112 | 538.0096 | 14000 | 4.64 | 3017.2414 | 585.481 | 14000 | 4.26 | 3286.385 | 648.578 | 14000 | 3.83 | 3655.3525 | 770.1863 | 14000 | 3.35 | 4179.1045 | 947.9216
|  |  | 42.7452 | mid | 11200 | 5.73 | 1954.6248 | 0 | 11200 | 5.4 | 2074.0741 | 0 | 11200 | 5.07 | 2209.073 | 0 | 11200 | 4.69 | 2388.0597 | 0 | 11200 | 4.12 | 2718.4466 | 0 | 11200 | 3.54 | 3163.8418 | 0
|  |  | 494.6881 | min | 6180 | 5.44 | 1136.0294 | 0 | 5800 | 4.81 | 1205.8212 | 0 | 5380 | 4.42 | 1217.1946 | 0 | 4960 | 3.99 | 1243.1078 | 0 | 4700 | 3.36 | 1398.8095 | 0 | 4440 | 2.73 | 1626.3736 | 0
| 12 |  | 5.0899 | max | 17100 | 5.25 | 3257.1429 | 5.15 | 16800 | 4.9 | 3428.5714 | 4.9 | 16600 | 4.45 | 3730.3371 | 4.65 | 16400 | 4.2 | 3904.7619 | 4.35 | 15600 | 3.7 | 4216.2162 | 3.7 | 14800 | 3.2 | 4625 | 3.05
|  | 2264.3478 | 27.4047 | nom | 14000 | 5.5 | 2545.4545 | 439.6792 | 14000 | 5.15 | 2718.4466 | 462.1118 | 14000 | 4.8 | 2916.6667 | 486.9565 | 14000 | 4.45 | 3146.0674 | 520.5397 | 14000 | 4 | 3500 | 611.9859 | 14000 | 3.5 | 4000 | 742.4091
|  |  | 34.8157 | mid | 11200 | 5.85 | 1914.5299 | 0 | 11200 | 5.55 | 2018.018 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.9 | 2285.7143 | 0 | 11200 | 4.3 | 2604.6512 | 0 | 11200 | 3.7 | 3027.027 | 0
|  |  | 444.8722 | min | 6600 | 5.15 | 1281.5534 | 0 | 6200 | 4.9 | 1265.3061 | 0 | 5800 | 4.65 | 1247.3118 | 0 | 5400 | 4.35 | 1241.3793 | 0 | 5200 | 3.7 | 1405.4054 | 0 | 5000 | 3.05 | 1639.3443 | 0
| 13 |  | 5.1231 | max | 17566.6667 | 5.2833 | 3324.9211 | 5.15 | 17266.6667 | 4.9333 | 3500 | 4.9667 | 17033.3333 | 4.55 | 3743.5897 | 4.7833 | 16833.3333 | 4.3 | 3914.7287 | 4.55 | 16033.3333 | 3.8 | 4219.2982 | 3.9167 | 15200 | 3.3 | 4606.0606 | 3.2667
|  | 1940.8696 | 26.4649 | nom | 14000 | 5.5 | 2545.4545 | 376.8679 | 14000 | 5.1833 | 2700.9646 | 390.7791 | 14000 | 4.8667 | 2876.7123 | 405.7567 | 14000 | 4.55 | 3076.9231 | 426.5647 | 14000 | 4.1 | 3414.6341 | 495.5412 | 14000 | 3.6167 | 3870.9677 | 594.1437
|  |  | 29.2453 | mid | 11200 | 5.9 | 1898.3051 | 0 | 11200 | 5.5833 | 2005.9701 | 0 | 11200 | 5.3167 | 2106.5831 | 0 | 11200 | 5.0167 | 2232.5581 | 0 | 11200 | 4.4167 | 2535.8491 | 0 | 11200 | 3.8167 | 2934.4978 | 0
|  |  | 378.8435 | min | 6700 | 5.15 | 1300.9709 | 0 | 6266.6667 | 4.9667 | 1261.745 | 0 | 5833.3333 | 4.7833 | 1219.5122 | 0 | 5400 | 4.55 | 1186.8132 | 0 | 5233.3333 | 3.9167 | 1336.1702 | 0 | 5066.6667 | 3.2667 | 1551.0204 | 0
| 14 |  | 5.1443 | max | 18033.3333 | 5.3167 | 3391.8495 | 5.15 | 17733.3333 | 4.9667 | 3570.4698 | 5.0333 | 17466.6667 | 4.65 | 3756.2724 | 4.9167 | 17266.6667 | 4.4 | 3924.2424 | 4.75 | 16466.6667 | 3.9 | 4222.2222 | 4.1333 | 15600 | 3.4 | 4588.2353 | 3.4833
|  | 1617.3913 | 25.488 | nom | 14000 | 5.5 | 2545.4545 | 314.0566 | 14000 | 5.2167 | 2683.7061 | 321.336 | 14000 | 4.9333 | 2837.8378 | 328.9609 | 14000 | 4.65 | 3010.7527 | 340.5034 | 14000 | 4.2 | 3333.3333 | 391.3043 | 14000 | 3.7333 | 3750 | 464.3229
|  |  | 23.8651 | mid | 11200 | 5.95 | 1882.3529 | 0 | 11200 | 5.6167 | 1994.0653 | 0 | 11200 | 5.3833 | 2080.4954 | 0 | 11200 | 5.1333 | 2181.8182 | 0 | 11200 | 4.5333 | 2470.5882 | 0 | 11200 | 3.9333 | 2847.4576 | 0
|  |  | 314.4042 | min | 6800 | 5.15 | 1320.3883 | 0 | 6333.3333 | 5.0333 | 1258.2781 | 0 | 5866.6667 | 4.9167 | 1193.2203 | 0 | 5400 | 4.75 | 1136.8421 | 0 | 5266.6667 | 4.1333 | 1274.1935 | 0 | 5133.3333 | 3.4833 | 1473.6842 | 0
| 15 |  | 5.15 | max | 18500 | 5.35 | 3457.9439 | 5.15 | 18200 | 5 | 3640 | 5.1 | 17900 | 4.75 | 3768.4211 | 5.05 | 17700 | 4.5 | 3933.3333 | 4.95 | 16900 | 4 | 4225 | 4.35 | 16000 | 3.5 | 4571.4286 | 3.7
|  | 1293.913 | 24.4647 | nom | 14000 | 5.5 | 2545.4545 | 251.2453 | 14000 | 5.25 | 2666.6667 | 253.7084 | 14000 | 5 | 2800 | 256.2204 | 14000 | 4.75 | 2947.3684 | 261.3966 | 14000 | 4.3 | 3255.814 | 297.4513 | 14000 | 3.85 | 3636.3636 | 349.7062
|  |  | 18.7524 | mid | 11200 | 6 | 1866.6667 | 0 | 11200 | 5.65 | 1982.3009 | 0 | 11200 | 5.45 | 2055.0459 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.65 | 2408.6022 | 0 | 11200 | 4.05 | 2765.4321 | 0
|  |  | 251.2453 | min | 6900 | 5.15 | 1339.8058 | 0 | 6400 | 5.1 | 1254.902 | 0 | 5900 | 5.05 | 1168.3168 | 0 | 5400 | 4.95 | 1090.9091 | 0 | 5300 | 4.35 | 1218.3908 | 0 | 5200 | 3.7 | 1405.4054 | 0
| 16 |  | 6.92 | max | 19020 | 5.73 | 3319.3717 | 6.92 | 18720 | 5.3 | 3532.0755 | 5.68 | 18420 | 4.95 | 3721.2121 | 5.37 | 18200 | 4.59 | 3965.1416 | 5.02 | 17380 | 4.08 | 4259.8039 | 4.36 | 16460 | 3.56 | 4623.5955 | 3.65
|  | 970.4348 | 23.3799 | nom | 14000 | 5.93 | 2360.8769 | 140.2362 | 14000 | 5.57 | 2513.465 | 170.8512 | 14000 | 5.21 | 2687.1401 | 180.7141 | 14000 | 4.85 | 2886.5979 | 193.3137 | 14000 | 4.39 | 3189.0661 | 222.5768 | 14000 | 3.92 | 3571.4286 | 265.8725
|  |  | 13.9031 | mid | 11200 | 6.42 | 1744.5483 | 0 | 11200 | 5.99 | 1869.783 | 0 | 11200 | 5.68 | 1971.831 | 0 | 11200 | 5.36 | 2089.5522 | 0 | 11200 | 4.74 | 2362.8692 | 0 | 11200 | 4.12 | 2718.4466 | 0
|  |  | 140.2362 | min | 6980 | 6.92 | 1008.6705 | 0 | 6460 | 5.68 | 1137.3239 | 0 | 6000 | 5.37 | 1117.3184 | 0 | 5520 | 5.02 | 1099.6016 | 0 | 5360 | 4.36 | 1229.3578 | 0 | 5180 | 3.65 | 1419.1781 | 0
| 17 |  | 8.69 | max | 19540 | 6.11 | 3198.036 | 8.69 | 19240 | 5.6 | 3435.7143 | 6.26 | 18940 | 5.15 | 3677.6699 | 5.69 | 18700 | 4.68 | 3995.7265 | 5.09 | 17860 | 4.16 | 4293.2692 | 4.37 | 16920 | 3.62 | 4674.0331 | 3.6
|  | 646.9565 | 22.2063 | nom | 14000 | 6.36 | 2201.2579 | 74.4484 | 14000 | 5.89 | 2376.91 | 103.3477 | 14000 | 5.42 | 2583.0258 | 113.7006 | 14000 | 4.95 | 2828.2828 | 127.1034 | 14000 | 4.48 | 3125 | 148.045 | 14000 | 3.99 | 3508.7719 | 179.7101
|  |  | 9.1637 | mid | 11200 | 6.84 | 1637.4269 | 0 | 11200 | 6.33 | 1769.3523 | 0 | 11200 | 5.91 | 1895.0931 | 0 | 11200 | 5.47 | 2047.532 | 0 | 11200 | 4.83 | 2318.8406 | 0 | 11200 | 4.19 | 2673.031 | 0
|  |  | 74.4484 | min | 7060 | 8.69 | 812.4281 | 0 | 6520 | 6.26 | 1041.5335 | 0 | 6100 | 5.69 | 1072.0562 | 0 | 5640 | 5.09 | 1108.055 | 0 | 5420 | 4.37 | 1240.2746 | 0 | 5160 | 3.6 | 1433.3333 | 0
| 18 |  | 10.46 | max | 20060 | 6.49 | 3090.9091 | 10.46 | 19760 | 5.9 | 3349.1525 | 6.84 | 19460 | 5.35 | 3637.3832 | 6.01 | 19200 | 4.77 | 4025.1572 | 5.16 | 18340 | 4.24 | 4325.4717 | 4.38 | 17380 | 3.68 | 4722.8261 | 3.55
|  | 323.4783 | 20.8812 | nom | 14000 | 6.79 | 2061.8557 | 30.9253 | 14000 | 6.21 | 2254.4283 | 47.2921 | 14000 | 5.63 | 2486.6785 | 53.8233 | 14000 | 5.05 | 2772.2772 | 62.6896 | 14000 | 4.57 | 3063.4573 | 73.8535 | 14000 | 4.06 | 3448.2759 | 91.1206
|  |  | 4.5305 | mid | 11200 | 7.26 | 1542.6997 | 0 | 11200 | 6.67 | 1679.1604 | 0 | 11200 | 6.14 | 1824.1042 | 0 | 11200 | 5.58 | 2007.1685 | 0 | 11200 | 4.92 | 2276.4228 | 0 | 11200 | 4.26 | 2629.108 | 0
|  |  | 30.9253 | min | 7140 | 10.46 | 682.6004 | 0 | 6580 | 6.84 | 961.9883 | 0 | 6200 | 6.01 | 1031.614 | 0 | 5760 | 5.16 | 1116.2791 | 0 | 5480 | 4.38 | 1251.1416 | 0 | 5140 | 3.55 | 1447.8873 | 0
| 19 |  | 12.23 | max | 20580 | 6.87 | 2995.6332 | 12.23 | 20280 | 6.2 | 3270.9677 | 7.42 | 19980 | 5.55 | 3600 | 6.33 | 19700 | 4.86 | 4053.4979 | 5.23 | 18820 | 4.32 | 4356.4815 | 4.39 | 17840 | 3.74 | 4770.0535 | 3.5
|  | 0 | 19 | nom | 14000 | 7.22 | 1939.0582 | 0 | 14000 | 6.53 | 2143.951 | 0 | 14000 | 5.84 | 2397.2603 | 0 | 14000 | 5.15 | 2718.4466 | 0 | 14000 | 4.66 | 3004.2918 | 0 | 14000 | 4.13 | 3389.8305 | 0
|  |  | 0 | mid | 11200 | 7.68 | 1458.3333 | 0 | 11200 | 7.01 | 1597.7175 | 0 | 11200 | 6.37 | 1758.2418 | 0 | 11200 | 5.69 | 1968.3656 | 0 | 11200 | 5.01 | 2235.5289 | 0 | 11200 | 4.33 | 2586.6051 | 0
|  |  | 0 | min | 7220 | 12.23 | 590.3516 | 0 | 6640 | 7.42 | 894.8787 | 0 | 6300 | 6.33 | 995.2607 | 0 | 5880 | 5.23 | 1124.283 | 0 | 5540 | 4.39 | 1261.959 | 0 | 5120 | 3.5 | 1462.8571 | 0
| 20 |  | #NUM! | max | 21100 | 7.25 | 2910.3448 | 14 | 20800 | 6.5 | 3200 | 8 | 20500 | 5.75 | 3565.2174 | 6.65 | 20200 | 4.95 | 4080.8081 | 5.3 | 19300 | 4.4 | 4386.3636 | 4.4 | 18300 | 3.8 | 4815.7895 | 3.45
|  | -323.4783 | #NUM! | nom | 14000 | 7.65 | 1830.0654 | -23.1056 | 14000 | 6.85 | 2043.7956 | -40.4348 | 14000 | 6.05 | 2314.0496 | -48.6433 | 14000 | 5.25 | 2666.6667 | -61.0336 | 14000 | 4.75 | 2947.3684 | -73.5178 | 14000 | 4.2 | 3333.3333 | -93.7618
|  |  |  | mid | 11200 | 8.1 | 1382.716 | 0 | 11200 | 7.35 | 1523.8095 | 0 | 11200 | 6.6 | 1696.9697 | 0 | 11200 | 5.8 | 1931.0345 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.4 | 2545.4545 | 0
|  |  | #NUM! | min | 7300 | 14 | 521.4286 | 0 | 6700 | 8 | 837.5 | 0 | 6400 | 6.65 | 962.406 | 0 | 6000 | 5.3 | 1132.0755 | 0 | 5600 | 4.4 | 1272.7273 | 0 | 5100 | 3.45 | 1478.2609 | 0
Indoor Temp. |  | 20
LWT |  |  | 25 CAP: 25; 35 CAP: 35; 40 CAP: 40; 45 CAP: 45; 50 CAP: 50; 55 CAP: 55
Outdoor air temperature[℃] |  | Heating Demand | COP | CL | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP
|  |  | LWT |  |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI
| -15 |  | 1.7215 | max | - | - | - | - | 14000 | 1.85 | 7567.5676 | 2.2517 | 13500 | 1.7 | 7941.1765 | 2.0485 | 13100 | 1.55 | 8451.6129 | 1.8464 | 12600 | 1.45 | 8689.6552 | 1.6897 | 12200 | 1.3 | 9384.6154 | 1.5196
|  | 11321.7391 | 48.9861 | nom | - | - | - | - | 11000 | 2.3 | 4782.6087 | 5027.9977 | 11000 | 2.1 | 5238.0952 | 5526.785 | 11000 | 1.9 | 5789.4737 | 6131.8681 | 11000 | 1.75 | 6285.7143 | 6700.5468 | 11000 | 1.6 | 6875 | 7450.6438
|  |  | 100 | mid | - | - | - | - | 8800 | 2.5 | 3520 | 3 | 8800 | 2.3 | 3826.087 | 3 | 8800 | 2.1 | 4190.4762 | 3 | 8800 | 1.9 | 4631.5789 | 3 | 8800 | 1.7 | 5176.4706 | 3
|  |  | 6576.859 | min | - | - | - | - | 7800 | 2.35 | 3319.1489 | 0.10725 | 7200 | 2 | 3600 | 0.1287 | 6500 | 1.6 | 4062.5 | 0.15321 | 5700 | 1.3 | 4384.6154 | 0.20109 | 4800 | 1 | 4800 | 0.26812
| -14 |  | 1.988 | max | 14280 | 2.08 | 6865.3846 | 2.6842 | 14080 | 1.93 | 7295.3368 | 2.5293 | 13640 | 1.78 | 7662.9213 | 2.3341 | 13280 | 1.62 | 8197.5309 | 2.1288 | 12880 | 1.53 | 8418.3007 | 1.9185 | 12560 | 1.39 | 9035.9712 | 1.7082
|  | 10998.2609 | 48.3469 | nom | 14000 | 2.64 | 5303.0303 | 4097.4029 | 14000 | 2.34 | 5982.906 | 4348.2971 | 14000 | 2.12 | 6603.7736 | 4711.947 | 14000 | 1.9 | 7368.4211 | 5166.5 | 14000 | 1.77 | 7909.6045 | 5732.7818 | 14000 | 1.63 | 8588.9571 | 6438.6392
|  |  | 100 | mid | 11200 | 2.69 | 4163.5688 | 1 | 11200 | 2.54 | 4409.4488 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.15 | 5209.3023 | 1 | 11200 | 1.94 | 5773.1959 | 1 | 11200 | 1.73 | 6473.9884 | 1
|  |  | 5532.3015 | min | 7720 | 2.59 | 2980.695 | 0.94203 | 7420 | 2.34 | 3170.9402 | 0.94663 | 6880 | 2.01 | 3422.8856 | 0.9533 | 6260 | 1.63 | 3840.4908 | 0.95916 | 5480 | 1.33 | 4120.3008 | 0.96473 | 4640 | 1.02 | 4549.0196 | 0.96925
| -13 |  | 2.0263 | max | 14360 | 2.16 | 6648.1481 | 2.7096 | 14160 | 2.01 | 7044.7761 | 2.5484 | 13780 | 1.86 | 7408.6022 | 2.357 | 13460 | 1.69 | 7964.497 | 2.1452 | 13160 | 1.61 | 8173.913 | 1.9252 | 12920 | 1.48 | 8729.7297 | 1.7037
|  | 10674.7826 | 47.7034 | nom | 14000 | 2.68 | 5223.8806 | 3939.6302 | 14000 | 2.38 | 5882.3529 | 4188.7576 | 14000 | 2.14 | 6542.0561 | 4528.9961 | 14000 | 1.9 | 7368.4211 | 4976.0142 | 14000 | 1.79 | 7821.2291 | 5544.8251 | 14000 | 1.66 | 8433.7349 | 6265.5487
|  |  | 100 | mid | 11200 | 2.73 | 4102.5641 | 1 | 11200 | 2.58 | 4341.0853 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.2 | 5090.9091 | 1 | 11200 | 1.98 | 5656.5657 | 1 | 11200 | 1.76 | 6363.6364 | 1
|  |  | 5268.2123 | min | 7340 | 2.58 | 2844.9612 | 0.86393 | 7040 | 2.33 | 3021.4592 | 0.87375 | 6560 | 2.02 | 3247.5248 | 0.88681 | 6020 | 1.66 | 3626.506 | 0.89861 | 5260 | 1.36 | 3867.6471 | 0.91158 | 4480 | 1.04 | 4307.6923 | 0.92184
| -12 |  | 2.0681 | max | 14440 | 2.24 | 6446.4286 | 2.73 | 14240 | 2.09 | 6813.3971 | 2.5639 | 13920 | 1.94 | 7175.2577 | 2.3781 | 13640 | 1.76 | 7750 | 2.1623 | 13440 | 1.69 | 7952.6627 | 1.9332 | 13280 | 1.57 | 8458.5987 | 1.6999
|  | 10351.3043 | 47.0553 | nom | 14000 | 2.72 | 5147.0588 | 3791.7321 | 14000 | 2.42 | 5785.124 | 4037.2981 | 14000 | 2.16 | 6481.4815 | 4352.699 | 14000 | 1.9 | 7368.4211 | 4787.1468 | 14000 | 1.81 | 7734.8066 | 5354.4878 | 14000 | 1.69 | 8284.0237 | 6089.1836
|  |  | 100 | mid | 11200 | 2.77 | 4043.3213 | 1 | 11200 | 2.62 | 4274.8092 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.25 | 4977.7778 | 1 | 11200 | 2.02 | 5544.5545 | 1 | 11200 | 1.79 | 6256.9832 | 1
|  |  | 5005.1435 | min | 6960 | 2.57 | 2708.1712 | 0.79984 | 6660 | 2.32 | 2870.6897 | 0.81306 | 6240 | 2.03 | 3073.8916 | 0.82889 | 5780 | 1.69 | 3420.1183 | 0.84341 | 5040 | 1.39 | 3625.8993 | 0.86222 | 4320 | 1.06 | 4075.4717 | 0.87664
| -11 |  | 2.1133 | max | 14520 | 2.32 | 6258.6207 | 2.7466 | 14320 | 2.17 | 6599.0783 | 2.5766 | 14060 | 2.02 | 6960.396 | 2.3979 | 13820 | 1.83 | 7551.9126 | 2.1799 | 13720 | 1.77 | 7751.4124 | 1.9424 | 13640 | 1.66 | 8216.8675 | 1.6968
|  | 10027.8261 | 46.4026 | nom | 14000 | 2.76 | 5072.4638 | 3651.0352 | 14000 | 2.46 | 5691.0569 | 3891.8625 | 14000 | 2.18 | 6422.0183 | 4181.957 | 14000 | 1.9 | 7368.4211 | 4600.1666 | 14000 | 1.83 | 7650.2732 | 5162.5555 | 14000 | 1.72 | 8139.5349 | 5909.8856
|  |  | 100 | mid | 11200 | 2.81 | 3985.7651 | 1 | 11200 | 2.66 | 4210.5263 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1 | 11200 | 2.06 | 5436.8932 | 1 | 11200 | 1.82 | 6153.8462 | 1
|  |  | 4745.1696 | min | 6580 | 2.56 | 2570.3125 | 0.74628 | 6280 | 2.31 | 2718.6147 | 0.76175 | 5920 | 2.04 | 2901.9608 | 0.778 | 5540 | 1.72 | 3220.9302 | 0.7929 | 4820 | 1.42 | 3394.3662 | 0.81627 | 4160 | 1.08 | 3851.8519 | 0.8335
| -10 |  | 2.1614 | max | 14600 | 2.4 | 6083.3333 | 2.7603 | 14400 | 2.25 | 6400 | 2.5871 | 14200 | 2.1 | 6761.9048 | 2.4165 | 14000 | 1.9 | 7368.4211 | 2.1979 | 14000 | 1.85 | 7567.5676 | 1.9527 | 14000 | 1.75 | 8000 | 1.6942
|  | 9704.3478 | 45.7449 | nom | 14000 | 2.8 | 5000 | 3515.7358 | 14000 | 2.5 | 5600 | 3751.0226 | 14000 | 2.2 | 6363.6364 | 4015.9363 | 14000 | 1.9 | 7368.4211 | 4415.2822 | 14000 | 1.85 | 7567.5676 | 4969.7051 | 14000 | 1.75 | 8000 | 5727.9726
|  |  | 100 | mid | 11200 | 2.85 | 3929.8246 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.1 | 5333.3333 | 1 | 11200 | 1.85 | 6054.0541 | 1
|  |  | 4489.9102 | min | 6200 | 2.55 | 2431.3725 | 0.70087 | 5900 | 2.3 | 2565.2174 | 0.7178 | 5600 | 2.05 | 2731.7073 | 0.73292 | 5300 | 1.75 | 3028.5714 | 0.7465 | 4600 | 1.45 | 3172.4138 | 0.77339 | 4000 | 1.1 | 3636.3636 | 0.79227
| -9 |  | 2.2189 | max | 15100 | 2.5 | 6040 | 2.9607 | 14900 | 2.3333 | 6385.7143 | 2.6416 | 14700 | 2.1667 | 6784.6154 | 2.4486 | 14500 | 1.9667 | 7372.8814 | 2.2229 | 14233.3333 | 1.9167 | 7426.087 | 1.983 | 14000 | 1.8167 | 7706.422 | 1.7353
|  | 9380.8696 | 45.0822 | nom | 14000 | 2.8833 | 4855.4913 | 3168.4255 | 14000 | 2.6 | 5384.6154 | 3551.2174 | 14000 | 2.3167 | 6043.1655 | 3831.1236 | 14000 | 2.0333 | 6885.2459 | 4220.1533 | 14000 | 1.95 | 7179.4872 | 4730.6346 | 14000 | 1.8167 | 7706.422 | 5406.0615
|  |  | 100 | mid | 11200 | 2.9833 | 3754.1899 | 1 | 11200 | 2.8 | 4000 | 1 | 11200 | 2.6167 | 4280.2548 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.1667 | 5169.2308 | 1 | 11200 | 1.9333 | 5793.1034 | 1
|  |  | 4227.6571 | min | 5833.3333 | 2.9167 | 2000 | 0.66103 | 5266.6667 | 2.2833 | 2306.5693 | 0.6934 | 5066.6667 | 2.05 | 2471.5447 | 0.7034 | 4866.6667 | 1.7833 | 2728.972 | 0.71277 | 4266.6667 | 1.4667 | 2909.0909 | 0.73763 | 3700 | 1.1167 | 3313.4328 | 0.75745
| -8 |  | 2.2764 | max | 15600 | 2.6 | 6000 | 3.179 | 15400 | 2.4167 | 6372.4138 | 2.6934 | 15200 | 2.2333 | 6805.9701 | 2.4798 | 15000 | 2.0333 | 7377.0492 | 2.2495 | 14466.6667 | 1.9833 | 7294.1176 | 2.0122 | 14000 | 1.8833 | 7433.6283 | 1.774
|  | 9057.3913 | 44.4142 | nom | 14000 | 2.9667 | 4719.1011 | 2849.1754 | 14000 | 2.7 | 5185.1852 | 3362.8689 | 14000 | 2.4333 | 5753.4247 | 3652.4898 | 14000 | 2.1667 | 6461.5385 | 4026.4731 | 14000 | 2.05 | 6829.2683 | 4501.2548 | 14000 | 1.8833 | 7433.6283 | 5105.5722
|  |  | 100 | mid | 11200 | 3.1167 | 3593.5829 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.6833 | 4173.913 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.2333 | 5014.9254 | 1 | 11200 | 2.0167 | 5553.719 | 1
|  |  | 3978.7471 | min | 5466.6667 | 3.2833 | 1664.9746 | 0.62629 | 4633.3333 | 2.2667 | 2044.1176 | 0.67371 | 4533.3333 | 2.05 | 2211.3821 | 0.67861 | 4433.3333 | 1.8167 | 2440.367 | 0.68336 | 3933.3333 | 1.4833 | 2651.6854 | 0.70515 | 3400 | 1.1333 | 3000 | 0.72531
| -7 |  | 2.336 | max | 16100 | 2.7 | 5962.963 | 3.4117 | 15900 | 2.5 | 6360 | 2.7431 | 15700 | 2.3 | 6826.087 | 2.5102 | 15500 | 2.1 | 7380.9524 | 2.2774 | 14700 | 2.05 | 7170.7317 | 2.0404 | 14000 | 1.95 | 7179.4872 | 1.8108
|  | 8733.913 | 43.7407 | nom | 14000 | 3.05 | 4590.1639 | 2559.9806 | 14000 | 2.8 | 5000 | 3183.9387 | 14000 | 2.55 | 5490.1961 | 3479.3118 | 14000 | 2.3 | 6086.9565 | 3835.0922 | 14000 | 2.15 | 6511.6279 | 4280.4656 | 14000 | 1.95 | 7179.4872 | 4823.3209
|  |  | 100 | mid | 11200 | 3.25 | 3446.1538 | 1 | 11200 | 3 | 3733.3333 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1 | 11200 | 2.1 | 5333.3333 | 1
|  |  | 3738.8038 | min | 5100 | 3.65 | 1397.2603 | 0.59572 | 4000 | 2.25 | 1777.7778 | 0.65749 | 4000 | 2.05 | 1951.2195 | 0.65749 | 4000 | 1.85 | 2162.1622 | 0.65749 | 3600 | 1.5 | 2400 | 0.67551 | 3100 | 1.15 | 2695.6522 | 0.69554
| -6 |  | 2.398 | max | 16144.4444 | 2.7611 | 5847.0825 | 3.4867 | 15944.4444 | 2.5556 | 6239.1304 | 2.7926 | 15733.3333 | 2.35 | 6695.0355 | 2.5486 | 15533.3333 | 2.1444 | 7243.5233 | 2.3026 | 14744.4444 | 2.0944 | 7039.7878 | 2.06 | 14033.3333 | 1.9944 | 7036.2117 | 1.8205
|  | 8410.4348 | 43.0614 | nom | 14000 | 3.0889 | 4532.3741 | 2412.12 | 14000 | 2.8389 | 4931.5068 | 3011.644 | 14000 | 2.5889 | 5407.7253 | 3300.0703 | 14000 | 2.3389 | 5985.7482 | 3652.5428 | 14000 | 2.1944 | 6379.7468 | 4082.7038 | 14000 | 2 | 7000 | 4619.9416
|  |  | 100 | mid | 11200 | 3.2944 | 3399.6627 | 1 | 11200 | 3.0444 | 3678.8321 | 1 | 11200 | 2.7944 | 4007.9523 | 1 | 11200 | 2.5444 | 4401.7467 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.15 | 5209.3023 | 1
|  |  | 3507.3012 | min | 5155.5556 | 3.7111 | 1389.2216 | 0.53849 | 4122.2222 | 2.4056 | 1713.6259 | 0.60587 | 4077.7778 | 2.1667 | 1882.0513 | 0.60833 | 4022.2222 | 1.9222 | 2092.4855 | 0.61136 | 3611.1111 | 1.5611 | 2313.1673 | 0.63241 | 3111.1111 | 1.1944 | 2604.6512 | 0.65514
| -5 |  | 2.4684 | max | 16188.8889 | 2.8222 | 5736.2205 | 3.5641 | 15988.8889 | 2.6111 | 6123.4043 | 2.8527 | 15766.6667 | 2.4 | 6569.4444 | 2.5934 | 15566.6667 | 2.1889 | 7111.6751 | 2.3303 | 14788.8889 | 2.1389 | 6914.2857 | 2.0805 | 14066.6667 | 2.0389 | 6899.1826 | 1.8296
|  | 8086.9565 | 42.376 | nom | 14000 | 3.1278 | 4476.0213 | 2268.9803 | 14000 | 2.8778 | 4864.8649 | 2834.8673 | 14000 | 2.6278 | 5327.6956 | 3118.3067 | 14000 | 2.3778 | 5887.8505 | 3470.3883 | 14000 | 2.2389 | 6253.1017 | 3887.064 | 14000 | 2.05 | 6829.2683 | 4420.0596
|  |  | 100 | mid | 11200 | 3.3389 | 3354.4093 | 1 | 11200 | 3.0889 | 3625.8993 | 1 | 11200 | 2.8389 | 3945.2055 | 1 | 11200 | 2.5889 | 4326.1803 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.2 | 5090.9091 | 1
|  |  | 3276.2597 | min | 5211.1111 | 3.7722 | 1381.4433 | 0.4802 | 4244.4444 | 2.5611 | 1657.2668 | 0.55244 | 4155.5556 | 2.2833 | 1819.9513 | 0.55809 | 4044.4444 | 1.9944 | 2027.8552 | 0.56495 | 3622.2222 | 1.6222 | 2232.8767 | 0.58919 | 3122.2222 | 1.2389 | 2520.1794 | 0.61462
| -4 |  | 2.5491 | max | 16233.3333 | 2.8833 | 5630.0578 | 3.644 | 16033.3333 | 2.6667 | 6012.5 | 2.9238 | 15800 | 2.45 | 6448.9796 | 2.6449 | 15600 | 2.2333 | 6985.0746 | 2.3603 | 14833.3333 | 2.1833 | 6793.8931 | 2.1018 | 14100 | 2.0833 | 6768 | 1.8382
|  | 7763.4783 | 41.6843 | nom | 14000 | 3.1667 | 4421.0526 | 2130.501 | 14000 | 2.9167 | 4800 | 2655.2796 | 14000 | 2.6667 | 5250 | 2935.2475 | 14000 | 2.4167 | 5793.1034 | 3289.1375 | 14000 | 2.2833 | 6131.3869 | 3693.7175 | 14000 | 2.1 | 6666.6667 | 4223.4468
|  |  | 100 | mid | 11200 | 3.3833 | 3310.3448 | 1 | 11200 | 3.1333 | 3574.4681 | 1 | 11200 | 2.8833 | 3884.3931 | 1 | 11200 | 2.6333 | 4253.1646 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.25 | 4977.7778 | 1
|  |  | 3045.6346 | min | 5266.6667 | 3.8333 | 1373.913 | 0.42081 | 4366.6667 | 2.7167 | 1607.362 | 0.49709 | 4233.3333 | 2.4 | 1763.8889 | 0.50672 | 4066.6667 | 2.0667 | 1967.7419 | 0.51824 | 3633.3333 | 1.6833 | 2158.4158 | 0.54583 | 3133.3333 | 1.2833 | 2441.5584 | 0.57398
| -3 |  | 2.6422 | max | 16277.7778 | 2.9444 | 5528.3019 | 3.7263 | 16077.7778 | 2.7222 | 5906.1224 | 3.0066 | 15833.3333 | 2.5 | 6333.3333 | 2.7034 | 15633.3333 | 2.2778 | 6863.4146 | 2.3928 | 14877.7778 | 2.2278 | 6678.3042 | 2.124 | 14133.3333 | 2.1278 | 6642.2977 | 1.8462
|  | 7440 | 40.9859 | nom | 14000 | 3.2056 | 4367.4177 | 1996.6169 | 14000 | 2.9556 | 4736.8421 | 2474.5677 | 14000 | 2.7056 | 5174.538 | 2752.0994 | 14000 | 2.4556 | 5701.3575 | 3109.2756 | 14000 | 2.3278 | 6014.3198 | 3502.8249 | 14000 | 2.15 | 6511.6279 | 4029.8842
|  |  | 100 | mid | 11200 | 3.4278 | 3267.423 | 1 | 11200 | 3.1778 | 3524.4755 | 1 | 11200 | 2.9278 | 3825.4269 | 1 | 11200 | 2.6778 | 4182.5726 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1
|  |  | 2815.8824 | min | 5322.2222 | 3.8944 | 1366.6191 | 0.3603 | 4488.8889 | 2.8722 | 1562.8627 | 0.43974 | 4311.1111 | 2.5167 | 1713.0243 | 0.45419 | 4088.8889 | 2.1389 | 1911.6883 | 0.47125 | 3644.4444 | 1.7444 | 2089.172 | 0.50235 | 3144.4444 | 1.3278 | 2368.2008 | 0.53324
| -2 |  | 2.7499 | max | 16322.2222 | 3.0056 | 5430.6839 | 3.8112 | 16122.2222 | 2.7778 | 5804 | 3.1017 | 15866.6667 | 2.55 | 6222.2222 | 2.769 | 15666.6667 | 2.3222 | 6746.4115 | 2.4278 | 14922.2222 | 2.2722 | 6567.2372 | 2.1471 | 14166.6667 | 2.1722 | 6521.7391 | 1.8537
|  | 7116.5217 | 40.2805 | nom | 14000 | 3.2444 | 4315.0685 | 1867.2589 | 14000 | 2.9944 | 4675.3247 | 2294.383 | 14000 | 2.7444 | 5101.2146 | 2570.0251 | 14000 | 2.4944 | 5612.4722 | 2931.261 | 14000 | 2.3722 | 5901.6393 | 3314.5352 | 14000 | 2.2 | 6363.6364 | 3839.1615
|  |  | 100 | mid | 11200 | 3.4722 | 3225.6 | 1 | 11200 | 3.2222 | 3475.8621 | 1 | 11200 | 2.9722 | 3768.2243 | 1 | 11200 | 2.7222 | 4114.2857 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1
|  |  | 2587.9137 | min | 5377.7778 | 3.9556 | 1359.5506 | 0.29864 | 4611.1111 | 3.0278 | 1522.9358 | 0.38025 | 4388.8889 | 2.6333 | 1666.6667 | 0.40047 | 4111.1111 | 2.2111 | 1859.2965 | 0.42396 | 3655.5556 | 1.8056 | 2024.6154 | 0.45874 | 3155.5556 | 1.3722 | 2299.5951 | 0.49239
| -1 |  | 2.8739 | max | 16366.6667 | 3.0667 | 5336.9565 | 3.8988 | 16166.6667 | 2.8333 | 5705.8824 | 3.2099 | 15900 | 2.6 | 6115.3846 | 2.8421 | 15700 | 2.3667 | 6633.8028 | 2.4652 | 14966.6667 | 2.3167 | 6460.4317 | 2.171 | 14200 | 2.2167 | 6406.015 | 1.8606
|  | 6793.0435 | 39.5676 | nom | 14000 | 3.2833 | 4263.9594 | 1742.3543 | 14000 | 3.0333 | 4615.3846 | 2116.2947 | 14000 | 2.7833 | 5029.9401 | 2390.121 | 14000 | 2.5333 | 5526.3158 | 2755.5219 | 14000 | 2.4167 | 5793.1034 | 3128.9868 | 14000 | 2.25 | 6222.2222 | 3651.0761
|  |  | 100 | mid | 11200 | 3.5167 | 3184.8341 | 1 | 11200 | 3.2667 | 3428.5714 | 1 | 11200 | 3.0167 | 3712.7072 | 1 | 11200 | 2.7667 | 4048.1928 | 1 | 11200 | 2.6 | 4307.6923 | 1 | 11200 | 2.4 | 4666.6667 | 1
|  |  | 2363.6698 | min | 5433.3333 | 4.0167 | 1352.6971 | 0.23579 | 4733.3333 | 3.1833 | 1486.911 | 0.31851 | 4466.6667 | 2.75 | 1624.2424 | 0.3455 | 4133.3333 | 2.2833 | 1810.219 | 0.37637 | 3666.6667 | 1.8667 | 1964.2857 | 0.41501 | 3166.6667 | 1.4167 | 2235.2941 | 0.45142
| 0 |  | 3.0172 | max | 16411.1111 | 3.1278 | 5246.8917 | 3.9891 | 16211.1111 | 2.8889 | 5611.5385 | 3.3318 | 15933.3333 | 2.65 | 6012.5786 | 2.9229 | 15733.3333 | 2.4111 | 6525.3456 | 2.5052 | 15011.1111 | 2.3611 | 6357.6471 | 2.1958 | 14233.3333 | 2.2611 | 6294.8403 | 1.8669
|  | 6469.5652 | 38.8468 | nom | 14000 | 3.3222 | 4214.0468 | 1621.8274 | 14000 | 3.0722 | 4556.962 | 1941.7498 | 14000 | 2.8222 | 4960.6299 | 2213.3989 | 14000 | 2.5722 | 5442.7646 | 2582.4549 | 14000 | 2.4611 | 5688.4876 | 2946.3063 | 14000 | 2.3 | 6086.9565 | 3465.4323
|  |  | 100 | mid | 11200 | 3.5611 | 3145.0858 | 1 | 11200 | 3.3111 | 3382.5503 | 1 | 11200 | 3.0611 | 3658.8022 | 1 | 11200 | 2.8111 | 3984.1897 | 1 | 11200 | 2.65 | 4226.4151 | 1 | 11200 | 2.45 | 4571.4286 | 1
|  |  | 2144.2117 | min | 5488.8889 | 4.0778 | 1346.049 | 0.17171 | 4855.5556 | 3.3389 | 1454.2429 | 0.2544 | 4544.4444 | 2.8667 | 1585.2713 | 0.28925 | 4155.5556 | 2.3556 | 1764.1509 | 0.32849 | 3677.7778 | 1.9278 | 1907.781 | 0.37114 | 3177.7778 | 1.4611 | 2174.9049 | 0.41033
| 1 |  | 3.1836 | max | 16455.5556 | 3.1889 | 5160.2787 | 4.0822 | 16255.5556 | 2.9444 | 5520.7547 | 3.4684 | 15966.6667 | 2.7 | 5913.5802 | 3.0116 | 15766.6667 | 2.4556 | 6420.8145 | 2.5477 | 15055.5556 | 2.4056 | 6258.6605 | 2.2215 | 14266.6667 | 2.3056 | 6187.9518 | 1.8726
|  | 6146.087 | 38.1176 | nom | 14000 | 3.3611 | 4165.2893 | 1505.5996 | 14000 | 3.1111 | 4500 | 1772.041 | 14000 | 2.8611 | 4893.2039 | 2040.7718 | 14000 | 2.6111 | 5361.7021 | 2412.4225 | 14000 | 2.5056 | 5587.5831 | 2766.6096 | 14000 | 2.35 | 5957.4468 | 3282.0408
|  |  | 100 | mid | 11200 | 3.6056 | 3106.3174 | 1 | 11200 | 3.3556 | 3337.7483 | 1 | 11200 | 3.1056 | 3606.4401 | 1 | 11200 | 2.8556 | 3922.179 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.5 | 4480 | 1
|  |  | 1930.552 | min | 5544.4444 | 4.1389 | 1339.5973 | 0.10638 | 4977.7778 | 3.4944 | 1424.4833 | 0.18776 | 4622.2222 | 2.9833 | 1549.3482 | 0.23167 | 4177.7778 | 2.4278 | 1720.8238 | 0.2803 | 3688.8889 | 1.9889 | 1854.7486 | 0.32714 | 3188.8889 | 1.5056 | 2118.0812 | 0.36914
14kW-Maximum heating CAP | 2 |  | 3.3768 | max | 16500 | 3.25 | 5076.9231 | 4.1781 | 16300 | 3 | 5433.3333 | 3.6204 | 16000 | 2.75 | 5818.1818 | 3.1086 | 15800 | 2.5 | 6320 | 2.5927 | 15100 | 2.45 | 6163.2653 | 2.2481 | 14300 | 2.35 | 6085.1064 | 1.8778
|  | 5822.6087 | 37.3796 | nom | 14000 | 3.4 | 4117.6471 | 1393.5898 | 14000 | 3.15 | 4444.4444 | 1608.2844 | 14000 | 2.9 | 4827.5862 | 1873.0433 | 14000 | 2.65 | 5283.0189 | 2245.7526 | 14000 | 2.55 | 5490.1961 | 2590.0015 | 14000 | 2.4 | 5833.3333 | 3100.7178
|  |  | 100 | mid | 11200 | 3.65 | 3068.4932 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 3.15 | 3555.5556 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.55 | 4392.1569 | 1
|  |  | 1724.2794 | min | 5600 | 4.2 | 1333.3333 | 0.039752 | 5100 | 3.65 | 1397.2603 | 0.11846 | 4700 | 3.1 | 1516.129 | 0.17271 | 4200 | 2.5 | 1680 | 0.2318 | 3700 | 2.05 | 1804.878 | 0.28301 | 3200 | 1.55 | 2064.5161 | 0.32783
| 3 |  | 3.6065 | max | 16560 | 3.54 | 4677.9661 | 4.6655 | 16360 | 3.25 | 5033.8462 | 3.798 | 16080 | 2.96 | 5432.4324 | 3.2113 | 15860 | 2.66 | 5962.406 | 2.6308 | 15160 | 2.54 | 5968.5039 | 2.2581 | 14360 | 2.38 | 6033.6134 | 1.8622
|  | 5499.1304 | 36.632 | nom | 14000 | 3.7 | 3783.7838 | 1178.6881 | 14000 | 3.41 | 4105.5718 | 1447.8972 | 14000 | 3.12 | 4487.1795 | 1712.4227 | 14000 | 2.82 | 4964.539 | 2090.3175 | 14000 | 2.67 | 5243.4457 | 2435.305 | 14000 | 2.47 | 5668.0162 | 2953.0266
|  |  | 100 | mid | 11200 | 3.97 | 2821.1587 | 1 | 11200 | 3.68 | 3043.4783 | 1 | 11200 | 3.39 | 3303.8348 | 1 | 11200 | 3.09 | 3624.5955 | 1 | 11200 | 2.88 | 3888.8889 | 1 | 11200 | 2.62 | 4274.8092 | 1
|  |  | 1524.7762 | min | 5380 | 4.68 | 1149.5726 | 0.020469 | 4920 | 3.81 | 1291.3386 | 0.092218 | 4500 | 3.18 | 1415.0943 | 0.14912 | 4000 | 2.51 | 1593.6255 | 0.20821 | 3500 | 2.04 | 1715.6863 | 0.25963 | 3000 | 1.53 | 1960.7843 | 0.30477
| 4 |  | 3.8535 | max | 16620 | 3.83 | 4339.4256 | 5.1577 | 16420 | 3.5 | 4691.4286 | 3.9693 | 16160 | 3.17 | 5097.7918 | 3.307 | 15920 | 2.82 | 5645.3901 | 2.6613 | 15220 | 2.63 | 5787.0722 | 2.2627 | 14420 | 2.41 | 5983.4025 | 1.8437 | 3.75 | 3.91 | 0.16 | 4.2667
|  | 5175.6522 | 35.8742 | nom | 14000 | 4 | 3500 | 1003.4718 | 14000 | 3.67 | 3814.7139 | 1303.9122 | 14000 | 3.34 | 4191.6168 | 1565.0808 | 14000 | 2.99 | 4682.2742 | 1944.7957 | 14000 | 2.79 | 5017.9211 | 2287.4033 | 14000 | 2.54 | 5511.811 | 2807.1751 | 35.5
|  |  | 100 | mid | 11200 | 4.29 | 2610.7226 | 1 | 11200 | 3.96 | 2828.2828 | 1 | 11200 | 3.63 | 3085.3994 | 1 | 11200 | 3.28 | 3414.6341 | 1 | 11200 | 3.01 | 3720.9302 | 1 | 11200 | 2.69 | 4163.5688 | 1 | 5226
|  |  | 1343.0969 | min | 5160 | 5.16 | 1000 | 0.0025914 | 4740 | 3.97 | 1193.9547 | 0.067438 | 4300 | 3.26 | 1319.0184 | 0.12691 | 3800 | 2.52 | 1507.9365 | 0.1859 | 3300 | 2.03 | 1625.6158 | 0.23742 | 2800 | 1.51 | 1854.3046 | 0.28282 | 1395 | 1338 | 57 | 4.086 | 32112
| 5 |  | 4.1193 | max | 16680 | 4.12 | 4048.5437 | 5.64 | 16480 | 3.75 | 4394.6667 | 4.1348 | 16240 | 3.38 | 4804.7337 | 3.3961 | 15980 | 2.98 | 5362.4161 | 2.6849 | 15280 | 2.72 | 5617.6471 | 2.2623 | 14480 | 2.44 | 5934.4262 | 1.8226 | 3.75 | 4.07 | 0.32 | 8.5333
|  | 4852.1739 | 35.1053 | nom | 14000 | 4.3 | 3255.814 | 860.3145 | 14000 | 3.93 | 3562.341 | 1173.4852 | 14000 | 3.56 | 3932.5843 | 1428.7286 | 14000 | 3.16 | 4430.3797 | 1807.2258 | 14000 | 2.91 | 4810.9966 | 2144.8197 | 14000 | 2.61 | 5363.9847 | 2662.2433 | 35.5
|  |  | 100 | mid | 11200 | 4.61 | 2429.5011 | 0 | 11200 | 4.24 | 2641.5094 | 1 | 11200 | 3.87 | 2894.0568 | 1 | 11200 | 3.47 | 3227.6657 | 1 | 11200 | 3.14 | 3566.879 | 1 | 11200 | 2.76 | 4057.971 | 1 | 5226
|  |  | 1177.9185 | min | 4940 | 5.64 | 875.8865 | 0 | 4560 | 4.13 | 1104.1162 | 0.044002 | 4100 | 3.34 | 1227.5449 | 0.10594 | 3600 | 2.53 | 1422.9249 | 0.16476 | 3100 | 2.02 | 1534.6535 | 0.21632 | 2600 | 1.49 | 1744.9664 | 0.26188 | 1395 | 1283 | 112 | 8.0287 | 30792
| 6 |  | 4.4183 | max | 16740 | 4.41 | 3795.9184 | 6.12 | 16540 | 4 | 4135 | 4.295 | 16320 | 3.59 | 4545.961 | 3.4794 | 16040 | 3.14 | 5108.2803 | 2.7021 | 15340 | 2.81 | 5459.0747 | 2.2572 | 14540 | 2.47 | 5886.6397 | 1.799 | 3.75 | 4.24 | 0.49 | 13.0667
|  | 4528.6957 | 34.3246 | nom | 14000 | 4.6 | 3043.4783 | 739.9829 | 14000 | 4.19 | 3341.2888 | 1054.4075 | 14000 | 3.78 | 3703.7037 | 1301.5645 | 14000 | 3.33 | 4204.2042 | 1676.0103 | 14000 | 3.03 | 4620.462 | 2006.2909 | 14000 | 2.68 | 5223.8806 | 2517.3682 | 35.5
|  |  | 100 | mid | 11200 | 4.93 | 2271.8053 | 0 | 11200 | 4.52 | 2477.8761 | 1 | 11200 | 4.11 | 2725.0608 | 1 | 11200 | 3.66 | 3060.1093 | 1 | 11200 | 3.27 | 3425.0765 | 1 | 11200 | 2.83 | 3957.5972 | 1 | 5226
|  |  | 1024.991 | min | 4720 | 6.12 | 771.2418 | 0 | 4380 | 4.29 | 1020.979 | 0.021803 | 3900 | 3.42 | 1140.3509 | 0.086123 | 3400 | 2.54 | 1338.5827 | 0.1447 | 2900 | 2.01 | 1442.7861 | 0.19623 | 2400 | 1.47 | 1632.6531 | 0.2419 | 1395 | 1231 | 164 | 11.7563 | 29544
| 7 |  | 4.7661 | max | 16800 | 4.7 | 3574.4681 | 6.6 | 16600 | 4.25 | 3905.8824 | 4.4503 | 16400 | 3.8 | 4315.7895 | 3.5573 | 16100 | 3.3 | 4878.7879 | 2.7133 | 15400 | 2.9 | 5310.3448 | 2.2479 | 14600 | 2.5 | 5840 | 1.7731 | 3.75 | 4.42 | 0.67 | 17.8667
|  | 4205.2174 | 33.5308 | nom | 14000 | 4.9 | 2857.1429 | 637.1542 | 14000 | 4.45 | 3146.0674 | 944.9373 | 14000 | 4 | 3500 | 1182.1514 | 14000 | 3.5 | 4000 | 1549.8261 | 14000 | 3.15 | 4444.4444 | 1870.7164 | 14000 | 2.75 | 5090.9091 | 2371.725 | 35.5
|  |  | 100 | mid | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.8 | 2333.3333 | 1 | 11200 | 4.35 | 2574.7126 | 1 | 11200 | 3.85 | 2909.0909 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 2.9 | 3862.069 | 1 | 5226
|  |  | 882.3193 | min | 4500 | 6.6 | 681.8182 | 0 | 4200 | 4.45 | 943.8202 | 0.00074534 | 3700 | 3.5 | 1057.1429 | 0.067362 | 3200 | 2.55 | 1254.902 | 0.12565 | 2700 | 2 | 1350 | 0.17708 | 2200 | 1.45 | 1517.2414 | 0.2228 | 1395 | 1182 | 213 | 15.2688 | 28368
| 8 |  | 4.9431 | max | 16860 | 4.81 | 3505.1975 | 6.31 | 16640 | 4.38 | 3799.0868 | 4.54 | 16440 | 3.93 | 4183.2061 | 3.73 | 16160 | 3.48 | 4643.6782 | 2.9468 | 15440 | 3.06 | 5045.7516 | 2.4457 | 14640 | 2.64 | 5545.4545 | 1.9415 | 3.75 | 4.51 | 0.76 | 20.2667
|  | 3881.7391 | 32.7228 | nom | 14000 | 5.02 | 2788.8446 | 615.1726 | 14000 | 4.59 | 3050.1089 | 855.0086 | 14000 | 4.16 | 3365.3846 | 1040.6807 | 14000 | 3.69 | 3794.0379 | 1317.285 | 14000 | 3.32 | 4216.8675 | 1587.1887 | 14000 | 2.9 | 4827.5862 | 1999.4014 | 35.5
|  |  | 83.0697 | mid | 11200 | 5.37 | 2085.6611 | 0 | 11200 | 4.95 | 2262.6263 | 0 | 11200 | 4.53 | 2472.4062 | 0 | 11200 | 4.06 | 2758.6207 | 1 | 11200 | 3.58 | 3128.4916 | 1 | 11200 | 3.06 | 3660.1307 | 1 | 5226
|  |  | 785.2913 | min | 4920 | 6.31 | 779.7147 | 0 | 4600 | 4.54 | 1013.2159 | 0 | 4120 | 3.73 | 1104.5576 | 0 | 3640 | 2.91 | 1250.8591 | 0.031976 | 3200 | 2.34 | 1367.5214 | 0.085217 | 2760 | 1.77 | 1559.322 | 0.13291 | 1395 | 1159 | 236 | 16.9176 | 27816
| 9 |  | 5.061 | max | 16920 | 4.92 | 3439.0244 | 6.02 | 16680 | 4.51 | 3698.4479 | 4.63 | 16480 | 4.06 | 4059.1133 | 3.96 | 16220 | 3.66 | 4431.694 | 3.27 | 15480 | 3.22 | 4807.4534 | 2.68 | 14680 | 2.78 | 5280.5755 | 2.1242 | 3.75 | 4.59 | 0.84 | 22.4
|  | 3558.2609 | 31.8992 | nom | 14000 | 5.14 | 2723.7354 | 591.0732 | 14000 | 4.73 | 2959.8309 | 768.5229 | 14000 | 4.32 | 3240.7407 | 898.5507 | 14000 | 3.88 | 3608.2474 | 1088.1532 | 14000 | 3.49 | 4011.4613 | 1327.7093 | 14000 | 3.05 | 4590.1639 | 1675.1325 | 35.5
|  |  | 69.6956 | mid | 11200 | 5.49 | 2040.0729 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.71 | 2377.9193 | 0 | 11200 | 4.27 | 2622.9508 | 0 | 11200 | 3.76 | 2978.7234 | 0 | 11200 | 3.22 | 3478.2609 | 1 | 5226
|  |  | 703.0722 | min | 5340 | 6.02 | 887.0432 | 0 | 5000 | 4.63 | 1079.9136 | 0 | 4540 | 3.96 | 1146.4646 | 0 | 4080 | 3.27 | 1247.7064 | 0 | 3700 | 2.68 | 1380.597 | 0 | 3320 | 2.09 | 1588.5167 | 0.030236 | 1395 | 1139 | 256 | 18.3513 | 27336
| 10 |  | 5.1181 | max | 16980 | 5.03 | 3375.7455 | 5.73 | 16720 | 4.64 | 3603.4483 | 4.72 | 16520 | 4.19 | 3942.7208 | 4.19 | 16280 | 3.84 | 4239.5833 | 3.63 | 15520 | 3.38 | 4591.716 | 3.02 | 14720 | 2.92 | 5041.0959 | 2.41 | 3.75 | 4.67 | 0.92 | 24.5333
|  | 3234.7826 | 31.058 | nom | 14000 | 5.26 | 2661.597 | 564.5345 | 14000 | 4.87 | 2874.7433 | 685.3353 | 14000 | 4.48 | 3125 | 772.0245 | 14000 | 4.07 | 3439.8034 | 891.1247 | 14000 | 3.66 | 3825.1366 | 1071.1201 | 14000 | 3.2 | 4375 | 1342.2334 | 35.5
|  |  | 58.3694 | mid | 11200 | 5.61 | 1996.4349 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.89 | 2290.3885 | 0 | 11200 | 4.48 | 2500 | 0 | 11200 | 3.94 | 2842.6396 | 0 | 11200 | 3.38 | 3313.6095 | 0 | 5226
|  |  | 632.0225 | min | 5760 | 5.73 | 1005.2356 | 0 | 5400 | 4.72 | 1144.0678 | 0 | 4960 | 4.19 | 1183.7709 | 0 | 4520 | 3.63 | 1245.1791 | 0 | 4200 | 3.02 | 1390.7285 | 0 | 3880 | 2.41 | 1609.9585 | 0 | 1395 | 1119 | 276 | 19.7849 | 26856
| 11 |  | 5.1126 | max | 17040 | 5.14 | 3315.1751 | 5.44 | 16760 | 4.77 | 3513.6268 | 4.81 | 16560 | 4.32 | 3833.3333 | 4.42 | 16340 | 4.02 | 4064.6766 | 3.99 | 15560 | 3.54 | 4395.4802 | 3.36 | 14760 | 3.06 | 4823.5294 | 2.73 | 3.75 | 4.77 | 1.02 | 27.2
|  | 2911.3043 | 30.1971 | nom | 14000 | 5.38 | 2602.2305 | 535.1662 | 14000 | 5.01 | 2794.4112 | 605.2608 | 14000 | 4.64 | 3017.2414 | 658.6661 | 14000 | 4.26 | 3286.385 | 729.6502 | 14000 | 3.83 | 3655.3525 | 866.4596 | 14000 | 3.35 | 4179.1045 | 1066.4118 | 35.5
|  |  | 48.6636 | mid | 11200 | 5.73 | 1954.6248 | 0 | 11200 | 5.4 | 2074.0741 | 0 | 11200 | 5.07 | 2209.073 | 0 | 11200 | 4.69 | 2388.0597 | 0 | 11200 | 4.12 | 2718.4466 | 0 | 11200 | 3.54 | 3163.8418 | 0 | 5226
|  |  | 569.4392 | min | 6180 | 5.44 | 1136.0294 | 0 | 5800 | 4.81 | 1205.8212 | 0 | 5380 | 4.42 | 1217.1946 | 0 | 4960 | 3.99 | 1243.1078 | 0 | 4700 | 3.36 | 1398.8095 | 0 | 4440 | 2.73 | 1626.3736 | 0 | 1395 | 1095 | 300 | 21.5054 | 26280
| 12 |  | 5.0422 | max | 17100 | 5.25 | 3257.1429 | 5.15 | 16800 | 4.9 | 3428.5714 | 4.9 | 16600 | 4.45 | 3730.3371 | 4.65 | 16400 | 4.2 | 3904.7619 | 4.35 | 15600 | 3.7 | 4216.2162 | 3.7 | 14800 | 3.2 | 4625 | 3.05 | 3.75 | 4.88 | 1.13 | 30.1333
|  | 2587.8261 | 29.3139 | nom | 14000 | 5.5 | 2545.4545 | 502.4905 | 14000 | 5.15 | 2718.4466 | 528.1278 | 14000 | 4.8 | 2916.6667 | 556.5217 | 14000 | 4.45 | 3146.0674 | 594.9025 | 14000 | 4 | 3500 | 699.4125 | 14000 | 3.5 | 4000 | 848.4676 | 35.5
|  |  | 40.2621 | mid | 11200 | 5.85 | 1914.5299 | 0 | 11200 | 5.55 | 2018.018 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.9 | 2285.7143 | 0 | 11200 | 4.3 | 2604.6512 | 0 | 11200 | 3.7 | 3027.027 | 0 | 5226
|  |  | 513.2382 | min | 6600 | 5.15 | 1281.5534 | 0 | 6200 | 4.9 | 1265.3061 | 0 | 5800 | 4.65 | 1247.3118 | 0 | 5400 | 4.35 | 1241.3793 | 0 | 5200 | 3.7 | 1405.4054 | 0 | 5000 | 3.05 | 1639.3443 | 0 | 1395 | 1072 | 323 | 23.1541 | 25728
| 13 |  | 5.0876 | max | 17566.6667 | 5.2833 | 3324.9211 | 5.15 | 17266.6667 | 4.9333 | 3500 | 4.9667 | 17033.3333 | 4.55 | 3743.5897 | 4.7833 | 16833.3333 | 4.3 | 3914.7287 | 4.55 | 16033.3333 | 3.8 | 4219.2982 | 3.9167 | 15200 | 3.3 | 4606.0606 | 3.2667 | 3.75 | 4.95 | 1.2 | 32
|  | 2264.3478 | 28.4047 | nom | 14000 | 5.5 | 2545.4545 | 439.6792 | 14000 | 5.1833 | 2700.9646 | 455.909 | 14000 | 4.8667 | 2876.7123 | 473.3828 | 14000 | 4.55 | 3076.9231 | 497.6589 | 14000 | 4.1 | 3414.6341 | 578.1314 | 14000 | 3.6167 | 3870.9677 | 693.1677 | 35.5
|  |  | 34.5572 | mid | 11200 | 5.9 | 1898.3051 | 0 | 11200 | 5.5833 | 2005.9701 | 0 | 11200 | 5.3167 | 2106.5831 | 0 | 11200 | 5.0167 | 2232.5581 | 0 | 11200 | 4.4167 | 2535.8491 | 0 | 11200 | 3.8167 | 2934.4978 | 0 | 5226
|  |  | 445.0735 | min | 6700 | 5.15 | 1300.9709 | 0 | 6266.6667 | 4.9667 | 1261.745 | 0 | 5833.3333 | 4.7833 | 1219.5122 | 0 | 5400 | 4.55 | 1186.8132 | 0 | 5233.3333 | 3.9167 | 1336.1702 | 0 | 5066.6667 | 3.2667 | 1551.0204 | 0 | 1395 | 1056 | 339 | 24.3011 | 25344
| 14 |  | 5.1212 | max | 18033.3333 | 5.3167 | 3391.8495 | 5.15 | 17733.3333 | 4.9667 | 3570.4698 | 5.0333 | 17466.6667 | 4.65 | 3756.2724 | 4.9167 | 17266.6667 | 4.4 | 3924.2424 | 4.75 | 16466.6667 | 3.9 | 4222.2222 | 4.1333 | 15600 | 3.4 | 4588.2353 | 3.4833
|  | 1940.8696 | 27.4649 | nom | 14000 | 5.5 | 2545.4545 | 376.8679 | 14000 | 5.2167 | 2683.7061 | 385.6032 | 14000 | 4.9333 | 2837.8378 | 394.7531 | 14000 | 4.65 | 3010.7527 | 408.6041 | 14000 | 4.2 | 3333.3333 | 469.5652 | 14000 | 3.7333 | 3750 | 557.1874
|  |  | 29.0333 | mid | 11200 | 5.95 | 1882.3529 | 0 | 11200 | 5.6167 | 1994.0653 | 0 | 11200 | 5.3833 | 2080.4954 | 0 | 11200 | 5.1333 | 2181.8182 | 0 | 11200 | 4.5333 | 2470.5882 | 0 | 11200 | 3.9333 | 2847.4576 | 0
|  |  | 378.9841 | min | 6800 | 5.15 | 1320.3883 | 0 | 6333.3333 | 5.0333 | 1258.2781 | 0 | 5866.6667 | 4.9167 | 1193.2203 | 0 | 5400 | 4.75 | 1136.8421 | 0 | 5266.6667 | 4.1333 | 1274.1935 | 0 | 5133.3333 | 3.4833 | 1473.6842 | 0
| 15 |  | 5.1426 | max | 18500 | 5.35 | 3457.9439 | 5.15 | 18200 | 5 | 3640 | 5.1 | 17900 | 4.75 | 3768.4211 | 5.05 | 17700 | 4.5 | 3933.3333 | 4.95 | 16900 | 4 | 4225 | 4.35 | 16000 | 3.5 | 4571.4286 | 3.7
|  | 1617.3913 | 26.488 | nom | 14000 | 5.5 | 2545.4545 | 314.0566 | 14000 | 5.25 | 2666.6667 | 317.1355 | 14000 | 5 | 2800 | 320.2755 | 14000 | 4.75 | 2947.3684 | 326.7457 | 14000 | 4.3 | 3255.814 | 371.8141 | 14000 | 3.85 | 3636.3636 | 437.1328
|  |  | 23.696 | mid | 11200 | 6 | 1866.6667 | 0 | 11200 | 5.65 | 1982.3009 | 0 | 11200 | 5.45 | 2055.0459 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.65 | 2408.6022 | 0 | 11200 | 4.05 | 2765.4321 | 0
|  |  | 314.5109 | min | 6900 | 5.15 | 1339.8058 | 0 | 6400 | 5.1 | 1254.902 | 0 | 5900 | 5.05 | 1168.3168 | 0 | 5400 | 4.95 | 1090.9091 | 0 | 5300 | 4.35 | 1218.3908 | 0 | 5200 | 3.7 | 1405.4054 | 0
| 16 |  | 6.8624 | max | 19020 | 5.73 | 3319.3717 | 6.92 | 18720 | 5.3 | 3532.0755 | 5.68 | 18420 | 4.95 | 3721.2121 | 5.37 | 18200 | 4.59 | 3965.1416 | 5.02 | 17380 | 4.08 | 4259.8039 | 4.36 | 16460 | 3.56 | 4623.5955 | 3.65
|  | 1293.913 | 25.4647 | nom | 14000 | 5.93 | 2360.8769 | 186.9817 | 14000 | 5.57 | 2513.465 | 227.8016 | 14000 | 5.21 | 2687.1401 | 240.9521 | 14000 | 4.85 | 2886.5979 | 257.7516 | 14000 | 4.39 | 3189.0661 | 296.769 | 14000 | 3.92 | 3571.4286 | 354.4967
|  |  | 18.6018 | mid | 11200 | 6.42 | 1744.5483 | 0 | 11200 | 5.99 | 1869.783 | 0 | 11200 | 5.68 | 1971.831 | 0 | 11200 | 5.36 | 2089.5522 | 0 | 11200 | 4.74 | 2362.8692 | 0 | 11200 | 4.12 | 2718.4466 | 0
|  |  | 188.5518 | min | 6980 | 6.92 | 1008.6705 | 0 | 6460 | 5.68 | 1137.3239 | 0 | 6000 | 5.37 | 1117.3184 | 0 | 5520 | 5.02 | 1099.6016 | 0 | 5360 | 4.36 | 1229.3578 | 0 | 5180 | 3.65 | 1419.1781 | 0
| 17 |  | 8.69 | max | 19540 | 6.11 | 3198.036 | 8.69 | 19240 | 5.6 | 3435.7143 | 6.26 | 18940 | 5.15 | 3677.6699 | 5.69 | 18700 | 4.68 | 3995.7265 | 5.09 | 17860 | 4.16 | 4293.2692 | 4.37 | 16920 | 3.62 | 4674.0331 | 3.6
|  | 970.4348 | 24.3799 | nom | 14000 | 6.36 | 2201.2579 | 111.6726 | 14000 | 5.89 | 2376.91 | 155.0215 | 14000 | 5.42 | 2583.0258 | 170.5509 | 14000 | 4.95 | 2828.2828 | 190.6552 | 14000 | 4.48 | 3125 | 222.0675 | 14000 | 3.99 | 3508.7719 | 269.5652
|  |  | 13.7455 | mid | 11200 | 6.84 | 1637.4269 | 0 | 11200 | 6.33 | 1769.3523 | 0 | 11200 | 5.91 | 1895.0931 | 0 | 11200 | 5.47 | 2047.532 | 0 | 11200 | 4.83 | 2318.8406 | 0 | 11200 | 4.19 | 2673.031 | 0
|  |  | 111.6726 | min | 7060 | 8.69 | 812.4281 | 0 | 6520 | 6.26 | 1041.5335 | 0 | 6100 | 5.69 | 1072.0562 | 0 | 5640 | 5.09 | 1108.055 | 0 | 5420 | 4.37 | 1240.2746 | 0 | 5160 | 3.6 | 1433.3333 | 0
| 18 |  | 10.46 | max | 20060 | 6.49 | 3090.9091 | 10.46 | 19760 | 5.9 | 3349.1525 | 6.84 | 19460 | 5.35 | 3637.3832 | 6.01 | 19200 | 4.77 | 4025.1572 | 5.16 | 18340 | 4.24 | 4325.4717 | 4.38 | 17380 | 3.68 | 4722.8261 | 3.55
|  | 646.9565 | 23.2063 | nom | 14000 | 6.79 | 2061.8557 | 61.8505 | 14000 | 6.21 | 2254.4283 | 94.5843 | 14000 | 5.63 | 2486.6785 | 107.6467 | 14000 | 5.05 | 2772.2772 | 125.3792 | 14000 | 4.57 | 3063.4573 | 147.707 | 14000 | 4.06 | 3448.2759 | 182.2413
|  |  | 9.061 | mid | 11200 | 7.26 | 1542.6997 | 0 | 11200 | 6.67 | 1679.1604 | 0 | 11200 | 6.14 | 1824.1042 | 0 | 11200 | 5.58 | 2007.1685 | 0 | 11200 | 4.92 | 2276.4228 | 0 | 11200 | 4.26 | 2629.108 | 0
|  |  | 61.8505 | min | 7140 | 10.46 | 682.6004 | 0 | 6580 | 6.84 | 961.9883 | 0 | 6200 | 6.01 | 1031.614 | 0 | 5760 | 5.16 | 1116.2791 | 0 | 5480 | 4.38 | 1251.1416 | 0 | 5140 | 3.55 | 1447.8873 | 0
| 19 |  | 12.23 | max | 20580 | 6.87 | 2995.6332 | 12.23 | 20280 | 6.2 | 3270.9677 | 7.42 | 19980 | 5.55 | 3600 | 6.33 | 19700 | 4.86 | 4053.4979 | 5.23 | 18820 | 4.32 | 4356.4815 | 4.39 | 17840 | 3.74 | 4770.0535 | 3.5
|  | 323.4783 | 21.8812 | nom | 14000 | 7.22 | 1939.0582 | 26.4496 | 14000 | 6.53 | 2143.951 | 43.5955 | 14000 | 5.84 | 2397.2603 | 51.1024 | 14000 | 5.15 | 2718.4466 | 61.8505 | 14000 | 4.66 | 3004.2918 | 73.6853 | 14000 | 4.13 | 3389.8305 | 92.4224
|  |  | 4.4803 | mid | 11200 | 7.68 | 1458.3333 | 0 | 11200 | 7.01 | 1597.7175 | 0 | 11200 | 6.37 | 1758.2418 | 0 | 11200 | 5.69 | 1968.3656 | 0 | 11200 | 5.01 | 2235.5289 | 0 | 11200 | 4.33 | 2586.6051 | 0
|  |  | 26.4496 | min | 7220 | 12.23 | 590.3516 | 0 | 6640 | 7.42 | 894.8787 | 0 | 6300 | 6.33 | 995.2607 | 0 | 5880 | 5.23 | 1124.283 | 0 | 5540 | 4.39 | 1261.959 | 0 | 5120 | 3.5 | 1462.8571 | 0
| 20 |  | 14 | max | 21100 | 7.25 | 2910.3448 | 14 | 20800 | 6.5 | 3200 | 8 | 20500 | 5.75 | 3565.2174 | 6.65 | 20200 | 4.95 | 4080.8081 | 5.3 | 19300 | 4.4 | 4386.3636 | 4.4 | 18300 | 3.8 | 4815.7895 | 3.45
|  | 0 | 20 | nom | 14000 | 7.65 | 1830.0654 | 0 | 14000 | 6.85 | 2043.7956 | 0 | 14000 | 6.05 | 2314.0496 | 0 | 14000 | 5.25 | 2666.6667 | 0 | 14000 | 4.75 | 2947.3684 | 0 | 14000 | 4.2 | 3333.3333 | 0
|  |  | 0 | mid | 11200 | 8.1 | 1382.716 | 0 | 11200 | 7.35 | 1523.8095 | 0 | 11200 | 6.6 | 1696.9697 | 0 | 11200 | 5.8 | 1931.0345 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.4 | 2545.4545 | 0
|  |  | 0 | min | 7300 | 14 | 521.4286 | 0 | 6700 | 8 | 837.5 | 0 | 6400 | 6.65 | 962.406 | 0 | 6000 | 5.3 | 1132.0755 | 0 | 5600 | 4.4 | 1272.7273 | 0 | 5100 | 3.45 | 1478.2609 | 0
Indoor Temp. |  | 21
LWT |  |  | 25 CAP: 25; 35 CAP: 35; 40 CAP: 40; 45 CAP: 45; 50 CAP: 50; 55 CAP: 55
Outdoor air temperature[℃] |  | Heating Demand | COP | CL | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP
|  |  | LWT |  |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI
| -15 |  | 1.6054 | max | - | - | - | - | 14000 | 1.85 | 7567.5676 | 2.2032 | 13500 | 1.7 | 7941.1765 | 1.9968 | 13100 | 1.55 | 8451.6129 | 1.7925 | 12600 | 1.45 | 8689.6552 | 1.629 | 12200 | 1.3 | 9384.6154 | 1.4387
|  | 11645.2174 | 50.6211 | nom | - | - | - | - | 11000 | 2.3 | 4782.6087 | 5285.5508 | 11000 | 2.1 | 5238.0952 | 5832.0414 | 11000 | 1.9 | 5789.4737 | 6496.7658 | 11000 | 1.75 | 6285.7143 | 7148.5954 | 11000 | 1.6 | 6875 | 8094.2883 | [5 empty] | 11645.2174
|  |  | 100 | mid | - | - | - | - | 8800 | 2.5 | 3520 | 3 | 8800 | 2.3 | 3826.087 | 3 | 8800 | 2.1 | 4190.4762 | 3 | 8800 | 1.9 | 4631.5789 | 3 | 8800 | 1.7 | 5176.4706 | 3
|  |  | 7253.8654 | min | - | - | - | - | 7800 | 2.35 | 3319.1489 | 0.21507 | 7200 | 2 | 3600 | 0.25809 | 6500 | 1.6 | 4062.5 | 0.30725 | 5700 | 1.3 | 4384.6154 | 0.40326 | 4800 | 1 | 4800 | 0.53768
| -14 |  | 1.9332 | max | 14280 | 2.08 | 6865.3846 | 2.6878 | 14080 | 1.93 | 7295.3368 | 2.5313 | 13640 | 1.78 | 7662.9213 | 2.34 | 13280 | 1.62 | 8197.5309 | 2.1391 | 12880 | 1.53 | 8418.3007 | 1.9326 | 12560 | 1.39 | 9035.9712 | 1.7257
|  | 11321.7391 | 49.9861 | nom | 14000 | 2.64 | 5303.0303 | 4212.2291 | 14000 | 2.34 | 5982.906 | 4472.6898 | 14000 | 2.12 | 6603.7736 | 4838.3501 | 14000 | 1.9 | 7368.4211 | 5292.6829 | 14000 | 1.77 | 7909.6045 | 5858.2677 | 14000 | 1.63 | 8588.9571 | 6560.8466 | [5 empty] | 11321.7391 | 323.4783 | 2.7778
|  |  | 100 | mid | 11200 | 2.69 | 4163.5688 | 2 | 11200 | 2.54 | 4409.4488 | 2 | 11200 | 2.35 | 4765.9574 | 2 | 11200 | 2.15 | 5209.3023 | 2 | 11200 | 1.94 | 5773.1959 | 2 | 11200 | 1.73 | 6473.9884 | 2
|  |  | 5856.5253 | min | 7720 | 2.59 | 2980.695 | 0.043478 | 7420 | 2.34 | 3170.9402 | 0.043478 | 6880 | 2.01 | 3422.8856 | 0.043478 | 6260 | 1.63 | 3840.4908 | 0.043478 | 5480 | 1.33 | 4120.3008 | 0.043478 | 4640 | 1.02 | 4549.0196 | 0.043478
| -13 |  | 1.9877 | max | 14360 | 2.16 | 6648.1481 | 2.7222 | 14160 | 2.01 | 7044.7761 | 2.5679 | 13780 | 1.86 | 7408.6022 | 2.3835 | 13460 | 1.69 | 7964.497 | 2.179 | 13160 | 1.61 | 8173.913 | 1.9589 | 12920 | 1.48 | 8729.7297 | 1.7384
|  | 10998.2609 | 49.3469 | nom | 14000 | 2.68 | 5223.8806 | 4040.2692 | 14000 | 2.38 | 5882.3529 | 4283.0183 | 14000 | 2.14 | 6542.0561 | 4614.3743 | 14000 | 1.9 | 7368.4211 | 5047.4603 | 14000 | 1.79 | 7821.2291 | 5614.3852 | 14000 | 1.66 | 8433.7349 | 6326.7114 | [5 empty] | 10998.2609 | 323.4783 | 2.8571
|  |  | 100 | mid | 11200 | 2.73 | 4102.5641 | 1 | 11200 | 2.58 | 4341.0853 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.2 | 5090.9091 | 1 | 11200 | 1.98 | 5656.5657 | 1 | 11200 | 1.76 | 6363.6364 | 1
|  |  | 5533.2067 | min | 7340 | 2.58 | 2844.9612 | 0.94774 | 7040 | 2.33 | 3021.4592 | 0.95151 | 6560 | 2.02 | 3247.5248 | 0.95652 | 6020 | 1.66 | 3626.506 | 0.96105 | 5260 | 1.36 | 3867.6471 | 0.96604 | 4480 | 1.04 | 4307.6923 | 0.96998
| -12 |  | 2.0258 | max | 14440 | 2.24 | 6446.4286 | 2.7452 | 14240 | 2.09 | 6813.3971 | 2.5853 | 13920 | 1.94 | 7175.2577 | 2.4055 | 13640 | 1.76 | 7750 | 2.1957 | 13440 | 1.69 | 7952.6627 | 1.9663 | 13280 | 1.57 | 8458.5987 | 1.7343
|  | 10674.7826 | 48.7034 | nom | 14000 | 2.72 | 5147.0588 | 3888.4901 | 14000 | 2.42 | 5785.124 | 4129.0401 | 14000 | 2.16 | 6481.4815 | 4437.6086 | 14000 | 1.9 | 7368.4211 | 4861.601 | 14000 | 1.81 | 7734.8066 | 5428.9103 | 14000 | 1.69 | 8284.0237 | 6155.1952 | [5 empty] | 10674.7826 | 323.4783 | 2.9412
|  |  | 100 | mid | 11200 | 2.77 | 4043.3213 | 1 | 11200 | 2.62 | 4274.8092 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.25 | 4977.7778 | 1 | 11200 | 2.02 | 5544.5545 | 1 | 11200 | 1.79 | 6256.9832 | 1
|  |  | 5269.4492 | min | 6960 | 2.57 | 2708.1712 | 0.87613 | 6660 | 2.32 | 2870.6897 | 0.88431 | 6240 | 2.03 | 3073.8916 | 0.89411 | 5780 | 1.69 | 3420.1183 | 0.9031 | 5040 | 1.39 | 3625.8993 | 0.91474 | 4320 | 1.06 | 4075.4717 | 0.92366
| -11 |  | 2.0675 | max | 14520 | 2.32 | 6258.6207 | 2.7641 | 14320 | 2.17 | 6599.0783 | 2.5996 | 14060 | 2.02 | 6960.396 | 2.4261 | 13820 | 1.83 | 7551.9126 | 2.213 | 13720 | 1.77 | 7751.4124 | 1.9749 | 13640 | 1.66 | 8216.8675 | 1.7308
|  | 10351.3043 | 48.0553 | nom | 14000 | 2.76 | 5072.4638 | 3744.9435 | 14000 | 2.46 | 5691.0569 | 3981.8447 | 14000 | 2.18 | 6422.0183 | 4266.713 | 14000 | 1.9 | 7368.4211 | 4677.4327 | 14000 | 1.83 | 7650.2732 | 5241.5267 | 14000 | 1.72 | 8139.5349 | 5980.6801 | [5 empty] | 10351.3043 | 323.4783 | 3.0303
|  |  | 100 | mid | 11200 | 2.81 | 3985.7651 | 1 | 11200 | 2.66 | 4210.5263 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1 | 11200 | 2.06 | 5436.8932 | 1 | 11200 | 1.82 | 6153.8462 | 1
|  |  | 5006.6852 | min | 6580 | 2.56 | 2570.3125 | 0.8163 | 6280 | 2.31 | 2718.6147 | 0.8275 | 5920 | 2.04 | 2901.9608 | 0.83926 | 5540 | 1.72 | 3220.9302 | 0.85005 | 4820 | 1.42 | 3394.3662 | 0.86698 | 4160 | 1.08 | 3851.8519 | 0.87945
| -10 |  | 2.1125 | max | 14600 | 2.4 | 6083.3333 | 2.7797 | 14400 | 2.25 | 6400 | 2.6115 | 14200 | 2.1 | 6761.9048 | 2.4453 | 14000 | 1.9 | 7368.4211 | 2.2308 | 14000 | 1.85 | 7567.5676 | 1.9846 | 14000 | 1.75 | 8000 | 1.7279
|  | 10027.8261 | 47.4026 | nom | 14000 | 2.8 | 5000 | 3607.5605 | 14000 | 2.5 | 5600 | 3839.8221 | 14000 | 2.2 | 6363.6364 | 4100.7874 | 14000 | 1.9 | 7368.4211 | 4495.1787 | 14000 | 1.85 | 7567.5676 | 5052.9251 | 14000 | 1.75 | 8000 | 5803.4808 | [5 empty] | 10027.8261 | 323.4783 | 3.125
|  |  | 100 | mid | 11200 | 2.85 | 3929.8246 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.1 | 5333.3333 | 1 | 11200 | 1.85 | 6054.0541 | 1
|  |  | 4746.9546 | min | 6200 | 2.55 | 2431.3725 | 0.76557 | 5900 | 2.3 | 2565.2174 | 0.77884 | 5600 | 2.05 | 2731.7073 | 0.79068 | 5300 | 1.75 | 3028.5714 | 0.80133 | 4600 | 1.45 | 3172.4138 | 0.8224 | 4000 | 1.1 | 3636.3636 | 0.8372
| -9 |  | 2.1711 | max | 15100 | 2.5 | 6040 | 2.9648 | 14900 | 2.3333 | 6385.7143 | 2.6698 | 14700 | 2.1667 | 6784.6154 | 2.4785 | 14500 | 1.9667 | 7372.8814 | 2.2544 | 14233.3333 | 1.9167 | 7426.087 | 2.0157 | 14000 | 1.8167 | 7706.422 | 1.7705
|  | 9704.3478 | 46.7449 | nom | 14000 | 2.8833 | 4855.4913 | 3273.239 | 14000 | 2.6 | 5384.6154 | 3634.9131 | 14000 | 2.3167 | 6043.1655 | 3915.441 | 14000 | 2.0333 | 6885.2459 | 4304.6815 | 14000 | 1.95 | 7179.4872 | 4814.4686 | 14000 | 1.8167 | 7706.422 | 5481.2163 | [5 empty] | 9704.3478 | 323.4783 | 3.2258
|  |  | 100 | mid | 11200 | 2.9833 | 3754.1899 | 1 | 11200 | 2.8 | 4000 | 1 | 11200 | 2.6167 | 4280.2548 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.1667 | 5169.2308 | 1 | 11200 | 1.9333 | 5793.1034 | 1
|  |  | 4469.8569 | min | 5833.3333 | 2.9167 | 2000 | 0.72131 | 5266.6667 | 2.2833 | 2306.5693 | 0.74792 | 5066.6667 | 2.05 | 2471.5447 | 0.75614 | 4866.6667 | 1.7833 | 2728.972 | 0.76384 | 4266.6667 | 1.4667 | 2909.0909 | 0.78428 | 3700 | 1.1167 | 3313.4328 | 0.80058
| -8 |  | 2.2291 | max | 15600 | 2.6 | 6000 | 3.1695 | 15400 | 2.4167 | 6372.4138 | 2.7246 | 15200 | 2.2333 | 6805.9701 | 2.5105 | 15000 | 2.0333 | 7377.0492 | 2.2797 | 14466.6667 | 1.9833 | 7294.1176 | 2.0456 | 14000 | 1.8833 | 7433.6283 | 1.8107
|  | 9380.8696 | 46.0822 | nom | 14000 | 2.9667 | 4719.1011 | 2959.6865 | 14000 | 2.7 | 5185.1852 | 3443.0884 | 14000 | 2.4333 | 5753.4247 | 3736.6302 | 14000 | 2.1667 | 6461.5385 | 4114.8919 | 14000 | 2.05 | 6829.2683 | 4585.9238 | 14000 | 1.8833 | 7433.6283 | 5180.9288 | [5 empty] | 9380.8696 | 323.4783 | 3.3333
|  |  | 100 | mid | 11200 | 3.1167 | 3593.5829 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.6833 | 4173.913 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.2333 | 5014.9254 | 1 | 11200 | 2.0167 | 5553.719 | 1
|  |  | 4208.4542 | min | 5466.6667 | 3.2833 | 1664.9746 | 0.68271 | 4633.3333 | 2.2667 | 2044.1176 | 0.72298 | 4533.3333 | 2.05 | 2211.3821 | 0.72713 | 4433.3333 | 1.8167 | 2440.367 | 0.73116 | 3933.3333 | 1.4833 | 2651.6854 | 0.74966 | 3400 | 1.1333 | 3000 | 0.76678
| -7 |  | 2.2873 | max | 16100 | 2.7 | 5962.963 | 3.3905 | 15900 | 2.5 | 6360 | 2.7768 | 15700 | 2.3 | 6826.087 | 2.5417 | 15500 | 2.1 | 7380.9524 | 2.3066 | 14700 | 2.05 | 7170.7317 | 2.0745 | 14000 | 1.95 | 7179.4872 | 1.8487
|  | 9057.3913 | 45.4142 | nom | 14000 | 3.05 | 4590.1639 | 2671.4037 | 14000 | 2.8 | 5000 | 3261.7954 | 14000 | 2.55 | 5490.1961 | 3563.5299 | 14000 | 2.3 | 6086.9565 | 3926.7792 | 14000 | 2.15 | 6511.6279 | 4366.1394 | 14000 | 1.95 | 7179.4872 | 4899.313 | [5 empty] | 9057.3913 | 323.4783 | 3.4483
|  |  | 100 | mid | 11200 | 3.25 | 3446.1538 | 1 | 11200 | 3 | 3733.3333 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1 | 11200 | 2.1 | 5333.3333 | 1
|  |  | 3959.7921 | min | 5100 | 3.65 | 1397.2603 | 0.64875 | 4000 | 2.25 | 1777.7778 | 0.70242 | 4000 | 2.05 | 1951.2195 | 0.70242 | 4000 | 1.85 | 2162.1622 | 0.70242 | 3600 | 1.5 | 2400 | 0.71808 | 3100 | 1.15 | 2695.6522 | 0.73548
| -6 |  | 2.3434 | max | 16144.4444 | 2.7611 | 5847.0825 | 3.4644 | 15944.4444 | 2.5556 | 6239.1304 | 2.8218 | 15733.3333 | 2.35 | 6695.0355 | 2.5771 | 15533.3333 | 2.1444 | 7243.5233 | 2.3307 | 14744.4444 | 2.0944 | 7039.7878 | 2.0936 | 14033.3333 | 1.9944 | 7036.2117 | 1.8587
|  | 8733.913 | 44.7407 | nom | 14000 | 3.0889 | 4532.3741 | 2521.0164 | 14000 | 2.8389 | 4931.5068 | 3095.1144 | 14000 | 2.5889 | 5407.7253 | 3389.0801 | 14000 | 2.3389 | 5985.7482 | 3747.3894 | 14000 | 2.1944 | 6379.7468 | 4171.6353 | 14000 | 2 | 7000 | 4698.9957 | [5 empty] | 8733.913 | 323.4783 | 3.5714
|  |  | 100 | mid | 11200 | 3.2944 | 3399.6627 | 1 | 11200 | 3.0444 | 3678.8321 | 1 | 11200 | 2.7944 | 4007.9523 | 1 | 11200 | 2.5444 | 4401.7467 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.15 | 5209.3023 | 1
|  |  | 3726.9564 | min | 5155.5556 | 3.7111 | 1389.2216 | 0.59201 | 4122.2222 | 2.4056 | 1713.6259 | 0.65157 | 4077.7778 | 2.1667 | 1882.0513 | 0.65375 | 4022.2222 | 1.9222 | 2092.4855 | 0.65643 | 3611.1111 | 1.5611 | 2313.1673 | 0.67504 | 3111.1111 | 1.1944 | 2604.6512 | 0.69513
| -5 |  | 2.4063 | max | 16188.8889 | 2.8222 | 5736.2205 | 3.5407 | 15988.8889 | 2.6111 | 6123.4043 | 2.8772 | 15766.6667 | 2.4 | 6569.4444 | 2.6189 | 15566.6667 | 2.1889 | 7111.6751 | 2.3571 | 14788.8889 | 2.1389 | 6914.2857 | 2.1137 | 14066.6667 | 2.0389 | 6899.1826 | 1.8681
|  | 8410.4348 | 44.0614 | nom | 14000 | 3.1278 | 4476.0213 | 2375.3384 | 14000 | 2.8778 | 4864.8649 | 2923.1109 | 14000 | 2.6278 | 5327.6956 | 3211.4482 | 14000 | 2.3778 | 5887.8505 | 3568.0569 | 14000 | 2.2389 | 6253.1017 | 3979.0464 | 14000 | 2.05 | 6829.2683 | 4502.1533 | [5 empty] | 8410.4348 | 323.4783 | 3.7037
|  |  | 100 | mid | 11200 | 3.3389 | 3354.4093 | 1 | 11200 | 3.0889 | 3625.8993 | 1 | 11200 | 2.8389 | 3945.2055 | 1 | 11200 | 2.5889 | 4326.1803 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.2 | 5090.9091 | 1
|  |  | 3495.2003 | min | 5211.1111 | 3.7722 | 1381.4433 | 0.53421 | 4244.4444 | 2.5611 | 1657.2668 | 0.59894 | 4155.5556 | 2.2833 | 1819.9513 | 0.604 | 4044.4444 | 1.9944 | 2027.8552 | 0.61015 | 3622.2222 | 1.6222 | 2232.8767 | 0.63188 | 3122.2222 | 1.2389 | 2520.1794 | 0.65466
| -4 |  | 2.4774 | max | 16233.3333 | 2.8833 | 5630.0578 | 3.6194 | 16033.3333 | 2.6667 | 6012.5 | 2.9435 | 15800 | 2.45 | 6448.9796 | 2.6674 | 15600 | 2.2333 | 6985.0746 | 2.386 | 14833.3333 | 2.1833 | 6793.8931 | 2.1346 | 14100 | 2.0833 | 6768 | 1.8769
|  | 8086.9565 | 43.376 | nom | 14000 | 3.1667 | 4421.0526 | 2234.3146 | 14000 | 2.9167 | 4800 | 2747.3821 | 14000 | 2.6667 | 5250 | 3031.8242 | 14000 | 2.4167 | 5793.1034 | 3389.2859 | 14000 | 2.2833 | 6131.3869 | 3788.5443 | 14000 | 2.1 | 6666.6667 | 4308.5641 | [5 empty] | 8086.9565 | 323.4783 | 3.8462
|  |  | 100 | mid | 11200 | 3.3833 | 3310.3448 | 1 | 11200 | 3.1333 | 3574.4681 | 1 | 11200 | 2.8833 | 3884.3931 | 1 | 11200 | 2.6333 | 4253.1646 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.25 | 4977.7778 | 1
|  |  | 3264.2837 | min | 5266.6667 | 3.8333 | 1373.913 | 0.47533 | 4366.6667 | 2.7167 | 1607.362 | 0.54443 | 4233.3333 | 2.4 | 1763.8889 | 0.55315 | 4066.6667 | 2.0667 | 1967.7419 | 0.56359 | 3633.3333 | 1.6833 | 2158.4158 | 0.58858 | 3133.3333 | 1.2833 | 2441.5584 | 0.61409
| -3 |  | 2.5588 | max | 16277.7778 | 2.9444 | 5528.3019 | 3.7006 | 16077.7778 | 2.7222 | 5906.1224 | 3.0213 | 15833.3333 | 2.5 | 6333.3333 | 2.7227 | 15633.3333 | 2.2778 | 6863.4146 | 2.4174 | 14877.7778 | 2.2278 | 6678.3042 | 2.1563 | 14133.3333 | 2.1278 | 6642.2977 | 1.8852
|  | 7763.4783 | 42.6843 | nom | 14000 | 3.2056 | 4367.4177 | 2097.8854 | 14000 | 2.9556 | 4736.8421 | 2569.5705 | 14000 | 2.7056 | 5174.538 | 2851.3947 | 14000 | 2.4556 | 5701.3575 | 3211.5605 | 14000 | 2.3278 | 6014.3198 | 3600.2903 | 14000 | 2.15 | 6511.6279 | 4118.0157 | [5 empty] | 7763.4783 | 323.4783 | 4
|  |  | 100 | mid | 11200 | 3.4278 | 3267.423 | 1 | 11200 | 3.1778 | 3524.4755 | 1 | 11200 | 2.9278 | 3825.4269 | 1 | 11200 | 2.6778 | 4182.5726 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1
|  |  | 3034.0683 | min | 5322.2222 | 3.8944 | 1366.6191 | 0.41534 | 4488.8889 | 2.8722 | 1562.8627 | 0.48794 | 4311.1111 | 2.5167 | 1713.0243 | 0.50115 | 4088.8889 | 2.1389 | 1911.6883 | 0.51674 | 3644.4444 | 1.7444 | 2089.172 | 0.54517 | 3144.4444 | 1.3278 | 2368.2008 | 0.5734
| -2 |  | 2.6525 | max | 16322.2222 | 3.0056 | 5430.6839 | 3.7844 | 16122.2222 | 2.7778 | 5804 | 3.1113 | 15866.6667 | 2.55 | 6222.2222 | 2.7851 | 15666.6667 | 2.3222 | 6746.4115 | 2.4511 | 14922.2222 | 2.2722 | 6567.2372 | 2.179 | 14166.6667 | 2.1722 | 6521.7391 | 1.893
|  | 7440 | 41.9859 | nom | 14000 | 3.2444 | 4315.0685 | 1965.9865 | 14000 | 2.9944 | 4675.3247 | 2391.3134 | 14000 | 2.7444 | 5101.2146 | 2671.3177 | 14000 | 2.4944 | 5612.4722 | 3035.3409 | 14000 | 2.3722 | 5901.6393 | 3414.4357 | 14000 | 2.2 | 6363.6364 | 3930.3038 | [5 empty] | 7440 | 323.4783 | 4.1667
|  |  | 100 | mid | 11200 | 3.4722 | 3225.6 | 1 | 11200 | 3.2222 | 3475.8621 | 1 | 11200 | 2.9722 | 3768.2243 | 1 | 11200 | 2.7222 | 4114.2857 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1
|  |  | 2804.9256 | min | 5377.7778 | 3.9556 | 1359.5506 | 0.3542 | 4611.1111 | 3.0278 | 1522.9358 | 0.42934 | 4388.8889 | 2.6333 | 1666.6667 | 0.44796 | 4111.1111 | 2.2111 | 1859.2965 | 0.46959 | 3655.5556 | 1.8056 | 2024.6154 | 0.50162 | 3155.5556 | 1.3722 | 2299.5951 | 0.5326
| -1 |  | 2.7608 | max | 16366.6667 | 3.0667 | 5336.9565 | 3.8707 | 16166.6667 | 2.8333 | 5705.8824 | 3.214 | 15900 | 2.6 | 6115.3846 | 2.8549 | 15700 | 2.3667 | 6633.8028 | 2.4874 | 14966.6667 | 2.3167 | 6460.4317 | 2.2025 | 14200 | 2.2167 | 6406.015 | 1.9002
|  | 7116.5217 | 41.2805 | nom | 14000 | 3.2833 | 4263.9594 | 1838.5498 | 14000 | 3.0333 | 4615.3846 | 2214.1951 | 14000 | 2.7833 | 5029.9401 | 2492.7003 | 14000 | 2.5333 | 5526.3158 | 2861.0603 | 14000 | 2.4167 | 5793.1034 | 3231.1208 | 14000 | 2.25 | 6222.2222 | 3745.2319 | [5 empty] | 7116.5217 | 323.4783 | 4.3478
|  |  | 100 | mid | 11200 | 3.5167 | 3184.8341 | 1 | 11200 | 3.2667 | 3428.5714 | 1 | 11200 | 3.0167 | 3712.7072 | 1 | 11200 | 2.7667 | 4048.1928 | 1 | 11200 | 2.6 | 4307.6923 | 1 | 11200 | 2.4 | 4666.6667 | 1
|  |  | 2577.6907 | min | 5433.3333 | 4.0167 | 1352.6971 | 0.29188 | 4733.3333 | 3.1833 | 1486.911 | 0.36853 | 4466.6667 | 2.75 | 1624.2424 | 0.39354 | 4133.3333 | 2.2833 | 1810.219 | 0.42215 | 3666.6667 | 1.8667 | 1964.2857 | 0.45795 | 3166.6667 | 1.4167 | 2235.2941 | 0.49168
| 0 |  | 2.8862 | max | 16411.1111 | 3.1278 | 5246.8917 | 3.9598 | 16211.1111 | 2.8889 | 5611.5385 | 3.3304 | 15933.3333 | 2.65 | 6012.5786 | 2.9324 | 15733.3333 | 2.4111 | 6525.3456 | 2.5261 | 15011.1111 | 2.3611 | 6357.6471 | 2.2269 | 14233.3333 | 2.2611 | 6294.8403 | 1.9068
|  | 6793.0435 | 40.5676 | nom | 14000 | 3.3222 | 4214.0468 | 1715.5039 | 14000 | 3.0722 | 4556.962 | 2039.7043 | 14000 | 2.8222 | 4960.6299 | 2316.5787 | 14000 | 2.5722 | 5442.7646 | 2689.1229 | 14000 | 2.4611 | 5688.4876 | 3050.4756 | 14000 | 2.3 | 6086.9565 | 3562.6103 | [5 empty] | 6793.0435 | 323.4783 | 4.5455
|  |  | 100 | mid | 11200 | 3.5611 | 3145.0858 | 1 | 11200 | 3.3111 | 3382.5503 | 1 | 11200 | 3.0611 | 3658.8022 | 1 | 11200 | 2.8111 | 3984.1897 | 1 | 11200 | 2.65 | 4226.4151 | 1 | 11200 | 2.45 | 4571.4286 | 1
|  |  | 2353.5902 | min | 5488.8889 | 4.0778 | 1346.049 | 0.22835 | 4855.5556 | 3.3389 | 1454.2429 | 0.30538 | 4544.4444 | 2.8667 | 1585.2713 | 0.33785 | 4155.5556 | 2.3556 | 1764.1509 | 0.37441 | 3677.7778 | 1.9278 | 1907.781 | 0.41414 | 3177.7778 | 1.4611 | 2174.9049 | 0.45066
| 1 |  | 3.0312 | max | 16455.5556 | 3.1889 | 5160.2787 | 4.0516 | 16255.5556 | 2.9444 | 5520.7547 | 3.4611 | 15966.6667 | 2.7 | 5913.5802 | 3.0177 | 15766.6667 | 2.4556 | 6420.8145 | 2.5674 | 15055.5556 | 2.4056 | 6258.6605 | 2.2521 | 14266.6667 | 2.3056 | 6187.9518 | 1.9128
|  | 6469.5652 | 39.8468 | nom | 14000 | 3.3611 | 4165.2893 | 1596.7739 | 14000 | 3.1111 | 4500 | 1869.1976 | 14000 | 2.8611 | 4893.2039 | 2143.902 | 14000 | 2.6111 | 5361.7021 | 2519.9014 | 14000 | 2.5056 | 5587.5831 | 2872.6197 | 14000 | 2.35 | 5957.4468 | 3382.2553 | [5 empty] | 6469.5652 | 323.4783 | 4.7619
|  |  | 100 | mid | 11200 | 3.6056 | 3106.3174 | 1 | 11200 | 3.3556 | 3337.7483 | 1 | 11200 | 3.1056 | 3606.4401 | 1 | 11200 | 2.8556 | 3922.179 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.5 | 4480 | 1
|  |  | 2134.29 | min | 5544.4444 | 4.1389 | 1339.5973 | 0.16358 | 4977.7778 | 3.4944 | 1424.4833 | 0.23975 | 4622.2222 | 2.9833 | 1549.3482 | 0.28085 | 4177.7778 | 2.4278 | 1720.8238 | 0.32636 | 3688.8889 | 1.9889 | 1854.7486 | 0.37021 | 3188.8889 | 1.5056 | 2118.0812 | 0.40952
14kW-Maximum heating CAP | 2 |  | 3.1987 | max | 16500 | 3.25 | 5076.9231 | 4.1464 | 16300 | 3 | 5433.3333 | 3.6071 | 16000 | 2.75 | 5818.1818 | 3.1111 | 15800 | 2.5 | 6320 | 2.6112 | 15100 | 2.45 | 6163.2653 | 2.2783 | 14300 | 2.35 | 6085.1064 | 1.9183
|  | 6146.087 | 39.1176 | nom | 14000 | 3.4 | 4117.6471 | 1482.2826 | 14000 | 3.15 | 4444.4444 | 1703.8729 | 14000 | 2.9 | 4827.5862 | 1975.5199 | 14000 | 2.65 | 5283.0189 | 2353.7359 | 14000 | 2.55 | 5490.1961 | 2697.6619 | 14000 | 2.4 | 5833.3333 | 3203.9891 | [5 empty] | 6146.087 | 323.4783 | 5
|  |  | 100 | mid | 11200 | 3.65 | 3068.4932 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 3.15 | 3555.5556 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.55 | 4392.1569 | 1
|  |  | 1921.4596 | min | 5600 | 4.2 | 1333.3333 | 0.097516 | 5100 | 3.65 | 1397.2603 | 0.17149 | 4700 | 3.1 | 1516.129 | 0.22247 | 4200 | 2.5 | 1680 | 0.27801 | 3700 | 2.05 | 1804.878 | 0.32614 | 3200 | 1.55 | 2064.5161 | 0.36826
| 3 |  | 3.4061 | max | 16560 | 3.54 | 4677.9661 | 4.626 | 16360 | 3.25 | 5033.8462 | 3.7913 | 16080 | 2.96 | 5432.4324 | 3.2215 | 15860 | 2.66 | 5962.406 | 2.6568 | 15160 | 2.54 | 5968.5039 | 2.2934 | 14360 | 2.38 | 6033.6134 | 1.9052
|  | 5822.6087 | 38.3796 | nom | 14000 | 3.7 | 3783.7838 | 1258.669 | 14000 | 3.41 | 4105.5718 | 1535.7753 | 14000 | 3.12 | 4487.1795 | 1807.4469 | 14000 | 2.82 | 4964.539 | 2191.5696 | 14000 | 2.67 | 5243.4457 | 2538.8815 | 14000 | 2.47 | 5668.0162 | 3056.166 | [5 empty] | 5822.6087 | 323.4783 | 5.2632
|  |  | 100 | mid | 11200 | 3.97 | 2821.1587 | 1 | 11200 | 3.68 | 3043.4783 | 1 | 11200 | 3.39 | 3303.8348 | 1 | 11200 | 3.09 | 3624.5955 | 1 | 11200 | 2.88 | 3888.8889 | 1 | 11200 | 2.62 | 4274.8092 | 1
|  |  | 1709.4456 | min | 5380 | 4.68 | 1149.5726 | 0.07605 | 4920 | 3.81 | 1291.3386 | 0.14373 | 4500 | 3.18 | 1415.0943 | 0.1974 | 4000 | 2.51 | 1593.6255 | 0.25314 | 3500 | 2.04 | 1715.6863 | 0.30164 | 3000 | 1.53 | 1960.7843 | 0.34422
| 4 |  | 3.6295 | max | 16620 | 3.83 | 4339.4256 | 5.1112 | 16420 | 3.5 | 4691.4286 | 3.9688 | 16160 | 3.17 | 5097.7918 | 3.3243 | 15920 | 2.82 | 5645.3901 | 2.6945 | 15220 | 2.63 | 5787.0722 | 2.3028 | 14420 | 2.41 | 5983.4025 | 1.8892 | 3.33 | 3.69 | 0.36 | 10.8108
|  | 5499.1304 | 37.632 | nom | 14000 | 4 | 3500 | 1075.9083 | 14000 | 3.67 | 3814.7139 | 1385.5815 | 14000 | 3.34 | 4191.6168 | 1654.2215 | 14000 | 2.99 | 4682.2742 | 2040.8683 | 14000 | 2.79 | 5017.9211 | 2388.0155 | 14000 | 2.54 | 5511.811 | 2910.8811 | 37.9 |  |  |  |  | 5499.1304 | 323.4783 | 5.5556
|  |  | 100 | mid | 11200 | 4.29 | 2610.7226 | 1 | 11200 | 3.96 | 2828.2828 | 1 | 11200 | 3.63 | 3085.3994 | 1 | 11200 | 3.28 | 3414.6341 | 1 | 11200 | 3.01 | 3720.9302 | 1 | 11200 | 2.69 | 4163.5688 | 1 | 5841
|  |  | 1515.0998 | min | 5160 | 5.16 | 1000 | 0.056147 | 4740 | 3.97 | 1193.9547 | 0.11751 | 4300 | 3.26 | 1319.0184 | 0.17379 | 3800 | 2.52 | 1507.9365 | 0.22961 | 3300 | 2.03 | 1625.6158 | 0.27837 | 2800 | 1.51 | 1854.3046 | 0.32133 | 1756 | 1500 | 256 | 14.5786 | 36000
| 5 |  | 3.8704 | max | 16680 | 4.12 | 4048.5437 | 5.6012 | 16480 | 3.75 | 4394.6667 | 4.1402 | 16240 | 3.38 | 4804.7337 | 3.4203 | 15980 | 2.98 | 5362.4161 | 2.7249 | 15280 | 2.72 | 5617.6471 | 2.307 | 14480 | 2.44 | 5934.4262 | 1.8704 | 3.33 | 3.84 | 0.51 | 15.3153
|  | 5175.6522 | 36.8742 | nom | 14000 | 4.3 | 3255.814 | 924.0212 | 14000 | 3.93 | 3562.341 | 1250.0974 | 14000 | 3.56 | 3932.5843 | 1513.218 | 14000 | 3.16 | 4430.3797 | 1899.4032 | 14000 | 2.91 | 4810.9966 | 2243.452 | 14000 | 2.61 | 5363.9847 | 2767.1988 | 37.9 |  |  |  |  | 5175.6522 | 323.4783 | 5.8824
|  |  | 100 | mid | 11200 | 4.61 | 2429.5011 | 1 | 11200 | 4.24 | 2641.5094 | 1 | 11200 | 3.87 | 2894.0568 | 1 | 11200 | 3.47 | 3227.6657 | 1 | 11200 | 3.14 | 3566.879 | 1 | 11200 | 2.76 | 4057.971 | 1 | 5841
|  |  | 1337.2552 | min | 4940 | 5.64 | 875.8865 | 0.037644 | 4560 | 4.13 | 1104.1162 | 0.092719 | 4100 | 3.34 | 1227.5449 | 0.1515 | 3600 | 2.53 | 1422.9249 | 0.20732 | 3100 | 2.02 | 1534.6535 | 0.25625 | 2600 | 1.49 | 1744.9664 | 0.29949 | 1756 | 1440 | 316 | 17.9954 | 34560
| 6 |  | 4.13 | max | 16740 | 4.41 | 3795.9184 | 6.0957 | 16540 | 4 | 4135 | 4.3059 | 16320 | 3.59 | 4545.961 | 3.51 | 16040 | 3.14 | 5108.2803 | 2.7485 | 15340 | 2.81 | 5459.0747 | 2.3064 | 14540 | 2.47 | 5886.6397 | 1.849 | 3.33 | 4 | 0.67 | 20.1201
|  | 4852.1739 | 36.1053 | nom | 14000 | 4.6 | 3043.4783 | 795.9959 | 14000 | 4.19 | 3341.2888 | 1126.8602 | 14000 | 3.78 | 3703.7037 | 1382.3857 | 14000 | 3.33 | 4204.2042 | 1765.3787 | 14000 | 3.03 | 4620.462 | 2103.8287 | 14000 | 2.68 | 5223.8806 | 2624.2545 | 37.9 |  |  |  |  | 4852.1739 | 323.4783 | 6.25
|  |  | 100 | mid | 11200 | 4.93 | 2271.8053 | 1 | 11200 | 4.52 | 2477.8761 | 1 | 11200 | 4.11 | 2725.0608 | 1 | 11200 | 3.66 | 3060.1093 | 1 | 11200 | 3.27 | 3425.0765 | 1 | 11200 | 2.83 | 3957.5972 | 1 | 5841
|  |  | 1174.8688 | min | 4720 | 6.12 | 771.2418 | 0.020397 | 4380 | 4.29 | 1020.979 | 0.069234 | 3900 | 3.42 | 1140.3509 | 0.13043 | 3400 | 2.54 | 1338.5827 | 0.18618 | 2900 | 2.01 | 1442.7861 | 0.2352 | 2400 | 1.47 | 1632.6531 | 0.27866 | 1756 | 1383 | 373 | 21.2415 | 33192
| 7 |  | 4.4098 | max | 16800 | 4.7 | 3574.4681 | 6.5942 | 16600 | 4.25 | 3905.8824 | 4.4664 | 16400 | 3.8 | 4315.7895 | 3.5939 | 16100 | 3.3 | 4878.7879 | 2.7659 | 15400 | 2.9 | 5310.3448 | 2.3012 | 14600 | 2.5 | 5840 | 1.8252 | 3.33 | 4.16 | 0.83 | 24.9249
|  | 4528.6957 | 35.3246 | nom | 14000 | 4.9 | 2857.1429 | 686.7677 | 14000 | 4.45 | 3146.0674 | 1013.9397 | 14000 | 4 | 3500 | 1260.0996 | 14000 | 3.5 | 4000 | 1637.3239 | 14000 | 3.15 | 4444.4444 | 1967.974 | 14000 | 2.75 | 5090.9091 | 2481.2341 | 37.9 |  |  |  |  | 4528.6957 | 323.4783 | 6.6667
|  |  | 100 | mid | 11200 | 5.25 | 2133.3333 | 1 | 11200 | 4.8 | 2333.3333 | 1 | 11200 | 4.35 | 2574.7126 | 1 | 11200 | 3.85 | 2909.0909 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 2.9 | 3862.069 | 1 | 5841
|  |  | 1026.9628 | min | 4500 | 6.6 | 681.8182 | 0.0042829 | 4200 | 4.45 | 943.8202 | 0.046957 | 3700 | 3.5 | 1057.1429 | 0.11049 | 3200 | 2.55 | 1254.902 | 0.16609 | 2700 | 2 | 1350 | 0.21514 | 2200 | 1.45 | 1517.2414 | 0.25874 | 1756 | 1329 | 427 | 24.3166 | 31896
| 8 |  | 4.623 | max | 16860 | 4.81 | 3505.1975 | 6.31 | 16640 | 4.38 | 3799.0868 | 4.54 | 16440 | 3.93 | 4183.2061 | 3.7396 | 16160 | 3.48 | 4643.6782 | 2.996 | 15440 | 3.06 | 5045.7516 | 2.4958 | 14640 | 2.64 | 5545.4545 | 1.9909 | 3.33 | 4.29 | 0.96 | 28.8288
|  | 4205.2174 | 34.5308 | nom | 14000 | 5.02 | 2788.8446 | 666.437 | 14000 | 4.59 | 3050.1089 | 926.2593 | 14000 | 4.16 | 3365.3846 | 1124.5012 | 14000 | 3.69 | 3794.0379 | 1403.6205 | 14000 | 3.32 | 4216.8675 | 1684.9117 | 14000 | 2.9 | 4827.5862 | 2112.2275 | 37.9 |  |  |  |  | 4205.2174 | 323.4783 | 7.1429
|  |  | 91.1204 | mid | 11200 | 5.37 | 2085.6611 | 0 | 11200 | 4.95 | 2262.6263 | 0 | 11200 | 4.53 | 2472.4062 | 1 | 11200 | 4.06 | 2758.6207 | 1 | 11200 | 3.58 | 3128.4916 | 1 | 11200 | 3.06 | 3660.1307 | 1 | 5841
|  |  | 909.6209 | min | 4920 | 6.31 | 779.7147 | 0 | 4600 | 4.54 | 1013.2159 | 0 | 4120 | 3.73 | 1104.5576 | 0.012036 | 3640 | 2.91 | 1250.8591 | 0.074764 | 3200 | 2.34 | 1367.5214 | 0.12565 | 2760 | 1.77 | 1559.322 | 0.17123 | 1756 | 1290 | 466 | 26.5376 | 30960
| 9 |  | 4.8075 | max | 16920 | 4.92 | 3439.0244 | 6.02 | 16680 | 4.51 | 3698.4479 | 4.63 | 16480 | 4.06 | 4059.1133 | 3.96 | 16220 | 3.66 | 4431.694 | 3.27 | 15480 | 3.22 | 4807.4534 | 2.7062 | 14680 | 2.78 | 5280.5755 | 2.1706 | 3.33 | 4.41 | 1.08 | 32.4324
|  | 3881.7391 | 33.7228 | nom | 14000 | 5.14 | 2723.7354 | 644.8072 | 14000 | 4.73 | 2959.8309 | 838.3886 | 14000 | 4.32 | 3240.7407 | 980.2372 | 14000 | 3.88 | 3608.2474 | 1187.0762 | 14000 | 3.49 | 4011.4613 | 1434.4031 | 14000 | 3.05 | 4590.1639 | 1788.3633 | 37.9 |  |  |  |  | 3881.7391 | 323.4783 | 7.6923
|  |  | 76.9664 | mid | 11200 | 5.49 | 2040.0729 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.71 | 2377.9193 | 0 | 11200 | 4.27 | 2622.9508 | 0 | 11200 | 3.76 | 2978.7234 | 1 | 11200 | 3.22 | 3478.2609 | 1 | 5841
|  |  | 807.4299 | min | 5340 | 6.02 | 887.0432 | 0 | 5000 | 4.63 | 1079.9136 | 0 | 4540 | 3.96 | 1146.4646 | 0 | 4080 | 3.27 | 1247.7064 | 0 | 3700 | 2.68 | 1380.597 | 0.024232 | 3320 | 2.09 | 1588.5167 | 0.071287 | 1756 | 1255 | 501 | 28.5308 | 30120
| 10 |  | 4.9322 | max | 16980 | 5.03 | 3375.7455 | 5.73 | 16720 | 4.64 | 3603.4483 | 4.72 | 16520 | 4.19 | 3942.7208 | 4.19 | 16280 | 3.84 | 4239.5833 | 3.63 | 15520 | 3.38 | 4591.716 | 3.02 | 14720 | 2.92 | 5041.0959 | 2.41 | 3.33 | 4.52 | 1.19 | 35.7357
|  | 3558.2609 | 32.8992 | nom | 14000 | 5.26 | 2661.597 | 620.9879 | 14000 | 4.87 | 2874.7433 | 753.8688 | 14000 | 4.48 | 3125 | 849.2269 | 14000 | 4.07 | 3439.8034 | 980.2372 | 14000 | 3.66 | 3825.1366 | 1178.2321 | 14000 | 3.2 | 4375 | 1476.4568 | 37.9 |  |  |  |  | 3558.2609 | 323.4783 | 8.3333
|  |  | 64.9836 | mid | 11200 | 5.61 | 1996.4349 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.89 | 2290.3885 | 0 | 11200 | 4.48 | 2500 | 0 | 11200 | 3.94 | 2842.6396 | 0 | 11200 | 3.38 | 3313.6095 | 0 | 5841
|  |  | 721.437 | min | 5760 | 5.73 | 1005.2356 | 0 | 5400 | 4.72 | 1144.0678 | 0 | 4960 | 4.19 | 1183.7709 | 0 | 4520 | 3.63 | 1245.1791 | 0 | 4200 | 3.02 | 1390.7285 | 0 | 3880 | 2.41 | 1609.9585 | 0 | 1756 | 1223 | 533 | 30.3531 | 29352
| 11 |  | 4.9953 | max | 17040 | 5.14 | 3315.1751 | 5.44 | 16760 | 4.77 | 3513.6268 | 4.81 | 16560 | 4.32 | 3833.3333 | 4.42 | 16340 | 4.02 | 4064.6766 | 3.99 | 15560 | 3.54 | 4395.4802 | 3.36 | 14760 | 3.06 | 4823.5294 | 2.73 | 3.33 | 4.65 | 1.32 | 39.6396
|  | 3234.7826 | 32.058 | nom | 14000 | 5.38 | 2602.2305 | 594.6292 | 14000 | 5.01 | 2794.4112 | 672.512 | 14000 | 4.64 | 3017.2414 | 731.8513 | 14000 | 4.26 | 3286.385 | 810.7225 | 14000 | 3.83 | 3655.3525 | 962.7329 | 14000 | 3.35 | 4179.1045 | 1184.9021 | 37.9 |  |  |  |  | 3234.7826 | 323.4783 | 9.0909
|  |  | 54.7174 | mid | 11200 | 5.73 | 1954.6248 | 0 | 11200 | 5.4 | 2074.0741 | 0 | 11200 | 5.07 | 2209.073 | 0 | 11200 | 4.69 | 2388.0597 | 0 | 11200 | 4.12 | 2718.4466 | 0 | 11200 | 3.54 | 3163.8418 | 0 | 5841
|  |  | 647.5591 | min | 6180 | 5.44 | 1136.0294 | 0 | 5800 | 4.81 | 1205.8212 | 0 | 5380 | 4.42 | 1217.1946 | 0 | 4960 | 3.99 | 1243.1078 | 0 | 4700 | 3.36 | 1398.8095 | 0 | 4440 | 2.73 | 1626.3736 | 0 | 1756 | 1191 | 565 | 32.1754 | 28584
| 12 |  | 4.9951 | max | 17100 | 5.25 | 3257.1429 | 5.15 | 16800 | 4.9 | 3428.5714 | 4.9 | 16600 | 4.45 | 3730.3371 | 4.65 | 16400 | 4.2 | 3904.7619 | 4.35 | 15600 | 3.7 | 4216.2162 | 3.7 | 14800 | 3.2 | 4625 | 3.05 | 3.33 | 4.79 | 1.46 | 43.8438
|  | 2911.3043 | 31.1971 | nom | 14000 | 5.5 | 2545.4545 | 565.3018 | 14000 | 5.15 | 2718.4466 | 594.1437 | 14000 | 4.8 | 2916.6667 | 626.087 | 14000 | 4.45 | 3146.0674 | 669.2654 | 14000 | 4 | 3500 | 786.839 | 14000 | 3.5 | 4000 | 954.526 | 37.9 |  |  |  |  | 2911.3043 | 323.4783 | 10
|  |  | 45.832 | mid | 11200 | 5.85 | 1914.5299 | 0 | 11200 | 5.55 | 2018.018 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.9 | 2285.7143 | 0 | 11200 | 4.3 | 2604.6512 | 0 | 11200 | 3.7 | 3027.027 | 0 | 5841
|  |  | 582.8353 | min | 6600 | 5.15 | 1281.5534 | 0 | 6200 | 4.9 | 1265.3061 | 0 | 5800 | 4.65 | 1247.3118 | 0 | 5400 | 4.35 | 1241.3793 | 0 | 5200 | 3.7 | 1405.4054 | 0 | 5000 | 3.05 | 1639.3443 | 0 | 1756 | 1155 | 601 | 34.2255 | 27720
| 13 |  | 5.0526 | max | 17566.6667 | 5.2833 | 3324.9211 | 5.15 | 17266.6667 | 4.9333 | 3500 | 4.9667 | 17033.3333 | 4.55 | 3743.5897 | 4.7833 | 16833.3333 | 4.3 | 3914.7287 | 4.55 | 16033.3333 | 3.8 | 4219.2982 | 3.9167 | 15200 | 3.3 | 4606.0606 | 3.2667 | 3.33 | 4.89 | 1.56 | 46.8468
|  | 2587.8261 | 30.3139 | nom | 14000 | 5.5 | 2545.4545 | 502.4905 | 14000 | 5.1833 | 2700.9646 | 521.0388 | 14000 | 4.8667 | 2876.7123 | 541.0089 | 14000 | 4.55 | 3076.9231 | 568.753 | 14000 | 4.1 | 3414.6341 | 660.7216 | 14000 | 3.6167 | 3870.9677 | 792.1917 | 37.9 |  |  |  |  | 2587.8261 | 323.4783 | 11.1111
|  |  | 39.999 | mid | 11200 | 5.9 | 1898.3051 | 0 | 11200 | 5.5833 | 2005.9701 | 0 | 11200 | 5.3167 | 2106.5831 | 0 | 11200 | 5.0167 | 2232.5581 | 0 | 11200 | 4.4167 | 2535.8491 | 0 | 11200 | 3.8167 | 2934.4978 | 0 | 5841
|  |  | 512.1792 | min | 6700 | 5.15 | 1300.9709 | 0 | 6266.6667 | 4.9667 | 1261.745 | 0 | 5833.3333 | 4.7833 | 1219.5122 | 0 | 5400 | 4.55 | 1186.8132 | 0 | 5233.3333 | 3.9167 | 1336.1702 | 0 | 5066.6667 | 3.2667 | 1551.0204 | 0 | 1756 | 1132 | 624 | 35.5353 | 27168
| 14 |  | 5.0986 | max | 18033.3333 | 5.3167 | 3391.8495 | 5.15 | 17733.3333 | 4.9667 | 3570.4698 | 5.0333 | 17466.6667 | 4.65 | 3756.2724 | 4.9167 | 17266.6667 | 4.4 | 3924.2424 | 4.75 | 16466.6667 | 3.9 | 4222.2222 | 4.1333 | 15600 | 3.4 | 4588.2353 | 3.4833
|  | 2264.3478 | 29.4047 | nom | 14000 | 5.5 | 2545.4545 | 439.6792 | 14000 | 5.2167 | 2683.7061 | 449.8704 | 14000 | 4.9333 | 2837.8378 | 460.5453 | 14000 | 4.65 | 3010.7527 | 476.7048 | 14000 | 4.2 | 3333.3333 | 547.8261 | 14000 | 3.7333 | 3750 | 650.052 | [5 empty] | 2264.3478 | 323.4783 | 12.5
|  |  | 34.3372 | mid | 11200 | 5.95 | 1882.3529 | 0 | 11200 | 5.6167 | 1994.0653 | 0 | 11200 | 5.3833 | 2080.4954 | 0 | 11200 | 5.1333 | 2181.8182 | 0 | 11200 | 4.5333 | 2470.5882 | 0 | 11200 | 3.9333 | 2847.4576 | 0
|  |  | 444.1106 | min | 6800 | 5.15 | 1320.3883 | 0 | 6333.3333 | 5.0333 | 1258.2781 | 0 | 5866.6667 | 4.9167 | 1193.2203 | 0 | 5400 | 4.75 | 1136.8421 | 0 | 5266.6667 | 4.1333 | 1274.1935 | 0 | 5133.3333 | 3.4833 | 1473.6842 | 0
| 15 |  | 5.1327 | max | 18500 | 5.35 | 3457.9439 | 5.15 | 18200 | 5 | 3640 | 5.1 | 17900 | 4.75 | 3768.4211 | 5.05 | 17700 | 4.5 | 3933.3333 | 4.95 | 16900 | 4 | 4225 | 4.35 | 16000 | 3.5 | 4571.4286 | 3.7
|  | 1940.8696 | 28.4649 | nom | 14000 | 5.5 | 2545.4545 | 376.8679 | 14000 | 5.25 | 2666.6667 | 380.5627 | 14000 | 5 | 2800 | 384.3306 | 14000 | 4.75 | 2947.3684 | 392.0949 | 14000 | 4.3 | 3255.814 | 446.1769 | 14000 | 3.85 | 3636.3636 | 524.5593 | [5 empty] | 1940.8696 | 323.4783 | 14.2857
|  |  | 28.853 | mid | 11200 | 6 | 1866.6667 | 0 | 11200 | 5.65 | 1982.3009 | 0 | 11200 | 5.45 | 2055.0459 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.65 | 2408.6022 | 0 | 11200 | 4.05 | 2765.4321 | 0
|  |  | 378.1399 | min | 6900 | 5.15 | 1339.8058 | 0 | 6400 | 5.1 | 1254.902 | 0 | 5900 | 5.05 | 1168.3168 | 0 | 5400 | 4.95 | 1090.9091 | 0 | 5300 | 4.35 | 1218.3908 | 0 | 5200 | 3.7 | 1405.4054 | 0
| 16 |  | 6.6115 | max | 19020 | 5.73 | 3319.3717 | 6.92 | 18720 | 5.3 | 3532.0755 | 5.68 | 18420 | 4.95 | 3721.2121 | 5.37 | 18200 | 4.59 | 3965.1416 | 5.02 | 17380 | 4.08 | 4259.8039 | 4.36 | 16460 | 3.56 | 4623.5955 | 3.65
|  | 1617.3913 | 27.488 | nom | 14000 | 5.93 | 2360.8769 | 233.7271 | 14000 | 5.57 | 2513.465 | 284.752 | 14000 | 5.21 | 2687.1401 | 301.1902 | 14000 | 4.85 | 2886.5979 | 322.1895 | 14000 | 4.39 | 3189.0661 | 370.9613 | 14000 | 3.92 | 3571.4286 | 443.1209 | [5 empty] | 1617.3913 | 323.4783 | 16.6667
|  |  | 23.6094 | mid | 11200 | 6.42 | 1744.5483 | 0 | 11200 | 5.99 | 1869.783 | 0 | 11200 | 5.68 | 1971.831 | 0 | 11200 | 5.36 | 2089.5522 | 0 | 11200 | 4.74 | 2362.8692 | 0 | 11200 | 4.12 | 2718.4466 | 0
|  |  | 244.6337 | min | 6980 | 6.92 | 1008.6705 | 0 | 6460 | 5.68 | 1137.3239 | 0 | 6000 | 5.37 | 1117.3184 | 0 | 5520 | 5.02 | 1099.6016 | 0 | 5360 | 4.36 | 1229.3578 | 0 | 5180 | 3.65 | 1419.1781 | 0
| 17 |  | 8.3341 | max | 19540 | 6.11 | 3198.036 | 8.69 | 19240 | 5.6 | 3435.7143 | 6.26 | 18940 | 5.15 | 3677.6699 | 5.69 | 18700 | 4.68 | 3995.7265 | 5.09 | 17860 | 4.16 | 4293.2692 | 4.37 | 16920 | 3.62 | 4674.0331 | 3.6
|  | 1293.913 | 26.4647 | nom | 14000 | 6.36 | 2201.2579 | 148.8968 | 14000 | 5.89 | 2376.91 | 206.6954 | 14000 | 5.42 | 2583.0258 | 227.4012 | 14000 | 4.95 | 2828.2828 | 254.2069 | 14000 | 4.48 | 3125 | 296.0899 | 14000 | 3.99 | 3508.7719 | 359.4203 | [5 empty] | 1293.913 | 323.4783 | 20
|  |  | 18.535 | mid | 11200 | 6.84 | 1637.4269 | 0 | 11200 | 6.33 | 1769.3523 | 0 | 11200 | 5.91 | 1895.0931 | 0 | 11200 | 5.47 | 2047.532 | 0 | 11200 | 4.83 | 2318.8406 | 0 | 11200 | 4.19 | 2673.031 | 0
|  |  | 155.2558 | min | 7060 | 8.69 | 812.4281 | 0 | 6520 | 6.26 | 1041.5335 | 0 | 6100 | 5.69 | 1072.0562 | 0 | 5640 | 5.09 | 1108.055 | 0 | 5420 | 4.37 | 1240.2746 | 0 | 5160 | 3.6 | 1433.3333 | 0
| 18 |  | 10.3225 | max | 20060 | 6.49 | 3090.9091 | 10.46 | 19760 | 5.9 | 3349.1525 | 6.84 | 19460 | 5.35 | 3637.3832 | 6.01 | 19200 | 4.77 | 4025.1572 | 5.16 | 18340 | 4.24 | 4325.4717 | 4.38 | 17380 | 3.68 | 4722.8261 | 3.55
|  | 970.4348 | 25.3799 | nom | 14000 | 6.79 | 2061.8557 | 92.7758 | 14000 | 6.21 | 2254.4283 | 141.8764 | 14000 | 5.63 | 2486.6785 | 161.47 | 14000 | 5.05 | 2772.2772 | 188.0688 | 14000 | 4.57 | 3063.4573 | 221.5605 | 14000 | 4.06 | 3448.2759 | 273.3619 | [5 empty] | 970.4348 | 323.4783 | 25
|  |  | 13.6321 | mid | 11200 | 7.26 | 1542.6997 | 0 | 11200 | 6.67 | 1679.1604 | 0 | 11200 | 6.14 | 1824.1042 | 0 | 11200 | 5.58 | 2007.1685 | 0 | 11200 | 4.92 | 2276.4228 | 0 | 11200 | 4.26 | 2629.108 | 0
|  |  | 94.0117 | min | 7140 | 10.46 | 682.6004 | 0 | 6580 | 6.84 | 961.9883 | 0 | 6200 | 6.01 | 1031.614 | 0 | 5760 | 5.16 | 1116.2791 | 0 | 5480 | 4.38 | 1251.1416 | 0 | 5140 | 3.55 | 1447.8873 | 0
| 19 |  | 12.23 | max | 20580 | 6.87 | 2995.6332 | 12.23 | 20280 | 6.2 | 3270.9677 | 7.42 | 19980 | 5.55 | 3600 | 6.33 | 19700 | 4.86 | 4053.4979 | 5.23 | 18820 | 4.32 | 4356.4815 | 4.39 | 17840 | 3.74 | 4770.0535 | 3.5
|  | 646.9565 | 24.2063 | nom | 14000 | 7.22 | 1939.0582 | 52.8991 | 14000 | 6.53 | 2143.951 | 87.1909 | 14000 | 5.84 | 2397.2603 | 102.2048 | 14000 | 5.15 | 2718.4466 | 123.7011 | 14000 | 4.66 | 3004.2918 | 147.3705 | 14000 | 4.13 | 3389.8305 | 184.8447 | [5 empty] | 646.9565 | 323.4783 | 33.3333
|  |  | 8.9606 | mid | 11200 | 7.68 | 1458.3333 | 0 | 11200 | 7.01 | 1597.7175 | 0 | 11200 | 6.37 | 1758.2418 | 0 | 11200 | 5.69 | 1968.3656 | 0 | 11200 | 5.01 | 2235.5289 | 0 | 11200 | 4.33 | 2586.6051 | 0
|  |  | 52.8991 | min | 7220 | 12.23 | 590.3516 | 0 | 6640 | 7.42 | 894.8787 | 0 | 6300 | 6.33 | 995.2607 | 0 | 5880 | 5.23 | 1124.283 | 0 | 5540 | 4.39 | 1261.959 | 0 | 5120 | 3.5 | 1462.8571 | 0
| 20 |  | 14 | max | 21100 | 7.25 | 2910.3448 | 14 | 20800 | 6.5 | 3200 | 8 | 20500 | 5.75 | 3565.2174 | 6.65 | 20200 | 4.95 | 4080.8081 | 5.3 | 19300 | 4.4 | 4386.3636 | 4.4 | 18300 | 3.8 | 4815.7895 | 3.45
|  | 323.4783 | 22.8812 | nom | 14000 | 7.65 | 1830.0654 | 23.1056 | 14000 | 6.85 | 2043.7956 | 40.4348 | 14000 | 6.05 | 2314.0496 | 48.6433 | 14000 | 5.25 | 2666.6667 | 61.0336 | 14000 | 4.75 | 2947.3684 | 73.5178 | 14000 | 4.2 | 3333.3333 | 93.7618 | [5 empty] | 323.4783 | 323.4783 | 50
|  |  | 4.4312 | mid | 11200 | 8.1 | 1382.716 | 0 | 11200 | 7.35 | 1523.8095 | 0 | 11200 | 6.6 | 1696.9697 | 0 | 11200 | 5.8 | 1931.0345 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.4 | 2545.4545 | 0
|  |  | 23.1056 | min | 7300 | 14 | 521.4286 | 0 | 6700 | 8 | 837.5 | 0 | 6400 | 6.65 | 962.406 | 0 | 6000 | 5.3 | 1132.0755 | 0 | 5600 | 4.4 | 1272.7273 | 0 | 5100 | 3.45 | 1478.2609 | 0
Indoor Temp. |  | 22
LWT |  |  | 25 CAP: 25; 35 CAP: 35; 40 CAP: 40; 45 CAP: 45; 50 CAP: 50; 55 CAP: 55
Outdoor air temperature[℃] |  | Heating Demand | COP | CL | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP
|  |  | LWT |  |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI
| -15 |  | 1.4735 | max | - | - | - | - | 14000 | 1.85 | 7567.5676 | 2.1547 | 13500 | 1.7 | 7941.1765 | 1.945 | 13100 | 1.55 | 8451.6129 | 1.7386 | 12600 | 1.45 | 8689.6552 | 1.5684 | 12200 | 1.3 | 9384.6154 | 1.3578
|  | 11968.6957 | 52.252 | nom | - | - | - | - | 11000 | 2.3 | 4782.6087 | 5554.7036 | 11000 | 2.1 | 5238.0952 | 6153.5435 | 11000 | 1.9 | 5789.4737 | 6884.2948 | 11000 | 1.75 | 6285.7143 | 7631.2981 | 11000 | 1.6 | 6875 | 8814.6013
|  |  | 100 | mid | - | - | - | - | 8800 | 2.5 | 3520 | 3 | 8800 | 2.3 | 3826.087 | 3 | 8800 | 2.1 | 4190.4762 | 3 | 8800 | 1.9 | 4631.5789 | 3 | 8800 | 1.7 | 5176.4706 | 3
|  |  | 8122.4014 | min | - | - | - | - | 7800 | 2.35 | 3319.1489 | 0.3229 | 7200 | 2 | 3600 | 0.38748 | 6500 | 1.6 | 4062.5 | 0.46128 | 5700 | 1.3 | 4384.6154 | 0.60543 | 4800 | 1 | 4800 | 0.80725
| -14 |  | 1.8485 | max | 14280 | 2.08 | 6865.3846 | 2.682 | 14080 | 1.93 | 7295.3368 | 2.5082 | 13640 | 1.78 | 7662.9213 | 2.3134 | 13280 | 1.62 | 8197.5309 | 2.1102 | 12880 | 1.53 | 8418.3007 | 1.913 | 12560 | 1.39 | 9035.9712 | 1.7141
|  | 11645.2174 | 51.6211 | nom | 14000 | 2.64 | 5303.0303 | 4341.9096 | 14000 | 2.34 | 5982.906 | 4642.8607 | 14000 | 2.12 | 6603.7736 | 5033.7484 | 14000 | 1.9 | 7368.4211 | 5518.4106 | 14000 | 1.77 | 7909.6045 | 6087.5099 | 14000 | 1.63 | 8588.9571 | 6793.7819
|  |  | 100 | mid | 11200 | 2.69 | 4163.5688 | 2 | 11200 | 2.54 | 4409.4488 | 2 | 11200 | 2.35 | 4765.9574 | 2 | 11200 | 2.15 | 5209.3023 | 2 | 11200 | 1.94 | 5773.1959 | 2 | 11200 | 1.73 | 6473.9884 | 2
|  |  | 6299.8437 | min | 7720 | 2.59 | 2980.695 | 0.15901 | 7420 | 2.34 | 3170.9402 | 0.15901 | 6880 | 2.01 | 3422.8856 | 0.15901 | 6260 | 1.63 | 3840.4908 | 0.15901 | 5480 | 1.33 | 4120.3008 | 0.15901 | 4640 | 1.02 | 4549.0196 | 0.15901
| -13 |  | 1.9291 | max | 14360 | 2.16 | 6648.1481 | 2.7278 | 14160 | 2.01 | 7044.7761 | 2.5713 | 13780 | 1.86 | 7408.6022 | 2.3887 | 13460 | 1.69 | 7964.497 | 2.187 | 13160 | 1.61 | 8173.913 | 1.9717 | 12920 | 1.48 | 8729.7297 | 1.7557
|  | 11321.7391 | 50.9861 | nom | 14000 | 2.68 | 5223.8806 | 4150.4622 | 14000 | 2.38 | 5882.3529 | 4403.1113 | 14000 | 2.14 | 6542.0561 | 4739.7161 | 14000 | 1.9 | 7368.4211 | 5176.9384 | 14000 | 1.79 | 7821.2291 | 5742.0066 | 14000 | 1.66 | 8433.7349 | 6448.737
|  |  | 100 | mid | 11200 | 2.73 | 4102.5641 | 2 | 11200 | 2.58 | 4341.0853 | 2 | 11200 | 2.4 | 4666.6667 | 2 | 11200 | 2.2 | 5090.9091 | 2 | 11200 | 1.98 | 5656.5657 | 2 | 11200 | 1.76 | 6363.6364 | 2
|  |  | 5868.8518 | min | 7340 | 2.58 | 2844.9612 | 0.043478 | 7040 | 2.33 | 3021.4592 | 0.043478 | 6560 | 2.02 | 3247.5248 | 0.043478 | 6020 | 1.66 | 3626.506 | 0.043478 | 5260 | 1.36 | 3867.6471 | 0.043478 | 4480 | 1.04 | 4307.6923 | 0.043478
| -12 |  | 1.9834 | max | 14440 | 2.24 | 6446.4286 | 2.7605 | 14240 | 2.09 | 6813.3971 | 2.6067 | 13920 | 1.94 | 7175.2577 | 2.4329 | 13640 | 1.76 | 7750 | 2.2292 | 13440 | 1.69 | 7952.6627 | 1.9994 | 13280 | 1.57 | 8458.5987 | 1.7686
|  | 10998.2609 | 50.3469 | nom | 14000 | 2.72 | 5147.0588 | 3984.1784 | 14000 | 2.42 | 5785.124 | 4219.2775 | 14000 | 2.16 | 6481.4815 | 4520.6062 | 14000 | 1.9 | 7368.4211 | 4933.8226 | 14000 | 1.81 | 7734.8066 | 5500.8698 | 14000 | 1.69 | 8284.0237 | 6218.6446
|  |  | 100 | mid | 11200 | 2.77 | 4043.3213 | 1 | 11200 | 2.62 | 4274.8092 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.25 | 4977.7778 | 1 | 11200 | 2.02 | 5544.5545 | 1 | 11200 | 1.79 | 6256.9832 | 1
|  |  | 5545.2763 | min | 6960 | 2.57 | 2708.1712 | 0.95242 | 6660 | 2.32 | 2870.6897 | 0.95556 | 6240 | 2.03 | 3073.8916 | 0.95933 | 5780 | 1.69 | 3420.1183 | 0.96278 | 5040 | 1.39 | 3625.8993 | 0.96725 | 4320 | 1.06 | 4075.4717 | 0.97068
| -11 |  | 2.0215 | max | 14520 | 2.32 | 6258.6207 | 2.7816 | 14320 | 2.17 | 6599.0783 | 2.6226 | 14060 | 2.02 | 6960.396 | 2.4542 | 13820 | 1.83 | 7551.9126 | 2.2462 | 13720 | 1.77 | 7751.4124 | 2.0073 | 13640 | 1.66 | 8216.8675 | 1.7648
|  | 10674.7826 | 49.7034 | nom | 14000 | 2.76 | 5072.4638 | 3837.6699 | 14000 | 2.46 | 5691.0569 | 4070.2479 | 14000 | 2.18 | 6422.0183 | 4349.5225 | 14000 | 1.9 | 7368.4211 | 4752.4182 | 14000 | 1.83 | 7650.2732 | 5317.9446 | 14000 | 1.72 | 8139.5349 | 6048.7466
|  |  | 100 | mid | 11200 | 2.81 | 3985.7651 | 1 | 11200 | 2.66 | 4210.5263 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1 | 11200 | 2.06 | 5436.8932 | 1 | 11200 | 1.82 | 6153.8462 | 1
|  |  | 5280.6639 | min | 6580 | 2.56 | 2570.3125 | 0.88632 | 6280 | 2.31 | 2718.6147 | 0.89325 | 5920 | 2.04 | 2901.9608 | 0.90053 | 5540 | 1.72 | 3220.9302 | 0.90721 | 4820 | 1.42 | 3394.3662 | 0.91768 | 4160 | 1.08 | 3851.8519 | 0.9254
| -10 |  | 2.0631 | max | 14600 | 2.4 | 6083.3333 | 2.7991 | 14400 | 2.25 | 6400 | 2.6359 | 14200 | 2.1 | 6761.9048 | 2.4742 | 14000 | 1.9 | 7368.4211 | 2.2637 | 14000 | 1.85 | 7567.5676 | 2.0164 | 14000 | 1.75 | 8000 | 1.7616
|  | 10351.3043 | 49.0553 | nom | 14000 | 2.8 | 5000 | 3698.1118 | 14000 | 2.5 | 5600 | 3926.9767 | 14000 | 2.2 | 6363.6364 | 4183.6576 | 14000 | 1.9 | 7368.4211 | 4572.753 | 14000 | 1.85 | 7567.5676 | 5133.5154 | 14000 | 1.75 | 8000 | 5876.1004
|  |  | 100 | mid | 11200 | 2.85 | 3929.8246 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.1 | 5333.3333 | 1 | 11200 | 1.85 | 6054.0541 | 1
|  |  | 5017.2667 | min | 6200 | 2.55 | 2431.3725 | 0.83026 | 5900 | 2.3 | 2565.2174 | 0.83987 | 5600 | 2.05 | 2731.7073 | 0.84845 | 5300 | 1.75 | 3028.5714 | 0.85615 | 4600 | 1.45 | 3172.4138 | 0.87141 | 4000 | 1.1 | 3636.3636 | 0.88213
| -9 |  | 2.1242 | max | 15100 | 2.5 | 6040 | 2.9688 | 14900 | 2.3333 | 6385.7143 | 2.6979 | 14700 | 2.1667 | 6784.6154 | 2.5084 | 14500 | 1.9667 | 7372.8814 | 2.2859 | 14233.3333 | 1.9167 | 7426.087 | 2.0483 | 14000 | 1.8167 | 7706.422 | 1.8057
|  | 10027.8261 | 48.4026 | nom | 14000 | 2.8833 | 4855.4913 | 3377.7688 | 14000 | 2.6 | 5384.6154 | 3716.8611 | 14000 | 2.3167 | 6043.1655 | 3997.7492 | 14000 | 2.0333 | 6885.2459 | 4386.8803 | 14000 | 1.95 | 7179.4872 | 4895.6293 | 14000 | 1.8167 | 7706.422 | 5553.439
|  |  | 100 | mid | 11200 | 2.9833 | 3754.1899 | 1 | 11200 | 2.8 | 4000 | 1 | 11200 | 2.6167 | 4280.2548 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.1667 | 5169.2308 | 1 | 11200 | 1.9333 | 5793.1034 | 1
|  |  | 4720.7215 | min | 5833.3333 | 2.9167 | 2000 | 0.78158 | 5266.6667 | 2.2833 | 2306.5693 | 0.80244 | 5066.6667 | 2.05 | 2471.5447 | 0.80888 | 4866.6667 | 1.7833 | 2728.972 | 0.81492 | 4266.6667 | 1.4667 | 2909.0909 | 0.83094 | 3700 | 1.1167 | 3313.4328 | 0.84371
| -8 |  | 2.1832 | max | 15600 | 2.6 | 6000 | 3.1601 | 15400 | 2.4167 | 6372.4138 | 2.7557 | 15200 | 2.2333 | 6805.9701 | 2.5412 | 15000 | 2.0333 | 7377.0492 | 2.31 | 14466.6667 | 1.9833 | 7294.1176 | 2.079 | 14000 | 1.8833 | 7433.6283 | 1.8473
|  | 9704.3478 | 47.7449 | nom | 14000 | 2.9667 | 4719.1011 | 3070.8553 | 14000 | 2.7 | 5185.1852 | 3521.4916 | 14000 | 2.4333 | 5753.4247 | 3818.7355 | 14000 | 2.1667 | 6461.5385 | 4200.993 | 14000 | 2.05 | 6829.2683 | 4667.8733 | 14000 | 1.8833 | 7433.6283 | 5253.2966
|  |  | 100 | mid | 11200 | 3.1167 | 3593.5829 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.6833 | 4173.913 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.2333 | 5014.9254 | 1 | 11200 | 2.0167 | 5553.719 | 1
|  |  | 4445.071 | min | 5466.6667 | 3.2833 | 1664.9746 | 0.73913 | 4633.3333 | 2.2667 | 2044.1176 | 0.77224 | 4533.3333 | 2.05 | 2211.3821 | 0.77565 | 4433.3333 | 1.8167 | 2440.367 | 0.77897 | 3933.3333 | 1.4833 | 2651.6854 | 0.79418 | 3400 | 1.1333 | 3000 | 0.80825
| -7 |  | 2.2411 | max | 16100 | 2.7 | 5962.963 | 3.3693 | 15900 | 2.5 | 6360 | 2.8105 | 15700 | 2.3 | 6826.087 | 2.5731 | 15500 | 2.1 | 7380.9524 | 2.3358 | 14700 | 2.05 | 7170.7317 | 2.1085 | 14000 | 1.95 | 7179.4872 | 1.8866
|  | 9380.8696 | 47.0822 | nom | 14000 | 3.05 | 4590.1639 | 2784.2297 | 14000 | 2.8 | 5000 | 3337.7852 | 14000 | 2.55 | 5490.1961 | 3645.6894 | 14000 | 2.3 | 6086.9565 | 4016.1736 | 14000 | 2.15 | 6511.6279 | 4449.046 | 14000 | 1.95 | 7179.4872 | 4972.2489
|  |  | 100 | mid | 11200 | 3.25 | 3446.1538 | 1 | 11200 | 3 | 3733.3333 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1 | 11200 | 2.1 | 5333.3333 | 1
|  |  | 4185.7753 | min | 5100 | 3.65 | 1397.2603 | 0.70178 | 4000 | 2.25 | 1777.7778 | 0.74734 | 4000 | 2.05 | 1951.2195 | 0.74734 | 4000 | 1.85 | 2162.1622 | 0.74734 | 3600 | 1.5 | 2400 | 0.76064 | 3100 | 1.15 | 2695.6522 | 0.77542
| -6 |  | 2.2932 | max | 16144.4444 | 2.7611 | 5847.0825 | 3.4421 | 15944.4444 | 2.5556 | 6239.1304 | 2.851 | 15733.3333 | 2.35 | 6695.0355 | 2.6056 | 15533.3333 | 2.1444 | 7243.5233 | 2.3587 | 14744.4444 | 2.0944 | 7039.7878 | 2.1273 | 14033.3333 | 1.9944 | 7036.2117 | 1.8969
|  | 9057.3913 | 46.4142 | nom | 14000 | 3.0889 | 4532.3741 | 2631.3236 | 14000 | 2.8389 | 4931.5068 | 3176.8752 | 14000 | 2.5889 | 5407.7253 | 3476.1419 | 14000 | 2.3389 | 5985.7482 | 3839.9808 | 14000 | 2.1944 | 6379.7468 | 4257.7553 | 14000 | 2 | 7000 | 4774.8647
|  |  | 100 | mid | 11200 | 3.2944 | 3399.6627 | 1 | 11200 | 3.0444 | 3678.8321 | 1 | 11200 | 2.7944 | 4007.9523 | 1 | 11200 | 2.5444 | 4401.7467 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.15 | 5209.3023 | 1
|  |  | 3949.5954 | min | 5155.5556 | 3.7111 | 1389.2216 | 0.64552 | 4122.2222 | 2.4056 | 1713.6259 | 0.69728 | 4077.7778 | 2.1667 | 1882.0513 | 0.69917 | 4022.2222 | 1.9222 | 2092.4855 | 0.70149 | 3611.1111 | 1.5611 | 2313.1673 | 0.71767 | 3111.1111 | 1.1944 | 2604.6512 | 0.73512
| -5 |  | 2.3489 | max | 16188.8889 | 2.8222 | 5736.2205 | 3.5173 | 15988.8889 | 2.6111 | 6123.4043 | 2.9018 | 15766.6667 | 2.4 | 6569.4444 | 2.6444 | 15566.6667 | 2.1889 | 7111.6751 | 2.384 | 14788.8889 | 2.1389 | 6914.2857 | 2.1469 | 14066.6667 | 2.0389 | 6899.1826 | 1.9066
|  | 8733.913 | 45.7407 | nom | 14000 | 3.1278 | 4476.0213 | 2483.1119 | 14000 | 2.8778 | 4864.8649 | 3009.8616 | 14000 | 2.6278 | 5327.6956 | 3302.7926 | 14000 | 2.3778 | 5887.8505 | 3663.5236 | 14000 | 2.2389 | 6253.1017 | 4068.1839 | 14000 | 2.05 | 6829.2683 | 4580.9324
|  |  | 100 | mid | 11200 | 3.3389 | 3354.4093 | 1 | 11200 | 3.0889 | 3625.8993 | 1 | 11200 | 2.8389 | 3945.2055 | 1 | 11200 | 2.5889 | 4326.1803 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.2 | 5090.9091 | 1
|  |  | 3718.3159 | min | 5211.1111 | 3.7722 | 1381.4433 | 0.58822 | 4244.4444 | 2.5611 | 1657.2668 | 0.64545 | 4155.5556 | 2.2833 | 1819.9513 | 0.64992 | 4044.4444 | 1.9944 | 2027.8552 | 0.65536 | 3622.2222 | 1.6222 | 2232.8767 | 0.67456 | 3122.2222 | 1.2389 | 2520.1794 | 0.69471
| -4 |  | 2.4087 | max | 16233.3333 | 2.8833 | 5630.0578 | 3.5949 | 16033.3333 | 2.6667 | 6012.5 | 2.9632 | 15800 | 2.45 | 6448.9796 | 2.6898 | 15600 | 2.2333 | 6985.0746 | 2.4117 | 14833.3333 | 2.1833 | 6793.8931 | 2.1674 | 14100 | 2.0833 | 6768 | 1.9157
|  | 8410.4348 | 45.0614 | nom | 14000 | 3.1667 | 4421.0526 | 2339.5453 | 14000 | 2.9167 | 4800 | 2838.2584 | 14000 | 2.6667 | 5250 | 3126.7894 | 14000 | 2.4167 | 5793.1034 | 3487.3002 | 14000 | 2.2833 | 6131.3869 | 3880.5031 | 14000 | 2.1 | 6666.6667 | 4390.2368
|  |  | 100 | mid | 11200 | 3.3833 | 3310.3448 | 1 | 11200 | 3.1333 | 3574.4681 | 1 | 11200 | 2.8833 | 3884.3931 | 1 | 11200 | 2.6333 | 4253.1646 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.25 | 4977.7778 | 1
|  |  | 3491.6456 | min | 5266.6667 | 3.8333 | 1373.913 | 0.52985 | 4366.6667 | 2.7167 | 1607.362 | 0.59177 | 4233.3333 | 2.4 | 1763.8889 | 0.59958 | 4066.6667 | 2.0667 | 1967.7419 | 0.60894 | 3633.3333 | 1.6833 | 2158.4158 | 0.63133 | 3133.3333 | 1.2833 | 2441.5584 | 0.65419
| -3 |  | 2.4793 | max | 16277.7778 | 2.9444 | 5528.3019 | 3.6749 | 16077.7778 | 2.7222 | 5906.1224 | 3.036 | 15833.3333 | 2.5 | 6333.3333 | 2.742 | 15633.3333 | 2.2778 | 6863.4146 | 2.4419 | 14877.7778 | 2.2278 | 6678.3042 | 2.1887 | 14133.3333 | 2.1278 | 6642.2977 | 1.9243
|  | 8086.9565 | 44.376 | nom | 14000 | 3.2056 | 4367.4177 | 2200.5694 | 14000 | 2.9556 | 4736.8421 | 2663.6515 | 14000 | 2.7056 | 5174.538 | 2949.2919 | 14000 | 2.4556 | 5701.3575 | 3311.7918 | 14000 | 2.3278 | 6014.3198 | 3694.8749 | 14000 | 2.15 | 6511.6279 | 4202.5711
|  |  | 100 | mid | 11200 | 3.4278 | 3267.423 | 1 | 11200 | 3.1778 | 3524.4755 | 1 | 11200 | 2.9278 | 3825.4269 | 1 | 11200 | 2.6778 | 4182.5726 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1
|  |  | 3261.7622 | min | 5322.2222 | 3.8944 | 1366.6191 | 0.47037 | 4488.8889 | 2.8722 | 1562.8627 | 0.53614 | 4311.1111 | 2.5167 | 1713.0243 | 0.54811 | 4088.8889 | 2.1389 | 1911.6883 | 0.56223 | 3644.4444 | 1.7444 | 2089.172 | 0.58798 | 3144.4444 | 1.3278 | 2368.2008 | 0.61355
| -2 |  | 2.5604 | max | 16322.2222 | 3.0056 | 5430.6839 | 3.7575 | 16122.2222 | 2.7778 | 5804 | 3.1208 | 15866.6667 | 2.55 | 6222.2222 | 2.8012 | 15666.6667 | 2.3222 | 6746.4115 | 2.4744 | 14922.2222 | 2.2722 | 6567.2372 | 2.2109 | 14166.6667 | 2.1722 | 6521.7391 | 1.9323
|  | 7763.4783 | 43.6843 | nom | 14000 | 3.2444 | 4315.0685 | 2066.1253 | 14000 | 2.9944 | 4675.3247 | 2487.6507 | 14000 | 2.7444 | 5101.2146 | 2771.4464 | 14000 | 2.4944 | 5612.4722 | 3137.4587 | 14000 | 2.3722 | 5901.6393 | 3511.4515 | 14000 | 2.2 | 6363.6364 | 4017.7371
|  |  | 100 | mid | 11200 | 3.4722 | 3225.6 | 1 | 11200 | 3.2222 | 3475.8621 | 1 | 11200 | 2.9722 | 3768.2243 | 1 | 11200 | 2.7222 | 4114.2857 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1
|  |  | 3032.0899 | min | 5377.7778 | 3.9556 | 1359.5506 | 0.40976 | 4611.1111 | 3.0278 | 1522.9358 | 0.47844 | 4388.8889 | 2.6333 | 1666.6667 | 0.49545 | 4111.1111 | 2.2111 | 1859.2965 | 0.51522 | 3655.5556 | 1.8056 | 2024.6154 | 0.5445 | 3155.5556 | 1.3722 | 2299.5951 | 0.57281
| -1 |  | 2.6538 | max | 16366.6667 | 3.0667 | 5336.9565 | 3.8427 | 16166.6667 | 2.8333 | 5705.8824 | 3.2182 | 15900 | 2.6 | 6115.3846 | 2.8678 | 15700 | 2.3667 | 6633.8028 | 2.5095 | 14966.6667 | 2.3167 | 6460.4317 | 2.234 | 14200 | 2.2167 | 6406.015 | 1.9398
|  | 7440 | 42.9859 | nom | 14000 | 3.2833 | 4263.9594 | 1936.1496 | 14000 | 3.0333 | 4615.3846 | 2311.842 | 14000 | 2.7833 | 5029.9401 | 2594.3632 | 14000 | 2.5333 | 5526.3158 | 2964.7377 | 14000 | 2.4167 | 5793.1034 | 3330.3755 | 14000 | 2.25 | 6222.2222 | 3835.5438
|  |  | 100 | mid | 11200 | 3.5167 | 3184.8341 | 1 | 11200 | 3.2667 | 3428.5714 | 1 | 11200 | 3.0167 | 3712.7072 | 1 | 11200 | 2.7667 | 4048.1928 | 1 | 11200 | 2.6 | 4307.6923 | 1 | 11200 | 2.4 | 4666.6667 | 1
|  |  | 2803.5163 | min | 5433.3333 | 4.0167 | 1352.6971 | 0.34798 | 4733.3333 | 3.1833 | 1486.911 | 0.41856 | 4466.6667 | 2.75 | 1624.2424 | 0.44158 | 4133.3333 | 2.2833 | 1810.219 | 0.46792 | 3666.6667 | 1.8667 | 1964.2857 | 0.50088 | 3166.6667 | 1.4167 | 2235.2941 | 0.53195
| 0 |  | 2.7618 | max | 16411.1111 | 3.1278 | 5246.8917 | 3.9305 | 16211.1111 | 2.8889 | 5611.5385 | 3.329 | 15933.3333 | 2.65 | 6012.5786 | 2.9418 | 15733.3333 | 2.4111 | 6525.3456 | 2.547 | 15011.1111 | 2.3611 | 6357.6471 | 2.2579 | 14233.3333 | 2.2611 | 6294.8403 | 1.9466
|  | 7116.5217 | 42.2805 | nom | 14000 | 3.3222 | 4214.0468 | 1810.5752 | 14000 | 3.0722 | 4556.962 | 2137.7422 | 14000 | 2.8222 | 4960.6299 | 2419.0956 | 14000 | 2.5722 | 5442.7646 | 2794.0387 | 14000 | 2.4611 | 5688.4876 | 3151.7793 | 14000 | 2.3 | 6086.9565 | 3655.807
|  |  | 100 | mid | 11200 | 3.5611 | 3145.0858 | 1 | 11200 | 3.3111 | 3382.5503 | 1 | 11200 | 3.0611 | 3658.8022 | 1 | 11200 | 2.8111 | 3984.1897 | 1 | 11200 | 2.65 | 4226.4151 | 1 | 11200 | 2.45 | 4571.4286 | 1
|  |  | 2576.8082 | min | 5488.8889 | 4.0778 | 1346.049 | 0.28499 | 4855.5556 | 3.3389 | 1454.2429 | 0.35637 | 4544.4444 | 2.8667 | 1585.2713 | 0.38646 | 4155.5556 | 2.3556 | 1764.1509 | 0.42033 | 3677.7778 | 1.9278 | 1907.781 | 0.45714 | 3177.7778 | 1.4611 | 2174.9049 | 0.49098
| 1 |  | 2.8868 | max | 16455.5556 | 3.1889 | 5160.2787 | 4.0211 | 16255.5556 | 2.9444 | 5520.7547 | 3.4539 | 15966.6667 | 2.7 | 5913.5802 | 3.0237 | 15766.6667 | 2.4556 | 6420.8145 | 2.5871 | 15055.5556 | 2.4056 | 6258.6605 | 2.2828 | 14266.6667 | 2.3056 | 6187.9518 | 1.953
|  | 6793.0435 | 41.5676 | nom | 14000 | 3.3611 | 4165.2893 | 1689.3316 | 14000 | 3.1111 | 4500 | 1966.7605 | 14000 | 2.8611 | 4893.2039 | 2246.6223 | 14000 | 2.6111 | 5361.7021 | 2625.743 | 14000 | 2.5056 | 5587.5831 | 2975.7853 | 14000 | 2.35 | 5957.4468 | 3478.3488
|  |  | 100 | mid | 11200 | 3.6056 | 3106.3174 | 1 | 11200 | 3.3556 | 3337.7483 | 1 | 11200 | 3.1056 | 3606.4401 | 1 | 11200 | 2.8556 | 3922.179 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.5 | 4480 | 1
|  |  | 2353.1411 | min | 5544.4444 | 4.1389 | 1339.5973 | 0.22077 | 4977.7778 | 3.4944 | 1424.4833 | 0.29174 | 4622.2222 | 2.9833 | 1549.3482 | 0.33002 | 4177.7778 | 2.4278 | 1720.8238 | 0.37243 | 3688.8889 | 1.9889 | 1854.7486 | 0.41328 | 3188.8889 | 1.5056 | 2118.0812 | 0.44989
14kW-Maximum heating CAP | 2 |  | 3.0317 | max | 16500 | 3.25 | 5076.9231 | 4.1146 | 16300 | 3 | 5433.3333 | 3.5939 | 16000 | 2.75 | 5818.1818 | 3.1136 | 15800 | 2.5 | 6320 | 2.6297 | 15100 | 2.45 | 6163.2653 | 2.3085 | 14300 | 2.35 | 6085.1064 | 1.9587
|  | 6469.5652 | 40.8468 | nom | 14000 | 3.4 | 4117.6471 | 1572.3451 | 14000 | 3.15 | 4444.4444 | 1800.1666 | 14000 | 2.9 | 4827.5862 | 2077.8328 | 14000 | 2.65 | 5283.0189 | 2460.2012 | 14000 | 2.55 | 5490.1961 | 2802.5062 | 14000 | 2.4 | 5833.3333 | 3302.9967
|  |  | 100 | mid | 11200 | 3.65 | 3068.4932 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 3.15 | 3555.5556 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.55 | 4392.1569 | 1
|  |  | 2134.003 | min | 5600 | 4.2 | 1333.3333 | 0.15528 | 5100 | 3.65 | 1397.2603 | 0.22452 | 4700 | 3.1 | 1516.129 | 0.27224 | 4200 | 2.5 | 1680 | 0.32422 | 3700 | 2.05 | 1804.878 | 0.36928 | 3200 | 1.55 | 2064.5161 | 0.4087
| 3 |  | 3.2187 | max | 16560 | 3.54 | 4677.9661 | 4.5865 | 16360 | 3.25 | 5033.8462 | 3.7846 | 16080 | 2.96 | 5432.4324 | 3.2316 | 15860 | 2.66 | 5962.406 | 2.6829 | 15160 | 2.54 | 5968.5039 | 2.3287 | 14360 | 2.38 | 6033.6134 | 1.9482
|  | 6146.087 | 40.1176 | nom | 14000 | 3.7 | 3783.7838 | 1340.0261 | 14000 | 3.41 | 4105.5718 | 1623.9644 | 14000 | 3.12 | 4487.1795 | 1901.8749 | 14000 | 2.82 | 4964.539 | 2290.8549 | 14000 | 2.67 | 5243.4457 | 2639.3189 | 14000 | 2.47 | 5668.0162 | 3154.7526
|  |  | 100 | mid | 11200 | 3.97 | 2821.1587 | 1 | 11200 | 3.68 | 3043.4783 | 1 | 11200 | 3.39 | 3303.8348 | 1 | 11200 | 3.09 | 3624.5955 | 1 | 11200 | 2.88 | 3888.8889 | 1 | 11200 | 2.62 | 4274.8092 | 1
|  |  | 1909.5028 | min | 5380 | 4.68 | 1149.5726 | 0.13163 | 4920 | 3.81 | 1291.3386 | 0.19524 | 4500 | 3.18 | 1415.0943 | 0.24568 | 4000 | 2.51 | 1593.6255 | 0.29807 | 3500 | 2.04 | 1715.6863 | 0.34365 | 3000 | 1.53 | 1960.7843 | 0.38367
| 4 |  | 3.4194 | max | 16620 | 3.83 | 4339.4256 | 5.0646 | 16420 | 3.5 | 4691.4286 | 3.9683 | 16160 | 3.17 | 5097.7918 | 3.3416 | 15920 | 2.82 | 5645.3901 | 2.7277 | 15220 | 2.63 | 5787.0722 | 2.3429 | 14420 | 2.41 | 5983.4025 | 1.9346
|  | 5822.6087 | 39.3796 | nom | 14000 | 4 | 3500 | 1149.6776 | 14000 | 3.67 | 3814.7139 | 1467.2714 | 14000 | 3.34 | 4191.6168 | 1742.4367 | 14000 | 2.99 | 4682.2742 | 2134.6007 | 14000 | 2.79 | 5017.9211 | 2485.1812 | 14000 | 2.54 | 5511.811 | 3009.7152
|  |  | 100 | mid | 11200 | 4.29 | 2610.7226 | 1 | 11200 | 3.96 | 2828.2828 | 1 | 11200 | 3.63 | 3085.3994 | 1 | 11200 | 3.28 | 3414.6341 | 1 | 11200 | 3.01 | 3720.9302 | 1 | 11200 | 2.69 | 4163.5688 | 1
|  |  | 1702.8115 | min | 5160 | 5.16 | 1000 | 0.1097 | 4740 | 3.97 | 1193.9547 | 0.16759 | 4300 | 3.26 | 1319.0184 | 0.22067 | 3800 | 2.52 | 1507.9365 | 0.27333 | 3300 | 2.03 | 1625.6158 | 0.31932 | 2800 | 1.51 | 1854.3046 | 0.35983
| 5 |  | 3.6363 | max | 16680 | 4.12 | 4048.5437 | 5.548 | 16480 | 3.75 | 4394.6667 | 4.1456 | 16240 | 3.38 | 4804.7337 | 3.4444 | 15980 | 2.98 | 5362.4161 | 2.7649 | 15280 | 2.72 | 5617.6471 | 2.3517 | 14480 | 2.44 | 5934.4262 | 1.9181
|  | 5499.1304 | 38.632 | nom | 14000 | 4.3 | 3255.814 | 991.1911 | 14000 | 3.93 | 3562.341 | 1326.5116 | 14000 | 3.56 | 3932.5843 | 1596.5228 | 14000 | 3.16 | 4430.3797 | 1988.913 | 14000 | 2.91 | 4810.9966 | 2338.3325 | 14000 | 2.61 | 5363.9847 | 2866.9266
|  |  | 100 | mid | 11200 | 4.61 | 2429.5011 | 1 | 11200 | 4.24 | 2641.5094 | 1 | 11200 | 3.87 | 2894.0568 | 1 | 11200 | 3.47 | 3227.6657 | 1 | 11200 | 3.14 | 3566.879 | 1 | 11200 | 2.76 | 4057.971 | 1
|  |  | 1512.2998 | min | 4940 | 5.64 | 875.8865 | 0.089318 | 4560 | 4.13 | 1104.1162 | 0.14144 | 4100 | 3.34 | 1227.5449 | 0.19706 | 3600 | 2.53 | 1422.9249 | 0.24989 | 3100 | 2.02 | 1534.6535 | 0.29619 | 2600 | 1.49 | 1744.9664 | 0.33711
| 6 |  | 3.8706 | max | 16740 | 4.41 | 3795.9184 | 6.0363 | 16540 | 4 | 4135 | 4.3168 | 16320 | 3.59 | 4545.961 | 3.5406 | 16040 | 3.14 | 5108.2803 | 2.795 | 15340 | 2.81 | 5459.0747 | 2.3555 | 14540 | 2.47 | 5886.6397 | 1.899
|  | 5175.6522 | 37.8742 | nom | 14000 | 4.6 | 3043.4783 | 857.418 | 14000 | 4.19 | 3341.2888 | 1198.9466 | 14000 | 3.78 | 3703.7037 | 1461.8111 | 14000 | 3.33 | 4204.2042 | 1851.7768 | 14000 | 3.03 | 4620.462 | 2197.2995 | 14000 | 2.68 | 5223.8806 | 2725.513
|  |  | 100 | mid | 11200 | 4.93 | 2271.8053 | 1 | 11200 | 4.52 | 2477.8761 | 1 | 11200 | 4.11 | 2725.0608 | 1 | 11200 | 3.66 | 3060.1093 | 1 | 11200 | 3.27 | 3425.0765 | 1 | 11200 | 2.83 | 3957.5972 | 1
|  |  | 1337.1657 | min | 4720 | 6.12 | 771.2418 | 0.070317 | 4380 | 4.29 | 1020.979 | 0.11666 | 3900 | 3.42 | 1140.3509 | 0.17475 | 3400 | 2.54 | 1338.5827 | 0.22765 | 2900 | 2.01 | 1442.7861 | 0.27417 | 2400 | 1.47 | 1632.6531 | 0.31542
| 7 |  | 4.1238 | max | 16800 | 4.7 | 3574.4681 | 6.529 | 16600 | 4.25 | 3905.8824 | 4.4826 | 16400 | 3.8 | 4315.7895 | 3.6306 | 16100 | 3.3 | 4878.7879 | 2.8185 | 15400 | 2.9 | 5310.3448 | 2.3545 | 14600 | 2.5 | 5840 | 1.8773
|  | 4852.1739 | 37.1053 | nom | 14000 | 4.9 | 2857.1429 | 743.1681 | 14000 | 4.45 | 3146.0674 | 1082.4442 | 14000 | 4 | 3500 | 1336.4736 | 14000 | 3.5 | 4000 | 1721.558 | 14000 | 3.15 | 4444.4444 | 2060.8299 | 14000 | 2.75 | 5090.9091 | 2584.6629
|  |  | 100 | mid | 11200 | 5.25 | 2133.3333 | 1 | 11200 | 4.8 | 2333.3333 | 1 | 11200 | 4.35 | 2574.7126 | 1 | 11200 | 3.85 | 2909.0909 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 2.9 | 3862.069 | 1
|  |  | 1176.6134 | min | 4500 | 6.6 | 681.8182 | 0.052563 | 4200 | 4.45 | 943.8202 | 0.093168 | 3700 | 3.5 | 1057.1429 | 0.15362 | 3200 | 2.55 | 1254.902 | 0.20652 | 2700 | 2 | 1350 | 0.2532 | 2200 | 1.45 | 1517.2414 | 0.29469
| 8 |  | 4.3377 | max | 16860 | 4.81 | 3505.1975 | 6.31 | 16640 | 4.38 | 3799.0868 | 4.54 | 16440 | 3.93 | 4183.2061 | 3.7762 | 16160 | 3.48 | 4643.6782 | 3.0452 | 15440 | 3.06 | 5045.7516 | 2.5459 | 14640 | 2.64 | 5545.4545 | 2.0403
|  | 4528.6957 | 36.3246 | nom | 14000 | 5.02 | 2788.8446 | 717.7014 | 14000 | 4.59 | 3050.1089 | 997.5101 | 14000 | 4.16 | 3365.3846 | 1199.2795 | 14000 | 3.69 | 3794.0379 | 1487.1659 | 14000 | 3.32 | 4216.8675 | 1778.7857 | 14000 | 2.9 | 4827.5862 | 2219.5856
|  |  | 100 | mid | 11200 | 5.37 | 2085.6611 | 0 | 11200 | 4.95 | 2262.6263 | 0 | 11200 | 4.53 | 2472.4062 | 1 | 11200 | 4.06 | 2758.6207 | 1 | 11200 | 3.58 | 3128.4916 | 1 | 11200 | 3.06 | 3660.1307 | 1
|  |  | 1044.043 | min | 4920 | 6.31 | 779.7147 | 0 | 4600 | 4.54 | 1013.2159 | 0 | 4120 | 3.73 | 1104.5576 | 0.057725 | 3640 | 2.91 | 1250.8591 | 0.11755 | 3200 | 2.34 | 1367.5214 | 0.16609 | 2760 | 1.77 | 1559.322 | 0.20956
| 9 |  | 4.5589 | max | 16920 | 4.92 | 3439.0244 | 6.02 | 16680 | 4.51 | 3698.4479 | 4.63 | 16480 | 4.06 | 4059.1133 | 3.96 | 16220 | 3.66 | 4431.694 | 3.2876 | 15480 | 3.22 | 4807.4534 | 2.7528 | 14680 | 2.78 | 5280.5755 | 2.2169
|  | 4205.2174 | 35.5308 | nom | 14000 | 5.14 | 2723.7354 | 698.5411 | 14000 | 4.73 | 2959.8309 | 908.2543 | 14000 | 4.32 | 3240.7407 | 1061.9236 | 14000 | 3.88 | 3608.2474 | 1279.1198 | 14000 | 3.49 | 4011.4613 | 1527.6416 | 14000 | 3.05 | 4590.1639 | 1896.8557
|  |  | 84.9339 | mid | 11200 | 5.49 | 2040.0729 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.71 | 2377.9193 | 0 | 11200 | 4.27 | 2622.9508 | 1 | 11200 | 3.76 | 2978.7234 | 1 | 11200 | 3.22 | 3478.2609 | 1
|  |  | 922.4255 | min | 5340 | 6.02 | 887.0432 | 0 | 5000 | 4.63 | 1079.9136 | 0 | 4540 | 3.96 | 1146.4646 | 0 | 4080 | 3.27 | 1247.7064 | 0.017587 | 3700 | 2.68 | 1380.597 | 0.067362 | 3320 | 2.09 | 1588.5167 | 0.11234
| 10 |  | 4.748 | max | 16980 | 5.03 | 3375.7455 | 5.73 | 16720 | 4.64 | 3603.4483 | 4.72 | 16520 | 4.19 | 3942.7208 | 4.19 | 16280 | 3.84 | 4239.5833 | 3.63 | 15520 | 3.38 | 4591.716 | 3.02 | 14720 | 2.92 | 5041.0959 | 2.4102
|  | 3881.7391 | 34.7228 | nom | 14000 | 5.26 | 2661.597 | 677.4414 | 14000 | 4.87 | 2874.7433 | 822.4024 | 14000 | 4.48 | 3125 | 926.4294 | 14000 | 4.07 | 3439.8034 | 1069.3496 | 14000 | 3.66 | 3825.1366 | 1285.3441 | 14000 | 3.2 | 4375 | 1610.5261
|  |  | 71.7515 | mid | 11200 | 5.61 | 1996.4349 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.89 | 2290.3885 | 0 | 11200 | 4.48 | 2500 | 0 | 11200 | 3.94 | 2842.6396 | 0 | 11200 | 3.38 | 3313.6095 | 1
|  |  | 817.5537 | min | 5760 | 5.73 | 1005.2356 | 0 | 5400 | 4.72 | 1144.0678 | 0 | 4960 | 4.19 | 1183.7709 | 0 | 4520 | 3.63 | 1245.1791 | 0 | 4200 | 3.02 | 1390.7285 | 0 | 3880 | 2.41 | 1609.9585 | 0.00023759
| 11 |  | 4.8794 | max | 17040 | 5.14 | 3315.1751 | 5.44 | 16760 | 4.77 | 3513.6268 | 4.81 | 16560 | 4.32 | 3833.3333 | 4.42 | 16340 | 4.02 | 4064.6766 | 3.99 | 15560 | 3.54 | 4395.4802 | 3.36 | 14760 | 3.06 | 4823.5294 | 2.73
|  | 3558.2609 | 33.8992 | nom | 14000 | 5.38 | 2602.2305 | 654.0921 | 14000 | 5.01 | 2794.4112 | 739.7632 | 14000 | 4.64 | 3017.2414 | 805.0364 | 14000 | 4.26 | 3286.385 | 891.7947 | 14000 | 3.83 | 3655.3525 | 1059.0062 | 14000 | 3.35 | 4179.1045 | 1303.3923
|  |  | 60.91 | mid | 11200 | 5.73 | 1954.6248 | 0 | 11200 | 5.4 | 2074.0741 | 0 | 11200 | 5.07 | 2209.073 | 0 | 11200 | 4.69 | 2388.0597 | 0 | 11200 | 4.12 | 2718.4466 | 0 | 11200 | 3.54 | 3163.8418 | 0
|  |  | 729.2485 | min | 6180 | 5.44 | 1136.0294 | 0 | 5800 | 4.81 | 1205.8212 | 0 | 5380 | 4.42 | 1217.1946 | 0 | 4960 | 3.99 | 1243.1078 | 0 | 4700 | 3.36 | 1398.8095 | 0 | 4440 | 2.73 | 1626.3736 | 0
| 12 |  | 4.9486 | max | 17100 | 5.25 | 3257.1429 | 5.15 | 16800 | 4.9 | 3428.5714 | 4.9 | 16600 | 4.45 | 3730.3371 | 4.65 | 16400 | 4.2 | 3904.7619 | 4.35 | 15600 | 3.7 | 4216.2162 | 3.7 | 14800 | 3.2 | 4625 | 3.05
|  | 3234.7826 | 33.058 | nom | 14000 | 5.5 | 2545.4545 | 628.1131 | 14000 | 5.15 | 2718.4466 | 660.1597 | 14000 | 4.8 | 2916.6667 | 695.6522 | 14000 | 4.45 | 3146.0674 | 743.6282 | 14000 | 4 | 3500 | 874.2656 | 14000 | 3.5 | 4000 | 1060.5845
|  |  | 51.5283 | mid | 11200 | 5.85 | 1914.5299 | 0 | 11200 | 5.55 | 2018.018 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.9 | 2285.7143 | 0 | 11200 | 4.3 | 2604.6512 | 0 | 11200 | 3.7 | 3027.027 | 0
|  |  | 653.6828 | min | 6600 | 5.15 | 1281.5534 | 0 | 6200 | 4.9 | 1265.3061 | 0 | 5800 | 4.65 | 1247.3118 | 0 | 5400 | 4.35 | 1241.3793 | 0 | 5200 | 3.7 | 1405.4054 | 0 | 5000 | 3.05 | 1639.3443 | 0
| 13 |  | 5.0181 | max | 17566.6667 | 5.2833 | 3324.9211 | 5.15 | 17266.6667 | 4.9333 | 3500 | 4.9667 | 17033.3333 | 4.55 | 3743.5897 | 4.7833 | 16833.3333 | 4.3 | 3914.7287 | 4.55 | 16033.3333 | 3.8 | 4219.2982 | 3.9167 | 15200 | 3.3 | 4606.0606 | 3.2667
|  | 2911.3043 | 32.1971 | nom | 14000 | 5.5 | 2545.4545 | 565.3018 | 14000 | 5.1833 | 2700.9646 | 586.1687 | 14000 | 4.8667 | 2876.7123 | 608.6351 | 14000 | 4.55 | 3076.9231 | 639.8471 | 14000 | 4.1 | 3414.6341 | 743.3117 | 14000 | 3.6167 | 3870.9677 | 891.2156
|  |  | 45.5737 | mid | 11200 | 5.9 | 1898.3051 | 0 | 11200 | 5.5833 | 2005.9701 | 0 | 11200 | 5.3167 | 2106.5831 | 0 | 11200 | 5.0167 | 2232.5581 | 0 | 11200 | 4.4167 | 2535.8491 | 0 | 11200 | 3.8167 | 2934.4978 | 0
|  |  | 580.1661 | min | 6700 | 5.15 | 1300.9709 | 0 | 6266.6667 | 4.9667 | 1261.745 | 0 | 5833.3333 | 4.7833 | 1219.5122 | 0 | 5400 | 4.55 | 1186.8132 | 0 | 5233.3333 | 3.9167 | 1336.1702 | 0 | 5066.6667 | 3.2667 | 1551.0204 | 0
| 14 |  | 5.0763 | max | 18033.3333 | 5.3167 | 3391.8495 | 5.15 | 17733.3333 | 4.9667 | 3570.4698 | 5.0333 | 17466.6667 | 4.65 | 3756.2724 | 4.9167 | 17266.6667 | 4.4 | 3924.2424 | 4.75 | 16466.6667 | 3.9 | 4222.2222 | 4.1333 | 15600 | 3.4 | 4588.2353 | 3.4833
|  | 2587.8261 | 31.3139 | nom | 14000 | 5.5 | 2545.4545 | 502.4905 | 14000 | 5.2167 | 2683.7061 | 514.1376 | 14000 | 4.9333 | 2837.8378 | 526.3375 | 14000 | 4.65 | 3010.7527 | 544.8055 | 14000 | 4.2 | 3333.3333 | 626.087 | 14000 | 3.7333 | 3750 | 742.9166
|  |  | 39.7799 | mid | 11200 | 5.95 | 1882.3529 | 0 | 11200 | 5.6167 | 1994.0653 | 0 | 11200 | 5.3833 | 2080.4954 | 0 | 11200 | 5.1333 | 2181.8182 | 0 | 11200 | 4.5333 | 2470.5882 | 0 | 11200 | 3.9333 | 2847.4576 | 0
|  |  | 509.782 | min | 6800 | 5.15 | 1320.3883 | 0 | 6333.3333 | 5.0333 | 1258.2781 | 0 | 5866.6667 | 4.9167 | 1193.2203 | 0 | 5400 | 4.75 | 1136.8421 | 0 | 5266.6667 | 4.1333 | 1274.1935 | 0 | 5133.3333 | 3.4833 | 1473.6842 | 0
| 15 |  | 5.123 | max | 18500 | 5.35 | 3457.9439 | 5.15 | 18200 | 5 | 3640 | 5.1 | 17900 | 4.75 | 3768.4211 | 5.05 | 17700 | 4.5 | 3933.3333 | 4.95 | 16900 | 4 | 4225 | 4.35 | 16000 | 3.5 | 4571.4286 | 3.7
|  | 2264.3478 | 30.4047 | nom | 14000 | 5.5 | 2545.4545 | 439.6792 | 14000 | 5.25 | 2666.6667 | 443.9898 | 14000 | 5 | 2800 | 448.3857 | 14000 | 4.75 | 2947.3684 | 457.444 | 14000 | 4.3 | 3255.814 | 520.5397 | 14000 | 3.85 | 3636.3636 | 611.9859
|  |  | 34.1543 | mid | 11200 | 6 | 1866.6667 | 0 | 11200 | 5.65 | 1982.3009 | 0 | 11200 | 5.45 | 2055.0459 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.65 | 2408.6022 | 0 | 11200 | 4.05 | 2765.4321 | 0
|  |  | 441.9985 | min | 6900 | 5.15 | 1339.8058 | 0 | 6400 | 5.1 | 1254.902 | 0 | 5900 | 5.05 | 1168.3168 | 0 | 5400 | 4.95 | 1090.9091 | 0 | 5300 | 4.35 | 1218.3908 | 0 | 5200 | 3.7 | 1405.4054 | 0
| 16 |  | 6.3664 | max | 19020 | 5.73 | 3319.3717 | 6.92 | 18720 | 5.3 | 3532.0755 | 5.68 | 18420 | 4.95 | 3721.2121 | 5.37 | 18200 | 4.59 | 3965.1416 | 5.02 | 17380 | 4.08 | 4259.8039 | 4.36 | 16460 | 3.56 | 4623.5955 | 3.65
|  | 1940.8696 | 29.4649 | nom | 14000 | 5.93 | 2360.8769 | 280.4725 | 14000 | 5.57 | 2513.465 | 341.7024 | 14000 | 5.21 | 2687.1401 | 361.4282 | 14000 | 4.85 | 2886.5979 | 386.6274 | 14000 | 4.39 | 3189.0661 | 445.1536 | 14000 | 3.92 | 3571.4286 | 531.7451
|  |  | 28.7629 | mid | 11200 | 6.42 | 1744.5483 | 0 | 11200 | 5.99 | 1869.783 | 0 | 11200 | 5.68 | 1971.831 | 0 | 11200 | 5.36 | 2089.5522 | 0 | 11200 | 4.74 | 2362.8692 | 0 | 11200 | 4.12 | 2718.4466 | 0
|  |  | 304.8635 | min | 6980 | 6.92 | 1008.6705 | 0 | 6460 | 5.68 | 1137.3239 | 0 | 6000 | 5.37 | 1117.3184 | 0 | 5520 | 5.02 | 1099.6016 | 0 | 5360 | 4.36 | 1229.3578 | 0 | 5180 | 3.65 | 1419.1781 | 0
| 17 |  | 7.8424 | max | 19540 | 6.11 | 3198.036 | 8.69 | 19240 | 5.6 | 3435.7143 | 6.26 | 18940 | 5.15 | 3677.6699 | 5.69 | 18700 | 4.68 | 3995.7265 | 5.09 | 17860 | 4.16 | 4293.2692 | 4.37 | 16920 | 3.62 | 4674.0331 | 3.6
|  | 1617.3913 | 28.488 | nom | 14000 | 6.36 | 2201.2579 | 186.121 | 14000 | 5.89 | 2376.91 | 258.3692 | 14000 | 5.42 | 2583.0258 | 284.2515 | 14000 | 4.95 | 2828.2828 | 317.7586 | 14000 | 4.48 | 3125 | 370.1124 | 14000 | 3.99 | 3508.7719 | 449.2754
|  |  | 23.5372 | mid | 11200 | 6.84 | 1637.4269 | 0 | 11200 | 6.33 | 1769.3523 | 0 | 11200 | 5.91 | 1895.0931 | 0 | 11200 | 5.47 | 2047.532 | 0 | 11200 | 4.83 | 2318.8406 | 0 | 11200 | 4.19 | 2673.031 | 0
|  |  | 206.2367 | min | 7060 | 8.69 | 812.4281 | 0 | 6520 | 6.26 | 1041.5335 | 0 | 6100 | 5.69 | 1072.0562 | 0 | 5640 | 5.09 | 1108.055 | 0 | 5420 | 4.37 | 1240.2746 | 0 | 5160 | 3.6 | 1433.3333 | 0
| 18 |  | 9.5678 | max | 20060 | 6.49 | 3090.9091 | 10.46 | 19760 | 5.9 | 3349.1525 | 6.84 | 19460 | 5.35 | 3637.3832 | 6.01 | 19200 | 4.77 | 4025.1572 | 5.16 | 18340 | 4.24 | 4325.4717 | 4.38 | 17380 | 3.68 | 4722.8261 | 3.55
|  | 1293.913 | 27.4647 | nom | 14000 | 6.79 | 2061.8557 | 123.7011 | 14000 | 6.21 | 2254.4283 | 189.1686 | 14000 | 5.63 | 2486.6785 | 215.2934 | 14000 | 5.05 | 2772.2772 | 250.7583 | 14000 | 4.57 | 3063.4573 | 295.4139 | 14000 | 4.06 | 3448.2759 | 364.4825
|  |  | 18.4793 | mid | 11200 | 7.26 | 1542.6997 | 0 | 11200 | 6.67 | 1679.1604 | 0 | 11200 | 6.14 | 1824.1042 | 0 | 11200 | 5.58 | 2007.1685 | 0 | 11200 | 4.92 | 2276.4228 | 0 | 11200 | 4.26 | 2629.108 | 0
|  |  | 135.2366 | min | 7140 | 10.46 | 682.6004 | 0 | 6580 | 6.84 | 961.9883 | 0 | 6200 | 6.01 | 1031.614 | 0 | 5760 | 5.16 | 1116.2791 | 0 | 5480 | 4.38 | 1251.1416 | 0 | 5140 | 3.55 | 1447.8873 | 0
| 19 |  | 11.5663 | max | 20580 | 6.87 | 2995.6332 | 12.23 | 20280 | 6.2 | 3270.9677 | 7.42 | 19980 | 5.55 | 3600 | 6.33 | 19700 | 4.86 | 4053.4979 | 5.23 | 18820 | 4.32 | 4356.4815 | 4.39 | 17840 | 3.74 | 4770.0535 | 3.5
|  | 970.4348 | 26.3799 | nom | 14000 | 7.22 | 1939.0582 | 79.3487 | 14000 | 6.53 | 2143.951 | 130.7864 | 14000 | 5.84 | 2397.2603 | 153.3072 | 14000 | 5.15 | 2718.4466 | 185.5516 | 14000 | 4.66 | 3004.2918 | 221.0558 | 14000 | 4.13 | 3389.8305 | 277.2671
|  |  | 13.5916 | mid | 11200 | 7.68 | 1458.3333 | 0 | 11200 | 7.01 | 1597.7175 | 0 | 11200 | 6.37 | 1758.2418 | 0 | 11200 | 5.69 | 1968.3656 | 0 | 11200 | 5.01 | 2235.5289 | 0 | 11200 | 4.33 | 2586.6051 | 0
|  |  | 83.902 | min | 7220 | 12.23 | 590.3516 | 0 | 6640 | 7.42 | 894.8787 | 0 | 6300 | 6.33 | 995.2607 | 0 | 5880 | 5.23 | 1124.283 | 0 | 5540 | 4.39 | 1261.959 | 0 | 5120 | 3.5 | 1462.8571 | 0
| 20 |  | 13.8762 | max | 21100 | 7.25 | 2910.3448 | 14 | 20800 | 6.5 | 3200 | 8 | 20500 | 5.75 | 3565.2174 | 6.65 | 20200 | 4.95 | 4080.8081 | 5.3 | 19300 | 4.4 | 4386.3636 | 4.4 | 18300 | 3.8 | 4815.7895 | 3.45
|  | 646.9565 | 25.2063 | nom | 14000 | 7.65 | 1830.0654 | 46.2112 | 14000 | 6.85 | 2043.7956 | 80.8696 | 14000 | 6.05 | 2314.0496 | 97.2867 | 14000 | 5.25 | 2666.6667 | 122.0673 | 14000 | 4.75 | 2947.3684 | 147.0356 | 14000 | 4.2 | 3333.3333 | 187.5236
|  |  | 8.8775 | mid | 11200 | 8.1 | 1382.716 | 0 | 11200 | 7.35 | 1523.8095 | 0 | 11200 | 6.6 | 1696.9697 | 0 | 11200 | 5.8 | 1931.0345 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.4 | 2545.4545 | 0
|  |  | 46.6234 | min | 7300 | 14 | 521.4286 | 0 | 6700 | 8 | 837.5 | 0 | 6400 | 6.65 | 962.406 | 0 | 6000 | 5.3 | 1132.0755 | 0 | 5600 | 4.4 | 1272.7273 | 0 | 5100 | 3.45 | 1478.2609 | 0
Indoor Temp. |  | 23
LWT |  |  | 25 CAP: 25; 35 CAP: 35; 40 CAP: 40; 45 CAP: 45; 50 CAP: 50; 55 CAP: 55
Outdoor air temperature[℃] |  | Heating Demand | COP | CL | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP
|  |  | LWT |  |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI
| -15 |  | 1.3287 | max | - | - | - | - | 14000 | 1.85 | 7567.5676 | 2.1062 | 13500 | 1.7 | 7941.1765 | 1.8933 | 13100 | 1.55 | 8451.6129 | 1.6846 | 12600 | 1.45 | 8689.6552 | 1.5077 | 12200 | 1.3 | 9384.6154 | 1.277
|  | 12292.1739 | 53.879 | nom | - | - | - | - | 11000 | 2.3 | 4782.6087 | 5836.2578 | 11000 | 2.1 | 5238.0952 | 6492.6237 | 11000 | 1.9 | 5789.4737 | 7296.6277 | 11000 | 1.75 | 6285.7143 | 8152.8369 | 11000 | 1.6 | 6875 | 9626.1491
|  |  | 100 | mid | - | - | - | - | 8800 | 2.5 | 3520 | 3 | 8800 | 2.3 | 3826.087 | 3 | 8800 | 2.1 | 4190.4762 | 3 | 8800 | 1.9 | 4631.5789 | 3 | 8800 | 1.7 | 5176.4706 | 3
|  |  | 9251.3208 | min | - | - | - | - | 7800 | 2.35 | 3319.1489 | 0.43072 | 7200 | 2 | 3600 | 0.51687 | 6500 | 1.6 | 4062.5 | 0.61532 | 5700 | 1.3 | 4384.6154 | 0.80761 | 4800 | 1 | 4800 | 1.0768
| -14 |  | 1.7692 | max | 14280 | 2.08 | 6865.3846 | 2.6763 | 14080 | 1.93 | 7295.3368 | 2.4851 | 13640 | 1.78 | 7662.9213 | 2.2869 | 13280 | 1.62 | 8197.5309 | 2.0814 | 12880 | 1.53 | 8418.3007 | 1.8933 | 12560 | 1.39 | 9035.9712 | 1.7025
|  | 11968.6957 | 53.252 | nom | 14000 | 2.64 | 5303.0303 | 4472.15 | 14000 | 2.34 | 5982.906 | 4816.196 | 14000 | 2.12 | 6603.7736 | 5233.6875 | 14000 | 1.9 | 7368.4211 | 5750.4029 | 14000 | 1.77 | 7909.6045 | 6321.508 | 14000 | 1.63 | 8588.9571 | 7029.8785
|  |  | 100 | mid | 11200 | 2.69 | 4163.5688 | 2 | 11200 | 2.54 | 4409.4488 | 2 | 11200 | 2.35 | 4765.9574 | 2 | 11200 | 2.15 | 5209.3023 | 2 | 11200 | 1.94 | 5773.1959 | 2 | 11200 | 1.73 | 6473.9884 | 2
|  |  | 6764.8611 | min | 7720 | 2.59 | 2980.695 | 0.27453 | 7420 | 2.34 | 3170.9402 | 0.27453 | 6880 | 2.01 | 3422.8856 | 0.27453 | 6260 | 1.63 | 3840.4908 | 0.27453 | 5480 | 1.33 | 4120.3008 | 0.27453 | 4640 | 1.02 | 4549.0196 | 0.27453
| -13 |  | 1.842 | max | 14360 | 2.16 | 6648.1481 | 2.722 | 14160 | 2.01 | 7044.7761 | 2.5482 | 13780 | 1.86 | 7408.6022 | 2.3587 | 13460 | 1.69 | 7964.497 | 2.1523 | 13160 | 1.61 | 8173.913 | 1.9498 | 12920 | 1.48 | 8729.7297 | 1.7441
|  | 11645.2174 | 52.6211 | nom | 14000 | 2.68 | 5223.8806 | 4278.1061 | 14000 | 2.38 | 5882.3529 | 4569.98 | 14000 | 2.14 | 6542.0561 | 4937.2209 | 14000 | 1.9 | 7368.4211 | 5410.5968 | 14000 | 1.79 | 7821.2291 | 5972.5532 | 14000 | 1.66 | 8433.7349 | 6676.9231
|  |  | 100 | mid | 11200 | 2.73 | 4102.5641 | 2 | 11200 | 2.58 | 4341.0853 | 2 | 11200 | 2.4 | 4666.6667 | 2 | 11200 | 2.2 | 5090.9091 | 2 | 11200 | 1.98 | 5656.5657 | 2 | 11200 | 1.76 | 6363.6364 | 2
|  |  | 6322.1744 | min | 7340 | 2.58 | 2844.9612 | 0.15901 | 7040 | 2.33 | 3021.4592 | 0.15901 | 6560 | 2.02 | 3247.5248 | 0.15901 | 6020 | 1.66 | 3626.506 | 0.15901 | 5260 | 1.36 | 3867.6471 | 0.15901 | 4480 | 1.04 | 4307.6923 | 0.15901
| -12 |  | 1.9214 | max | 14440 | 2.24 | 6446.4286 | 2.7678 | 14240 | 2.09 | 6813.3971 | 2.6113 | 13920 | 1.94 | 7175.2577 | 2.4374 | 13640 | 1.76 | 7750 | 2.2348 | 13440 | 1.69 | 7952.6627 | 2.0109 | 13280 | 1.57 | 8458.5987 | 1.7857
|  | 11321.7391 | 51.9861 | nom | 14000 | 2.72 | 5147.0588 | 4090.4807 | 14000 | 2.42 | 5785.124 | 4335.6643 | 14000 | 2.16 | 6481.4815 | 4645.0232 | 14000 | 1.9 | 7368.4211 | 5066.1479 | 14000 | 1.81 | 7734.8066 | 5630.2703 | 14000 | 1.69 | 8284.0237 | 6340.3944
|  |  | 100 | mid | 11200 | 2.77 | 4043.3213 | 2 | 11200 | 2.62 | 4274.8092 | 2 | 11200 | 2.45 | 4571.4286 | 2 | 11200 | 2.25 | 4977.7778 | 2 | 11200 | 2.02 | 5544.5545 | 2 | 11200 | 1.79 | 6256.9832 | 2
|  |  | 5892.4129 | min | 6960 | 2.57 | 2708.1712 | 0.043478 | 6660 | 2.32 | 2870.6897 | 0.043478 | 6240 | 2.03 | 3073.8916 | 0.043478 | 5780 | 1.69 | 3420.1183 | 0.043478 | 5040 | 1.39 | 3625.8993 | 0.043478 | 4320 | 1.06 | 4075.4717 | 0.043478
| -11 |  | 1.9749 | max | 14520 | 2.32 | 6258.6207 | 2.7991 | 14320 | 2.17 | 6599.0783 | 2.6456 | 14060 | 2.02 | 6960.396 | 2.4824 | 13820 | 1.83 | 7551.9126 | 2.2793 | 13720 | 1.77 | 7751.4124 | 2.0398 | 13640 | 1.66 | 8216.8675 | 1.7988
|  | 10998.2609 | 51.3469 | nom | 14000 | 2.76 | 5072.4638 | 3929.2366 | 14000 | 2.46 | 5691.0569 | 4157.1132 | 14000 | 2.18 | 6422.0183 | 4430.4518 | 14000 | 1.9 | 7368.4211 | 4825.2227 | 14000 | 1.83 | 7650.2732 | 5391.9312 | 14000 | 1.72 | 8139.5349 | 6114.2399
|  |  | 100 | mid | 11200 | 2.81 | 3985.7651 | 1 | 11200 | 2.66 | 4210.5263 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1 | 11200 | 2.06 | 5436.8932 | 1 | 11200 | 1.82 | 6153.8462 | 1
|  |  | 5569.1601 | min | 6580 | 2.56 | 2570.3125 | 0.95633 | 6280 | 2.31 | 2718.6147 | 0.959 | 5920 | 2.04 | 2901.9608 | 0.96179 | 5540 | 1.72 | 3220.9302 | 0.96436 | 4820 | 1.42 | 3394.3662 | 0.96838 | 4160 | 1.08 | 3851.8519 | 0.97134
| -10 |  | 2.0127 | max | 14600 | 2.4 | 6083.3333 | 2.8185 | 14400 | 2.25 | 6400 | 2.6604 | 14200 | 2.1 | 6761.9048 | 2.5031 | 14000 | 1.9 | 7368.4211 | 2.2966 | 14000 | 1.85 | 7567.5676 | 2.0483 | 14000 | 1.75 | 8000 | 1.7953
|  | 10674.7826 | 50.7034 | nom | 14000 | 2.8 | 5000 | 3787.416 | 14000 | 2.5 | 5600 | 4012.5317 | 14000 | 2.2 | 6363.6364 | 4264.6154 | 14000 | 1.9 | 7368.4211 | 4648.1051 | 14000 | 1.85 | 7567.5676 | 5211.5988 | 14000 | 1.75 | 8000 | 5945.9939
|  |  | 100 | mid | 11200 | 2.85 | 3929.8246 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.1 | 5333.3333 | 1 | 11200 | 1.85 | 6054.0541 | 1
|  |  | 5303.7491 | min | 6200 | 2.55 | 2431.3725 | 0.89496 | 5900 | 2.3 | 2565.2174 | 0.9009 | 5600 | 2.05 | 2731.7073 | 0.90621 | 5300 | 1.75 | 3028.5714 | 0.91098 | 4600 | 1.45 | 3172.4138 | 0.92042 | 4000 | 1.1 | 3636.3636 | 0.92705
| -9 |  | 2.0783 | max | 15100 | 2.5 | 6040 | 2.9728 | 14900 | 2.3333 | 6385.7143 | 2.7261 | 14700 | 2.1667 | 6784.6154 | 2.5383 | 14500 | 1.9667 | 7372.8814 | 2.3174 | 14233.3333 | 1.9167 | 7426.087 | 2.081 | 14000 | 1.8167 | 7706.422 | 1.8409
|  | 10351.3043 | 50.0553 | nom | 14000 | 2.8833 | 4855.4913 | 3482.0161 | 14000 | 2.6 | 5384.6154 | 3797.1156 | 14000 | 2.3167 | 6043.1655 | 4078.1191 | 14000 | 2.0333 | 6885.2459 | 4466.8447 | 14000 | 1.95 | 7179.4872 | 4974.2425 | 14000 | 1.8167 | 7706.422 | 5622.898
|  |  | 100 | mid | 11200 | 2.9833 | 3754.1899 | 1 | 11200 | 2.8 | 4000 | 1 | 11200 | 2.6167 | 4280.2548 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.1667 | 5169.2308 | 1 | 11200 | 1.9333 | 5793.1034 | 1
|  |  | 4980.5982 | min | 5833.3333 | 2.9167 | 2000 | 0.84186 | 5266.6667 | 2.2833 | 2306.5693 | 0.85696 | 5066.6667 | 2.05 | 2471.5447 | 0.86163 | 4866.6667 | 1.7833 | 2728.972 | 0.866 | 4266.6667 | 1.4667 | 2909.0909 | 0.87759 | 3700 | 1.1167 | 3313.4328 | 0.88684
| -8 |  | 2.1396 | max | 15600 | 2.6 | 6000 | 3.1507 | 15400 | 2.4167 | 6372.4138 | 2.7869 | 15200 | 2.2333 | 6805.9701 | 2.572 | 15000 | 2.0333 | 7377.0492 | 2.3403 | 14466.6667 | 1.9833 | 7294.1176 | 2.1124 | 14000 | 1.8833 | 7433.6283 | 1.8839
|  | 10027.8261 | 49.4026 | nom | 14000 | 2.9667 | 4719.1011 | 3182.6877 | 14000 | 2.7 | 5185.1852 | 3598.1393 | 14000 | 2.4333 | 5753.4247 | 3898.8789 | 14000 | 2.1667 | 6461.5385 | 4284.8663 | 14000 | 2.05 | 6829.2683 | 4747.2323 | 14000 | 1.8833 | 7433.6283 | 5322.85
|  |  | 100 | mid | 11200 | 3.1167 | 3593.5829 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.6833 | 4173.913 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.2333 | 5014.9254 | 1 | 11200 | 2.0167 | 5553.719 | 1
|  |  | 4686.8033 | min | 5466.6667 | 3.2833 | 1664.9746 | 0.79555 | 4633.3333 | 2.2667 | 2044.1176 | 0.8215 | 4533.3333 | 2.05 | 2211.3821 | 0.82417 | 4433.3333 | 1.8167 | 2440.367 | 0.82677 | 3933.3333 | 1.4833 | 2651.6854 | 0.83869 | 3400 | 1.1333 | 3000 | 0.84972
| -7 |  | 2.1984 | max | 16100 | 2.7 | 5962.963 | 3.3481 | 15900 | 2.5 | 6360 | 2.8442 | 15700 | 2.3 | 6826.087 | 2.6046 | 15500 | 2.1 | 7380.9524 | 2.365 | 14700 | 2.05 | 7170.7317 | 2.1426 | 14000 | 1.95 | 7179.4872 | 1.9246
|  | 9704.3478 | 48.7449 | nom | 14000 | 3.05 | 4590.1639 | 2898.4853 | 14000 | 2.8 | 5000 | 3411.9745 | 14000 | 2.55 | 5490.1961 | 3725.8648 | 14000 | 2.3 | 6086.9565 | 4103.3602 | 14000 | 2.15 | 6511.6279 | 4529.3175 | 14000 | 1.95 | 7179.4872 | 5042.3093
|  |  | 100 | mid | 11200 | 3.25 | 3446.1538 | 1 | 11200 | 3 | 3733.3333 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1 | 11200 | 2.1 | 5333.3333 | 1
|  |  | 4414.2955 | min | 5100 | 3.65 | 1397.2603 | 0.75481 | 4000 | 2.25 | 1777.7778 | 0.79227 | 4000 | 2.05 | 1951.2195 | 0.79227 | 4000 | 1.85 | 2162.1622 | 0.79227 | 3600 | 1.5 | 2400 | 0.8032 | 3100 | 1.15 | 2695.6522 | 0.81535
| -6 |  | 2.2475 | max | 16144.4444 | 2.7611 | 5847.0825 | 3.4198 | 15944.4444 | 2.5556 | 6239.1304 | 2.8802 | 15733.3333 | 2.35 | 6695.0355 | 2.6341 | 15533.3333 | 2.1444 | 7243.5233 | 2.3867 | 14744.4444 | 2.0944 | 7039.7878 | 2.1609 | 14033.3333 | 1.9944 | 7036.2117 | 1.9351
|  | 9380.8696 | 48.0822 | nom | 14000 | 3.0889 | 4532.3741 | 2743.0694 | 14000 | 2.8389 | 4931.5068 | 3256.9781 | 14000 | 2.5889 | 5407.7253 | 3561.3189 | 14000 | 2.3389 | 5985.7482 | 3930.3965 | 14000 | 2.1944 | 6379.7468 | 4341.1951 | 14000 | 2 | 7000 | 4847.7373
|  |  | 100 | mid | 11200 | 3.2944 | 3399.6627 | 1 | 11200 | 3.0444 | 3678.8321 | 1 | 11200 | 2.7944 | 4007.9523 | 1 | 11200 | 2.5444 | 4401.7467 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.15 | 5209.3023 | 1
|  |  | 4173.8721 | min | 5155.5556 | 3.7111 | 1389.2216 | 0.69904 | 4122.2222 | 2.4056 | 1713.6259 | 0.74298 | 4077.7778 | 2.1667 | 1882.0513 | 0.74458 | 4022.2222 | 1.9222 | 2092.4855 | 0.74656 | 3611.1111 | 1.5611 | 2313.1673 | 0.76029 | 3111.1111 | 1.1944 | 2604.6512 | 0.77511
| -5 |  | 2.2994 | max | 16188.8889 | 2.8222 | 5736.2205 | 3.4939 | 15988.8889 | 2.6111 | 6123.4043 | 2.9263 | 15766.6667 | 2.4 | 6569.4444 | 2.6699 | 15566.6667 | 2.1889 | 7111.6751 | 2.4109 | 14788.8889 | 2.1389 | 6914.2857 | 2.1801 | 14066.6667 | 2.0389 | 6899.1826 | 1.9451
|  | 9057.3913 | 47.4142 | nom | 14000 | 3.1278 | 4476.0213 | 2592.3294 | 14000 | 2.8778 | 4864.8649 | 3095.157 | 14000 | 2.6278 | 5327.6956 | 3392.3914 | 14000 | 2.3778 | 5887.8505 | 3756.8621 | 14000 | 2.2389 | 6253.1017 | 4154.6063 | 14000 | 2.05 | 6829.2683 | 4656.5939
|  |  | 100 | mid | 11200 | 3.3389 | 3354.4093 | 1 | 11200 | 3.0889 | 3625.8993 | 1 | 11200 | 2.8389 | 3945.2055 | 1 | 11200 | 2.5889 | 4326.1803 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.2 | 5090.9091 | 1
|  |  | 3938.9433 | min | 5211.1111 | 3.7722 | 1381.4433 | 0.64224 | 4244.4444 | 2.5611 | 1657.2668 | 0.69196 | 4155.5556 | 2.2833 | 1819.9513 | 0.69584 | 4044.4444 | 1.9944 | 2027.8552 | 0.70057 | 3622.2222 | 1.6222 | 2232.8767 | 0.71725 | 3122.2222 | 1.2389 | 2520.1794 | 0.73475
| -4 |  | 2.3548 | max | 16233.3333 | 2.8833 | 5630.0578 | 3.5704 | 16033.3333 | 2.6667 | 6012.5 | 2.983 | 15800 | 2.45 | 6448.9796 | 2.7122 | 15600 | 2.2333 | 6985.0746 | 2.4374 | 14833.3333 | 2.1833 | 6793.8931 | 2.2001 | 14100 | 2.0833 | 6768 | 1.9545
|  | 8733.913 | 46.7407 | nom | 14000 | 3.1667 | 4421.0526 | 2446.2221 | 14000 | 2.9167 | 4800 | 2927.9329 | 14000 | 2.6667 | 5250 | 3220.183 | 14000 | 2.4167 | 5793.1034 | 3583.2478 | 14000 | 2.2833 | 6131.3869 | 3969.722 | 14000 | 2.1 | 6666.6667 | 4468.6697
|  |  | 100 | mid | 11200 | 3.3833 | 3310.3448 | 1 | 11200 | 3.1333 | 3574.4681 | 1 | 11200 | 2.8833 | 3884.3931 | 1 | 11200 | 2.6333 | 4253.1646 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.25 | 4977.7778 | 1
|  |  | 3708.9582 | min | 5266.6667 | 3.8333 | 1373.913 | 0.58437 | 4366.6667 | 2.7167 | 1607.362 | 0.63911 | 4233.3333 | 2.4 | 1763.8889 | 0.64602 | 4066.6667 | 2.0667 | 1967.7419 | 0.65429 | 3633.3333 | 1.6833 | 2158.4158 | 0.67409 | 3133.3333 | 1.2833 | 2441.5584 | 0.69429
| -3 |  | 2.4143 | max | 16277.7778 | 2.9444 | 5528.3019 | 3.6493 | 16077.7778 | 2.7222 | 5906.1224 | 3.0508 | 15833.3333 | 2.5 | 6333.3333 | 2.7613 | 15633.3333 | 2.2778 | 6863.4146 | 2.4664 | 14877.7778 | 2.2278 | 6678.3042 | 2.221 | 14133.3333 | 2.1278 | 6642.2977 | 1.9633
|  | 8410.4348 | 46.0614 | nom | 14000 | 3.2056 | 4367.4177 | 2304.6988 | 14000 | 2.9556 | 4736.8421 | 2756.8241 | 14000 | 2.7056 | 5174.538 | 3045.8202 | 14000 | 2.4556 | 5701.3575 | 3410.0306 | 14000 | 2.3278 | 6014.3198 | 3786.7043 | 14000 | 2.15 | 6511.6279 | 4283.7638
|  |  | 100 | mid | 11200 | 3.4278 | 3267.423 | 1 | 11200 | 3.1778 | 3524.4755 | 1 | 11200 | 2.9278 | 3825.4269 | 1 | 11200 | 2.6778 | 4182.5726 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1
|  |  | 3483.591 | min | 5322.2222 | 3.8944 | 1366.6191 | 0.5254 | 4488.8889 | 2.8722 | 1562.8627 | 0.58434 | 4311.1111 | 2.5167 | 1713.0243 | 0.59506 | 4088.8889 | 2.1389 | 1911.6883 | 0.60772 | 3644.4444 | 1.7444 | 2089.172 | 0.63079 | 3144.4444 | 1.3278 | 2368.2008 | 0.65371
| -2 |  | 2.4786 | max | 16322.2222 | 3.0056 | 5430.6839 | 3.7307 | 16122.2222 | 2.7778 | 5804 | 3.1304 | 15866.6667 | 2.55 | 6222.2222 | 2.8173 | 15666.6667 | 2.3222 | 6746.4115 | 2.4978 | 14922.2222 | 2.2722 | 6567.2372 | 2.2428 | 14166.6667 | 2.1722 | 6521.7391 | 1.9716
|  | 8086.9565 | 45.376 | nom | 14000 | 3.2444 | 4315.0685 | 2167.7057 | 14000 | 2.9944 | 4675.3247 | 2583.4006 | 14000 | 2.7444 | 5101.2146 | 2870.431 | 14000 | 2.4944 | 5612.4722 | 3237.6696 | 14000 | 2.3722 | 5901.6393 | 3605.706 | 14000 | 2.2 | 6363.6364 | 4101.6831
|  |  | 100 | mid | 11200 | 3.4722 | 3225.6 | 1 | 11200 | 3.2222 | 3475.8621 | 1 | 11200 | 2.9722 | 3768.2243 | 1 | 11200 | 2.7222 | 4114.2857 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1
|  |  | 3262.7161 | min | 5377.7778 | 3.9556 | 1359.5506 | 0.46532 | 4611.1111 | 3.0278 | 1522.9358 | 0.52753 | 4388.8889 | 2.6333 | 1666.6667 | 0.54295 | 4111.1111 | 2.2111 | 1859.2965 | 0.56086 | 3655.5556 | 1.8056 | 2024.6154 | 0.58737 | 3155.5556 | 1.3722 | 2299.5951 | 0.61302
| -1 |  | 2.5537 | max | 16366.6667 | 3.0667 | 5336.9565 | 3.8146 | 16166.6667 | 2.8333 | 5705.8824 | 3.2224 | 15900 | 2.6 | 6115.3846 | 2.8806 | 15700 | 2.3667 | 6633.8028 | 2.5316 | 14966.6667 | 2.3167 | 6460.4317 | 2.2655 | 14200 | 2.2167 | 6406.015 | 1.9793
|  | 7763.4783 | 44.6843 | nom | 14000 | 3.2833 | 4263.9594 | 2035.1846 | 14000 | 3.0333 | 4615.3846 | 2409.2362 | 14000 | 2.7833 | 5029.9401 | 2695.1218 | 14000 | 2.5333 | 5526.3158 | 3066.603 | 14000 | 2.4167 | 5793.1034 | 3426.8711 | 14000 | 2.25 | 6222.2222 | 3922.2423
|  |  | 100 | mid | 11200 | 3.5167 | 3184.8341 | 1 | 11200 | 3.2667 | 3428.5714 | 1 | 11200 | 3.0167 | 3712.7072 | 1 | 11200 | 2.7667 | 4048.1928 | 1 | 11200 | 2.6 | 4307.6923 | 1 | 11200 | 2.4 | 4666.6667 | 1
|  |  | 3040.1465 | min | 5433.3333 | 4.0167 | 1352.6971 | 0.40407 | 4733.3333 | 3.1833 | 1486.911 | 0.46858 | 4466.6667 | 2.75 | 1624.2424 | 0.48963 | 4133.3333 | 2.2833 | 1810.219 | 0.5137 | 3666.6667 | 1.8667 | 1964.2857 | 0.54382 | 3166.6667 | 1.4167 | 2235.2941 | 0.57222
| 0 |  | 2.6457 | max | 16411.1111 | 3.1278 | 5246.8917 | 3.9013 | 16211.1111 | 2.8889 | 5611.5385 | 3.3276 | 15933.3333 | 2.65 | 6012.5786 | 2.9513 | 15733.3333 | 2.4111 | 6525.3456 | 2.568 | 15011.1111 | 2.3611 | 6357.6471 | 2.289 | 14233.3333 | 2.2611 | 6294.8403 | 1.9865
|  | 7440 | 43.9859 | nom | 14000 | 3.3222 | 4214.0468 | 1907.0729 | 14000 | 3.0722 | 4556.962 | 2235.8635 | 14000 | 2.8222 | 4960.6299 | 2520.956 | 14000 | 2.5722 | 5442.7646 | 2897.2453 | 14000 | 2.4611 | 5688.4876 | 3250.3339 | 14000 | 2.3 | 6086.9565 | 3745.2624
|  |  | 100 | mid | 11200 | 3.5611 | 3145.0858 | 1 | 11200 | 3.3111 | 3382.5503 | 1 | 11200 | 3.0611 | 3658.8022 | 1 | 11200 | 2.8111 | 3984.1897 | 1 | 11200 | 2.65 | 4226.4151 | 1 | 11200 | 2.45 | 4571.4286 | 1
|  |  | 2812.1126 | min | 5488.8889 | 4.0778 | 1346.049 | 0.34163 | 4855.5556 | 3.3389 | 1454.2429 | 0.40736 | 4544.4444 | 2.8667 | 1585.2713 | 0.43506 | 4155.5556 | 2.3556 | 1764.1509 | 0.46625 | 3677.7778 | 1.9278 | 1907.781 | 0.50015 | 3177.7778 | 1.4611 | 2174.9049 | 0.5313
| 1 |  | 2.7522 | max | 16455.5556 | 3.1889 | 5160.2787 | 3.9906 | 16255.5556 | 2.9444 | 5520.7547 | 3.4467 | 15966.6667 | 2.7 | 5913.5802 | 3.0297 | 15766.6667 | 2.4556 | 6420.8145 | 2.6068 | 15055.5556 | 2.4056 | 6258.6605 | 2.3134 | 14266.6667 | 2.3056 | 6187.9518 | 1.9931
|  | 7116.5217 | 43.2805 | nom | 14000 | 3.3611 | 4165.2893 | 1783.3043 | 14000 | 3.1111 | 4500 | 2064.7321 | 14000 | 2.8611 | 4893.2039 | 2348.935 | 14000 | 2.6111 | 5361.7021 | 2729.9845 | 14000 | 2.5056 | 5587.5831 | 3076.2196 | 14000 | 2.35 | 5957.4468 | 3570.5704
|  |  | 100 | mid | 11200 | 3.6056 | 3106.3174 | 1 | 11200 | 3.3556 | 3337.7483 | 1 | 11200 | 3.1056 | 3606.4401 | 1 | 11200 | 2.8556 | 3922.179 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.5 | 4480 | 1
|  |  | 2585.7274 | min | 5544.4444 | 4.1389 | 1339.5973 | 0.27797 | 4977.7778 | 3.4944 | 1424.4833 | 0.34373 | 4622.2222 | 2.9833 | 1549.3482 | 0.3792 | 4177.7778 | 2.4278 | 1720.8238 | 0.41849 | 3688.8889 | 1.9889 | 1854.7486 | 0.45634 | 3188.8889 | 1.5056 | 2118.0812 | 0.49027
14kW-Maximum heating CAP | 2 |  | 2.8758 | max | 16500 | 3.25 | 5076.9231 | 4.0828 | 16300 | 3 | 5433.3333 | 3.5806 | 16000 | 2.75 | 5818.1818 | 3.1161 | 15800 | 2.5 | 6320 | 2.6482 | 15100 | 2.45 | 6163.2653 | 2.3387 | 14300 | 2.35 | 6085.1064 | 1.9991
|  | 6793.0435 | 42.5676 | nom | 14000 | 3.4 | 4117.6471 | 1663.8092 | 14000 | 3.15 | 4444.4444 | 1897.1733 | 14000 | 2.9 | 4827.5862 | 2179.9823 | 14000 | 2.65 | 5283.0189 | 2565.1803 | 14000 | 2.55 | 5490.1961 | 2904.6435 | 14000 | 2.4 | 5833.3333 | 3397.9991
|  |  | 100 | mid | 11200 | 3.65 | 3068.4932 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 3.15 | 3555.5556 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.55 | 4392.1569 | 1
|  |  | 2362.1282 | min | 5600 | 4.2 | 1333.3333 | 0.21304 | 5100 | 3.65 | 1397.2603 | 0.27755 | 4700 | 3.1 | 1516.129 | 0.32201 | 4200 | 2.5 | 1680 | 0.37043 | 3700 | 2.05 | 1804.878 | 0.41241 | 3200 | 1.55 | 2064.5161 | 0.44913
| 3 |  | 3.0449 | max | 16560 | 3.54 | 4677.9661 | 4.5471 | 16360 | 3.25 | 5033.8462 | 3.7779 | 16080 | 2.96 | 5432.4324 | 3.2417 | 15860 | 2.66 | 5962.406 | 2.7089 | 15160 | 2.54 | 5968.5039 | 2.364 | 14360 | 2.38 | 6033.6134 | 1.9912
|  | 6469.5652 | 41.8468 | nom | 14000 | 3.7 | 3783.7838 | 1422.7954 | 14000 | 3.41 | 4105.5718 | 1712.4661 | 14000 | 3.12 | 4487.1795 | 1995.7121 | 14000 | 2.82 | 4964.539 | 2388.23 | 14000 | 2.67 | 5243.4457 | 2736.7576 | 14000 | 2.47 | 5668.0162 | 3249.0813
|  |  | 100 | mid | 11200 | 3.97 | 2821.1587 | 1 | 11200 | 3.68 | 3043.4783 | 1 | 11200 | 3.39 | 3303.8348 | 1 | 11200 | 3.09 | 3624.5955 | 1 | 11200 | 2.88 | 3888.8889 | 1 | 11200 | 2.62 | 4274.8092 | 1
|  |  | 2124.6927 | min | 5380 | 4.68 | 1149.5726 | 0.18721 | 4920 | 3.81 | 1291.3386 | 0.24675 | 4500 | 3.18 | 1415.0943 | 0.29396 | 4000 | 2.51 | 1593.6255 | 0.343 | 3500 | 2.04 | 1715.6863 | 0.38566 | 3000 | 1.53 | 1960.7843 | 0.42312
| 4 |  | 3.2253 | max | 16620 | 3.83 | 4339.4256 | 5.018 | 16420 | 3.5 | 4691.4286 | 3.9678 | 16160 | 3.17 | 5097.7918 | 3.359 | 15920 | 2.82 | 5645.3901 | 2.7609 | 15220 | 2.63 | 5787.0722 | 2.3831 | 14420 | 2.41 | 5983.4025 | 1.98
|  | 6146.087 | 41.1176 | nom | 14000 | 4 | 3500 | 1224.8168 | 14000 | 3.67 | 3814.7139 | 1548.982 | 14000 | 3.34 | 4191.6168 | 1829.7409 | 14000 | 2.99 | 4682.2742 | 2226.0773 | 14000 | 2.79 | 5017.9211 | 2579.0747 | 14000 | 2.54 | 5511.811 | 3104.0129
|  |  | 100 | mid | 11200 | 4.29 | 2610.7226 | 1 | 11200 | 3.96 | 2828.2828 | 1 | 11200 | 3.63 | 3085.3994 | 1 | 11200 | 3.28 | 3414.6341 | 1 | 11200 | 3.01 | 3720.9302 | 1 | 11200 | 2.69 | 4163.5688 | 1
|  |  | 1905.5776 | min | 5160 | 5.16 | 1000 | 0.16326 | 4740 | 3.97 | 1193.9547 | 0.21766 | 4300 | 3.26 | 1319.0184 | 0.26755 | 3800 | 2.52 | 1507.9365 | 0.31704 | 3300 | 2.03 | 1625.6158 | 0.36026 | 2800 | 1.51 | 1854.3046 | 0.39834
| 5 |  | 3.4182 | max | 16680 | 4.12 | 4048.5437 | 5.4948 | 16480 | 3.75 | 4394.6667 | 4.1509 | 16240 | 3.38 | 4804.7337 | 3.4686 | 15980 | 2.98 | 5362.4161 | 2.8049 | 15280 | 2.72 | 5617.6471 | 2.3965 | 14480 | 2.44 | 5934.4262 | 1.9659
|  | 5822.6087 | 40.3796 | nom | 14000 | 4.3 | 3255.814 | 1059.6621 | 14000 | 3.93 | 3562.341 | 1402.7284 | 14000 | 3.56 | 3932.5843 | 1678.6678 | 14000 | 3.16 | 4430.3797 | 2075.8691 | 14000 | 2.91 | 4810.9966 | 2429.6713 | 14000 | 2.61 | 5363.9847 | 2961.8078
|  |  | 100 | mid | 11200 | 4.61 | 2429.5011 | 1 | 11200 | 4.24 | 2641.5094 | 1 | 11200 | 3.87 | 2894.0568 | 1 | 11200 | 3.47 | 3227.6657 | 1 | 11200 | 3.14 | 3566.879 | 1 | 11200 | 2.76 | 4057.971 | 1
|  |  | 1703.4108 | min | 4940 | 5.64 | 875.8865 | 0.14099 | 4560 | 4.13 | 1104.1162 | 0.19015 | 4100 | 3.34 | 1227.5449 | 0.24262 | 3600 | 2.53 | 1422.9249 | 0.29245 | 3100 | 2.02 | 1534.6535 | 0.33612 | 2600 | 1.49 | 1744.9664 | 0.37472
| 6 |  | 3.6268 | max | 16740 | 4.41 | 3795.9184 | 5.9769 | 16540 | 4 | 4135 | 4.3277 | 16320 | 3.59 | 4545.961 | 3.5712 | 16040 | 3.14 | 5108.2803 | 2.8414 | 15340 | 2.81 | 5459.0747 | 2.4046 | 14540 | 2.47 | 5886.6397 | 1.949
|  | 5499.1304 | 39.632 | nom | 14000 | 4.6 | 3043.4783 | 920.0611 | 14000 | 4.19 | 3341.2888 | 1270.6697 | 14000 | 3.78 | 3703.7037 | 1539.8763 | 14000 | 3.33 | 4204.2042 | 1935.3502 | 14000 | 3.03 | 4620.462 | 2286.9527 | 14000 | 2.68 | 5223.8806 | 2821.5768
|  |  | 100 | mid | 11200 | 4.93 | 2271.8053 | 1 | 11200 | 4.52 | 2477.8761 | 1 | 11200 | 4.11 | 2725.0608 | 1 | 11200 | 3.66 | 3060.1093 | 1 | 11200 | 3.27 | 3425.0765 | 1 | 11200 | 2.83 | 3957.5972 | 1
|  |  | 1516.2325 | min | 4720 | 6.12 | 771.2418 | 0.12024 | 4380 | 4.29 | 1020.979 | 0.1641 | 3900 | 3.42 | 1140.3509 | 0.21906 | 3400 | 2.54 | 1338.5827 | 0.26912 | 2900 | 2.01 | 1442.7861 | 0.31315 | 2400 | 1.47 | 1632.6531 | 0.35217
| 7 |  | 3.8545 | max | 16800 | 4.7 | 3574.4681 | 6.4639 | 16600 | 4.25 | 3905.8824 | 4.4988 | 16400 | 3.8 | 4315.7895 | 3.6672 | 16100 | 3.3 | 4878.7879 | 2.871 | 15400 | 2.9 | 5310.3448 | 2.4078 | 14600 | 2.5 | 5840 | 1.9294
|  | 5175.6522 | 38.8742 | nom | 14000 | 4.9 | 2857.1429 | 800.706 | 14000 | 4.45 | 3146.0674 | 1150.4562 | 14000 | 4 | 3500 | 1411.3206 | 14000 | 3.5 | 4000 | 1802.7077 | 14000 | 3.15 | 4444.4444 | 2149.5764 | 14000 | 2.75 | 5090.9091 | 2682.5042
|  |  | 100 | mid | 11200 | 5.25 | 2133.3333 | 1 | 11200 | 4.8 | 2333.3333 | 1 | 11200 | 4.35 | 2574.7126 | 1 | 11200 | 3.85 | 2909.0909 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 2.9 | 3862.069 | 1
|  |  | 1342.7642 | min | 4500 | 6.6 | 681.8182 | 0.10084 | 4200 | 4.45 | 943.8202 | 0.13938 | 3700 | 3.5 | 1057.1429 | 0.19675 | 3200 | 2.55 | 1254.902 | 0.24696 | 2700 | 2 | 1350 | 0.29125 | 2200 | 1.45 | 1517.2414 | 0.33063
| 8 |  | 4.0943 | max | 16860 | 4.81 | 3505.1975 | 6.31 | 16640 | 4.38 | 3799.0868 | 4.5557 | 16440 | 3.93 | 4183.2061 | 3.8127 | 16160 | 3.48 | 4643.6782 | 3.0944 | 15440 | 3.06 | 5045.7516 | 2.5961 | 14640 | 2.64 | 5545.4545 | 2.0898
|  | 4852.1739 | 38.1053 | nom | 14000 | 5.02 | 2788.8446 | 768.9658 | 14000 | 4.59 | 3050.1089 | 1065.0857 | 14000 | 4.16 | 3365.3846 | 1272.6241 | 14000 | 3.69 | 3794.0379 | 1568.0543 | 14000 | 3.32 | 4216.8675 | 1869.0337 | 14000 | 2.9 | 4827.5862 | 2321.8638
|  |  | 100 | mid | 11200 | 5.37 | 2085.6611 | 0 | 11200 | 4.95 | 2262.6263 | 1 | 11200 | 4.53 | 2472.4062 | 1 | 11200 | 4.06 | 2758.6207 | 1 | 11200 | 3.58 | 3128.4916 | 1 | 11200 | 3.06 | 3660.1307 | 1
|  |  | 1185.1181 | min | 4920 | 6.31 | 779.7147 | 0 | 4600 | 4.54 | 1013.2159 | 0.038208 | 4120 | 3.73 | 1104.5576 | 0.10341 | 3640 | 2.91 | 1250.8591 | 0.16034 | 3200 | 2.34 | 1367.5214 | 0.20652 | 2760 | 1.77 | 1559.322 | 0.24789
| 9 |  | 4.3185 | max | 16920 | 4.92 | 3439.0244 | 6.02 | 16680 | 4.51 | 3698.4479 | 4.63 | 16480 | 4.06 | 4059.1133 | 3.96 | 16220 | 3.66 | 4431.694 | 3.333 | 15480 | 3.22 | 4807.4534 | 2.7993 | 14680 | 2.78 | 5280.5755 | 2.2633
|  | 4528.6957 | 37.3246 | nom | 14000 | 5.14 | 2723.7354 | 752.275 | 14000 | 4.73 | 2959.8309 | 978.12 | 14000 | 4.32 | 3240.7407 | 1143.61 | 14000 | 3.88 | 3608.2474 | 1358.7368 | 14000 | 3.49 | 4011.4613 | 1617.7772 | 14000 | 3.05 | 4590.1639 | 2000.901
|  |  | 94.6211 | mid | 11200 | 5.49 | 2040.0729 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.71 | 2377.9193 | 0 | 11200 | 4.27 | 2622.9508 | 1 | 11200 | 3.76 | 2978.7234 | 1 | 11200 | 3.22 | 3478.2609 | 1
|  |  | 1048.6716 | min | 5340 | 6.02 | 887.0432 | 0 | 5000 | 4.63 | 1079.9136 | 0 | 4540 | 3.96 | 1146.4646 | 0 | 4080 | 3.27 | 1247.7064 | 0.063019 | 3700 | 2.68 | 1380.597 | 0.11049 | 3320 | 2.09 | 1588.5167 | 0.15339
| 10 |  | 4.5577 | max | 16980 | 5.03 | 3375.7455 | 5.73 | 16720 | 4.64 | 3603.4483 | 4.72 | 16520 | 4.19 | 3942.7208 | 4.19 | 16280 | 3.84 | 4239.5833 | 3.63 | 15520 | 3.38 | 4591.716 | 3.0207 | 14720 | 2.92 | 5041.0959 | 2.4531
|  | 4205.2174 | 36.5308 | nom | 14000 | 5.26 | 2661.597 | 733.8948 | 14000 | 4.87 | 2874.7433 | 890.9359 | 14000 | 4.48 | 3125 | 1003.6318 | 14000 | 4.07 | 3439.8034 | 1158.4621 | 14000 | 3.66 | 3825.1366 | 1392.14 | 14000 | 3.2 | 4375 | 1714.2492
|  |  | 79.8668 | mid | 11200 | 5.61 | 1996.4349 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.89 | 2290.3885 | 0 | 11200 | 4.48 | 2500 | 0 | 11200 | 3.94 | 2842.6396 | 1 | 11200 | 3.38 | 3313.6095 | 1
|  |  | 922.6556 | min | 5760 | 5.73 | 1005.2356 | 0 | 5400 | 4.72 | 1144.0678 | 0 | 4960 | 4.19 | 1183.7709 | 0 | 4520 | 3.63 | 1245.1791 | 0 | 4200 | 3.02 | 1390.7285 | 0.00074534 | 3880 | 2.41 | 1609.9585 | 0.044429
| 11 |  | 4.7536 | max | 17040 | 5.14 | 3315.1751 | 5.44 | 16760 | 4.77 | 3513.6268 | 4.81 | 16560 | 4.32 | 3833.3333 | 4.42 | 16340 | 4.02 | 4064.6766 | 3.99 | 15560 | 3.54 | 4395.4802 | 3.36 | 14760 | 3.06 | 4823.5294 | 2.73
|  | 3881.7391 | 35.7228 | nom | 14000 | 5.38 | 2602.2305 | 713.555 | 14000 | 5.01 | 2794.4112 | 807.0144 | 14000 | 4.64 | 3017.2414 | 878.2215 | 14000 | 4.26 | 3286.385 | 972.8669 | 14000 | 3.83 | 3655.3525 | 1155.2795 | 14000 | 3.35 | 4179.1045 | 1421.8825
|  |  | 67.6346 | mid | 11200 | 5.73 | 1954.6248 | 0 | 11200 | 5.4 | 2074.0741 | 0 | 11200 | 5.07 | 2209.073 | 0 | 11200 | 4.69 | 2388.0597 | 0 | 11200 | 4.12 | 2718.4466 | 0 | 11200 | 3.54 | 3163.8418 | 0
|  |  | 816.5862 | min | 6180 | 5.44 | 1136.0294 | 0 | 5800 | 4.81 | 1205.8212 | 0 | 5380 | 4.42 | 1217.1946 | 0 | 4960 | 3.99 | 1243.1078 | 0 | 4700 | 3.36 | 1398.8095 | 0 | 4440 | 2.73 | 1626.3736 | 0
| 12 |  | 4.9025 | max | 17100 | 5.25 | 3257.1429 | 5.15 | 16800 | 4.9 | 3428.5714 | 4.9 | 16600 | 4.45 | 3730.3371 | 4.65 | 16400 | 4.2 | 3904.7619 | 4.35 | 15600 | 3.7 | 4216.2162 | 3.7 | 14800 | 3.2 | 4625 | 3.05
|  | 3558.2609 | 34.8992 | nom | 14000 | 5.5 | 2545.4545 | 690.9244 | 14000 | 5.15 | 2718.4466 | 726.1757 | 14000 | 4.8 | 2916.6667 | 765.2174 | 14000 | 4.45 | 3146.0674 | 817.991 | 14000 | 4 | 3500 | 961.6921 | 14000 | 3.5 | 4000 | 1166.6429
|  |  | 57.354 | mid | 11200 | 5.85 | 1914.5299 | 0 | 11200 | 5.55 | 2018.018 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.9 | 2285.7143 | 0 | 11200 | 4.3 | 2604.6512 | 0 | 11200 | 3.7 | 3027.027 | 0
|  |  | 725.8023 | min | 6600 | 5.15 | 1281.5534 | 0 | 6200 | 4.9 | 1265.3061 | 0 | 5800 | 4.65 | 1247.3118 | 0 | 5400 | 4.35 | 1241.3793 | 0 | 5200 | 3.7 | 1405.4054 | 0 | 5000 | 3.05 | 1639.3443 | 0
| 13 |  | 4.9839 | max | 17566.6667 | 5.2833 | 3324.9211 | 5.15 | 17266.6667 | 4.9333 | 3500 | 4.9667 | 17033.3333 | 4.55 | 3743.5897 | 4.7833 | 16833.3333 | 4.3 | 3914.7287 | 4.55 | 16033.3333 | 3.8 | 4219.2982 | 3.9167 | 15200 | 3.3 | 4606.0606 | 3.2667
|  | 3234.7826 | 34.058 | nom | 14000 | 5.5 | 2545.4545 | 628.1131 | 14000 | 5.1833 | 2700.9646 | 651.2985 | 14000 | 4.8667 | 2876.7123 | 676.2612 | 14000 | 4.55 | 3076.9231 | 710.9412 | 14000 | 4.1 | 3414.6341 | 825.9019 | 14000 | 3.6167 | 3870.9677 | 990.2396
|  |  | 51.2848 | mid | 11200 | 5.9 | 1898.3051 | 0 | 11200 | 5.5833 | 2005.9701 | 0 | 11200 | 5.3167 | 2106.5831 | 0 | 11200 | 5.0167 | 2232.5581 | 0 | 11200 | 4.4167 | 2535.8491 | 0 | 11200 | 3.8167 | 2934.4978 | 0
|  |  | 649.0416 | min | 6700 | 5.15 | 1300.9709 | 0 | 6266.6667 | 4.9667 | 1261.745 | 0 | 5833.3333 | 4.7833 | 1219.5122 | 0 | 5400 | 4.55 | 1186.8132 | 0 | 5233.3333 | 3.9167 | 1336.1702 | 0 | 5066.6667 | 3.2667 | 1551.0204 | 0
| 14 |  | 5.0544 | max | 18033.3333 | 5.3167 | 3391.8495 | 5.15 | 17733.3333 | 4.9667 | 3570.4698 | 5.0333 | 17466.6667 | 4.65 | 3756.2724 | 4.9167 | 17266.6667 | 4.4 | 3924.2424 | 4.75 | 16466.6667 | 3.9 | 4222.2222 | 4.1333 | 15600 | 3.4 | 4588.2353 | 3.4833
|  | 2911.3043 | 33.1971 | nom | 14000 | 5.5 | 2545.4545 | 565.3018 | 14000 | 5.2167 | 2683.7061 | 578.4048 | 14000 | 4.9333 | 2837.8378 | 592.1297 | 14000 | 4.65 | 3010.7527 | 612.9062 | 14000 | 4.2 | 3333.3333 | 704.3478 | 14000 | 3.7333 | 3750 | 835.7812
|  |  | 45.3653 | mid | 11200 | 5.95 | 1882.3529 | 0 | 11200 | 5.6167 | 1994.0653 | 0 | 11200 | 5.3833 | 2080.4954 | 0 | 11200 | 5.1333 | 2181.8182 | 0 | 11200 | 4.5333 | 2470.5882 | 0 | 11200 | 3.9333 | 2847.4576 | 0
|  |  | 575.9978 | min | 6800 | 5.15 | 1320.3883 | 0 | 6333.3333 | 5.0333 | 1258.2781 | 0 | 5866.6667 | 4.9167 | 1193.2203 | 0 | 5400 | 4.75 | 1136.8421 | 0 | 5266.6667 | 4.1333 | 1274.1935 | 0 | 5133.3333 | 3.4833 | 1473.6842 | 0
| 15 |  | 5.1134 | max | 18500 | 5.35 | 3457.9439 | 5.15 | 18200 | 5 | 3640 | 5.1 | 17900 | 4.75 | 3768.4211 | 5.05 | 17700 | 4.5 | 3933.3333 | 4.95 | 16900 | 4 | 4225 | 4.35 | 16000 | 3.5 | 4571.4286 | 3.7
|  | 2587.8261 | 32.3139 | nom | 14000 | 5.5 | 2545.4545 | 502.4905 | 14000 | 5.25 | 2666.6667 | 507.4169 | 14000 | 5 | 2800 | 512.4408 | 14000 | 4.75 | 2947.3684 | 522.7931 | 14000 | 4.3 | 3255.814 | 594.9025 | 14000 | 3.85 | 3636.3636 | 699.4125
|  |  | 39.6037 | mid | 11200 | 6 | 1866.6667 | 0 | 11200 | 5.65 | 1982.3009 | 0 | 11200 | 5.45 | 2055.0459 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.65 | 2408.6022 | 0 | 11200 | 4.05 | 2765.4321 | 0
|  |  | 506.0841 | min | 6900 | 5.15 | 1339.8058 | 0 | 6400 | 5.1 | 1254.902 | 0 | 5900 | 5.05 | 1168.3168 | 0 | 5400 | 4.95 | 1090.9091 | 0 | 5300 | 4.35 | 1218.3908 | 0 | 5200 | 3.7 | 1405.4054 | 0
| 16 |  | 6.1258 | max | 19020 | 5.73 | 3319.3717 | 6.92 | 18720 | 5.3 | 3532.0755 | 5.68 | 18420 | 4.95 | 3721.2121 | 5.37 | 18200 | 4.59 | 3965.1416 | 5.02 | 17380 | 4.08 | 4259.8039 | 4.36 | 16460 | 3.56 | 4623.5955 | 3.65
|  | 2264.3478 | 31.4047 | nom | 14000 | 5.93 | 2360.8769 | 327.2179 | 14000 | 5.57 | 2513.465 | 398.6528 | 14000 | 5.21 | 2687.1401 | 421.6663 | 14000 | 4.85 | 2886.5979 | 451.0653 | 14000 | 4.39 | 3189.0661 | 519.3458 | 14000 | 3.92 | 3571.4286 | 620.3693
|  |  | 34.0659 | mid | 11200 | 6.42 | 1744.5483 | 0 | 11200 | 5.99 | 1869.783 | 0 | 11200 | 5.68 | 1971.831 | 0 | 11200 | 5.36 | 2089.5522 | 0 | 11200 | 4.74 | 2362.8692 | 0 | 11200 | 4.12 | 2718.4466 | 0
|  |  | 369.6398 | min | 6980 | 6.92 | 1008.6705 | 0 | 6460 | 5.68 | 1137.3239 | 0 | 6000 | 5.37 | 1117.3184 | 0 | 5520 | 5.02 | 1099.6016 | 0 | 5360 | 4.36 | 1229.3578 | 0 | 5180 | 3.65 | 1419.1781 | 0
| 17 |  | 7.362 | max | 19540 | 6.11 | 3198.036 | 8.69 | 19240 | 5.6 | 3435.7143 | 6.26 | 18940 | 5.15 | 3677.6699 | 5.69 | 18700 | 4.68 | 3995.7265 | 5.09 | 17860 | 4.16 | 4293.2692 | 4.37 | 16920 | 3.62 | 4674.0331 | 3.6
|  | 1940.8696 | 30.4649 | nom | 14000 | 6.36 | 2201.2579 | 223.3452 | 14000 | 5.89 | 2376.91 | 310.0431 | 14000 | 5.42 | 2583.0258 | 341.1019 | 14000 | 4.95 | 2828.2828 | 381.3103 | 14000 | 4.48 | 3125 | 444.1349 | 14000 | 3.99 | 3508.7719 | 539.1304
|  |  | 28.6903 | mid | 11200 | 6.84 | 1637.4269 | 0 | 11200 | 6.33 | 1769.3523 | 0 | 11200 | 5.91 | 1895.0931 | 0 | 11200 | 5.47 | 2047.532 | 0 | 11200 | 4.83 | 2318.8406 | 0 | 11200 | 4.19 | 2673.031 | 0
|  |  | 263.6322 | min | 7060 | 8.69 | 812.4281 | 0 | 6520 | 6.26 | 1041.5335 | 0 | 6100 | 5.69 | 1072.0562 | 0 | 5640 | 5.09 | 1108.055 | 0 | 5420 | 4.37 | 1240.2746 | 0 | 5160 | 3.6 | 1433.3333 | 0
| 18 |  | 8.8353 | max | 20060 | 6.49 | 3090.9091 | 10.46 | 19760 | 5.9 | 3349.1525 | 6.84 | 19460 | 5.35 | 3637.3832 | 6.01 | 19200 | 4.77 | 4025.1572 | 5.16 | 18340 | 4.24 | 4325.4717 | 4.38 | 17380 | 3.68 | 4722.8261 | 3.55
|  | 1617.3913 | 29.488 | nom | 14000 | 6.79 | 2061.8557 | 154.6263 | 14000 | 6.21 | 2254.4283 | 236.4607 | 14000 | 5.63 | 2486.6785 | 269.1167 | 14000 | 5.05 | 2772.2772 | 313.4479 | 14000 | 4.57 | 3063.4573 | 369.2674 | 14000 | 4.06 | 3448.2759 | 455.6032
|  |  | 23.479 | mid | 11200 | 7.26 | 1542.6997 | 0 | 11200 | 6.67 | 1679.1604 | 0 | 11200 | 6.14 | 1824.1042 | 0 | 11200 | 5.58 | 2007.1685 | 0 | 11200 | 4.92 | 2276.4228 | 0 | 11200 | 4.26 | 2629.108 | 0
|  |  | 183.0596 | min | 7140 | 10.46 | 682.6004 | 0 | 6580 | 6.84 | 961.9883 | 0 | 6200 | 6.01 | 1031.614 | 0 | 5760 | 5.16 | 1116.2791 | 0 | 5480 | 4.38 | 1251.1416 | 0 | 5140 | 3.55 | 1447.8873 | 0
| 19 |  | 10.5635 | max | 20580 | 6.87 | 2995.6332 | 12.23 | 20280 | 6.2 | 3270.9677 | 7.42 | 19980 | 5.55 | 3600 | 6.33 | 19700 | 4.86 | 4053.4979 | 5.23 | 18820 | 4.32 | 4356.4815 | 4.39 | 17840 | 3.74 | 4770.0535 | 3.5
|  | 1293.913 | 28.4647 | nom | 14000 | 7.22 | 1939.0582 | 105.7983 | 14000 | 6.53 | 2143.951 | 174.3818 | 14000 | 5.84 | 2397.2603 | 204.4096 | 14000 | 5.15 | 2718.4466 | 247.4021 | 14000 | 4.66 | 3004.2918 | 294.741 | 14000 | 4.13 | 3389.8305 | 369.6894
|  |  | 18.4343 | mid | 11200 | 7.68 | 1458.3333 | 0 | 11200 | 7.01 | 1597.7175 | 0 | 11200 | 6.37 | 1758.2418 | 0 | 11200 | 5.69 | 1968.3656 | 0 | 11200 | 5.01 | 2235.5289 | 0 | 11200 | 4.33 | 2586.6051 | 0
|  |  | 122.4894 | min | 7220 | 12.23 | 590.3516 | 0 | 6640 | 7.42 | 894.8787 | 0 | 6300 | 6.33 | 995.2607 | 0 | 5880 | 5.23 | 1124.283 | 0 | 5540 | 4.39 | 1261.959 | 0 | 5120 | 3.5 | 1462.8571 | 0
| 20 |  | 12.5721 | max | 21100 | 7.25 | 2910.3448 | 14 | 20800 | 6.5 | 3200 | 8 | 20500 | 5.75 | 3565.2174 | 6.65 | 20200 | 4.95 | 4080.8081 | 5.3 | 19300 | 4.4 | 4386.3636 | 4.4 | 18300 | 3.8 | 4815.7895 | 3.45
|  | 970.4348 | 27.3799 | nom | 14000 | 7.65 | 1830.0654 | 69.3168 | 14000 | 6.85 | 2043.7956 | 121.3043 | 14000 | 6.05 | 2314.0496 | 145.93 | 14000 | 5.25 | 2666.6667 | 183.1009 | 14000 | 4.75 | 2947.3684 | 220.5534 | 14000 | 4.2 | 3333.3333 | 281.2854
|  |  | 13.5588 | mid | 11200 | 8.1 | 1382.716 | 0 | 11200 | 7.35 | 1523.8095 | 0 | 11200 | 6.6 | 1696.9697 | 0 | 11200 | 5.8 | 1931.0345 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.4 | 2545.4545 | 0
|  |  | 77.1897 | min | 7300 | 14 | 521.4286 | 0 | 6700 | 8 | 837.5 | 0 | 6400 | 6.65 | 962.406 | 0 | 6000 | 5.3 | 1132.0755 | 0 | 5600 | 4.4 | 1272.7273 | 0 | 5100 | 3.45 | 1478.2609 | 0

## Sheet1
Indoor Temp. = | 21 | [10 empty] | (a) Indoor Temp. 20C for 6 hours 21C for 18 hours
Outdoor Temp. C | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | Outdoor Temp. C | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
PI (W) | 51872 | 46922 | 42134 | 37487 | 33235 | 29351 | 25809 | 22463 | 20029 | 17959 | 16183 | PI (W) | 50728 | 45810 | 41064 | 36486 | 32311 | 28488 | 24976 | 21675 | 19363 | 17390 | 15687
PO (W) | 154949 | 147570 | 140192 | 132813 | 125435 | 118056 | 110678 | 103299 | 95921 | 88542 | 81164 | PO (W) | 153104 | 145726 | 128347 | 130969 | 123590 | 116212 | 108833 | 101455 | 94076 | 86698 | 79319
COP | 2.9871 | 3.145 | 3.3273 | 3.5429 | 3.7742 | 4.0222 | 4.2883 | 4.5986 | 4.7891 | 4.9302 | 5.0154 | COP | 3.0181 | 3.1811 | 3.1255 | 3.5896 | 3.825 | 4.0793 | 4.3575 | 4.6807 | 4.8585 | 4.9855 | 5.0564
PI change (%) |  | 90.4573 | 81.2269 | 72.2683 | 64.0712 | 56.5835 | 49.7552 | 43.3047 | 38.6124 | 34.6218 | 31.1979 | PI change (%) |  | 88.3135 | 79.1641 | 70.3385 | 62.2899 | 54.9198 | 48.1493 | 41.7855 | 37.3284 | 33.5248 | 30.2417
PO change (%) |  | 95.2378 | 90.4762 | 85.714 | 80.9524 | 76.1902 | 71.4287 | 66.6665 | 61.9049 | 57.1427 | 52.3811 | PO change (%) |  | 94.0477 | 82.8318 | 84.5239 | 79.7617 | 75.0002 | 70.2379 | 65.4764 | 60.7142 | 55.9526 | 51.1904
Indoor Temp. = | 21 0: 20 | (b) Indoor Temp. 19C for 4 hours, 20C for 2 hours 21C for 18 hours
Outdoor Temp. C | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | Outdoor Temp. C | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
PI (W) | 47298 | 42476 | 37852 | 33484 | 29539 | 25901 | 22479 | 19309 | 17364 | 15682 | 14202 | PI (W) | 50012 | 45119 | 40445 | 35929 | 31779 | 27969 | 24483 | 21218 | 18968 | 17044 | 15378
PO (W) | 147570 | 140192 | 132813 | 125435 | 118056 | 110678 | 103299 | 95921 | 88542 | 81164 | 73785 | PO (W) | 151874 | 144496 | 137117 | 129739 | 122360 | 114982 | 107603 | 100225 | 92846 | 85468 | 78089
COP | 3.12 | 3.3005 | 3.5087 | 3.7461 | 3.9966 | 4.2731 | 4.5954 | 4.9677 | 5.0992 | 5.1756 | 5.1954 | COP | 3.0368 | 3.2026 | 3.3902 | 3.611 | 3.8503 | 4.1111 | 4.395 | 4.7236 | 4.8949 | 5.0146 | 5.078
PI change (%) |  | 89.8051 | 80.0288 | 70.7937 | 62.453 | 54.7613 | 47.5263 | 40.8241 | 36.7119 | 33.1557 | 30.0266 | PI change (%) |  | 86.9814 | 77.9708 | 69.2647 | 61.2643 | 53.9193 | 47.1989 | 40.9045 | 36.5669 | 32.8578 | 29.6461
PO change (%) |  | 95.0003 | 90 | 85.0003 | 80 | 75.0003 | 70 | 65.0003 | 60 | 55.0003 | 50 | PO change (%) |  | 93.2539 | 88.4917 | 83.7301 | 78.9679 | 74.2064 | 69.4441 | 64.6826 | 59.9204 | 55.1588 | 50.3966
Indoor Temp. = | 20 0: 19 | (c)Indoor Temp. 18C for 2 hours, 19C for 2 hours, 20C for 2 hours 21C for 18 hours
Outdoor Temp. C | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | Outdoor Temp. C | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
PI (W) | 42997 | 38328 | 34143 | 30142 | 26345 | 22788 | 19522 | 16568 | 14997 | 13605 | 12349 | PI (W) | 49687 | 44838 | 40208 | 35686 | 31537 | 27737 | 24266 | 21019 | 18792 | 16885 | 15234
PO (W) | 140192 | 132813 | 125435 | 118056 | 110678 | 103299 | 95921 | 88542 | 81164 | 73785 | 66407 | PO (W) | 151260 | 143881 | 136502 | 129124 | 121745 | 114367 | 103988 | 99610 | 92231 | 84853 | 77474
COP | 3.2605 | 3.4652 | 3.6738 | 3.9167 | 4.2011 | 4.533 | 4.9135 | 5.3442 | 5.412 | 5.4234 | 5.3775 | COP | 3.0443 | 3.2089 | 3.3949 | 3.6183 | 3.8604 | 4.1233 | 4.2853 | 4.739 | 4.908 | 5.0253 | 5.0856
PI change (%) |  | 89.1411 | 79.4079 | 70.1026 | 61.2717 | 52.999 | 45.4032 | 38.5329 | 34.8792 | 31.6417 | 28.7206 | PI change (%) |  | 86.4397 | 77.5139 | 68.7963 | 60.7977 | 53.472 | 46.7805 | 40.5209 | 36.2276 | 32.5513 | 29.3684
PO change (%) |  | 94.7365 | 89.4737 | 84.2102 | 78.9474 | 73.6839 | 68.4212 | 63.1577 | 57.8949 | 52.6314 | 47.3686 | PO change (%) |  | 92.857 | 88.0948 | 83.3332 | 78.571 | 73.8094 | 67.1111 | 64.2857 | 59.5235 | 54.7619 | 49.9997
Indoor Temp. = | 19 0: 18 | Differences between 21C and (a)
Outdoor Temp. C | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | Outdoor Temp. C | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
PI (W) | 39099 | 34962 | 31294 | 27221 | 23442 | 20002 | 16916 | 14179 | 12883 | 11704 | 10614 | PI Reduction (W) | 1144 | 1112 | 1070 | 1001 | 924 | 863 | 833 | 788 | 666 | 569 | 496
PO (W) | 132813 | 125435 | 118056 | 110678 | 103299 | 95921 | 88542 | 81164 | 73785 | 66407 | 59028 | PO Reduction (W) | 1845 | 1844 | 11845 | 1844 | 1845 | 1844 | 1845 | 1844 | 1845 | 1844 | 1845
COP | 3.3968 | 3.5878 | 3.7725 | 4.0659 | 4.4066 | 4.7956 | 5.2342 | 5.7242 | 5.7273 | 5.6739 | 5.5613 | COP Increase | 0.030995 | 0.036089 | -0.20175 | 0.04666 | 0.050829 | 0.057118 | 0.069154 | 0.082109 | 0.069439 | 0.055279 | 0.040966
PI change (%) |  | 89.4192 | 80.0379 | 69.6207 | 59.9555 | 51.1573 | 43.2645 | 36.2644 | 32.9497 | 29.9343 | 27.1465 | PI Reduction (%) | 2.2054 | 2.3699 | 2.5395 | 2.6703 | 2.7802 | 2.9403 | 3.2276 | 3.508 | 3.3252 | 3.1683 | 3.0649
PO change (%) |  | 94.4448 | 88.8889 | 83.3337 | 77.7778 | 72.2226 | 66.6667 | 61.1115 | 55.5556 | 50.0004 | 44.4444 | PO Reduction (%) | 1.1907 | 1.2496 | 8.4491 | 1.3884 | 1.4709 | 1.562 | 1.667 | 1.7851 | 1.9235 | 2.0826 | 2.2732
Differences between 21C and 20C | [11 empty] | Differences between 21C and (b)
Outdoor Temp. C | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | Outdoor Temp. C | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
PI Reduction (W) | 4574 | 4446 | 4282 | 4003 | 3696 | 3450 | 3330 | 3154 | 2665 | 2277 | 1981 | PI Reduction (W) | 1860 | 1803 | 1689 | 1558 | 1456 | 1382 | 1326 | 1245 | 1061 | 915 | 805
PO Reduction (W) | 7379 | 7378 | 7379 | 7378 | 7379 | 7378 | 7379 | 7378 | 7379 | 7378 | 7379 | PO Reduction (W) | 3075 | 3074 | 3075 | 3074 | 3075 | 3074 | 3075 | 3074 | 3075 | 3074 | 3075
COP Increase | 0.13286 | 0.15549 | 0.18146 | 0.20321 | 0.22243 | 0.2509 | 0.30701 | 0.36905 | 0.31006 | 0.24539 | 0.18001 | COP Increase | 0.04961 | 0.057547 | 0.06292 | 0.068075 | 0.076158 | 0.088838 | 0.10666 | 0.12495 | 0.10577 | 0.084321 | 0.062582
PI Reduction (%) | 8.8179 | 9.4753 | 10.1628 | 10.6784 | 11.1208 | 11.7543 | 12.9025 | 14.0409 | 13.3057 | 12.6789 | 12.2412 | PI Reduction (%) | 3.5857 | 3.8425 | 4.0086 | 4.1561 | 4.3809 | 4.7085 | 5.1377 | 5.5424 | 5.2973 | 5.0949 | 4.9744
PO Reduction (%) | 4.7622 | 4.9997 | 5.2635 | 5.5552 | 5.8827 | 6.2496 | 6.6671 | 7.1424 | 7.6928 | 8.3328 | 9.0915 | PO Reduction (%) | 1.9845 | 2.0831 | 2.1934 | 2.3145 | 2.4515 | 2.6038 | 2.7783 | 2.9758 | 3.2058 | 3.4718 | 3.7886
Differences between 21C and 19C | [11 empty] | Differences between 21C and (c)
Outdoor Temp. C | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | Outdoor Temp. C | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
PI Reduction (W) | 8875 | 8594 | 7991 | 7345 | 6890 | 6563 | 6287 | 5895 | 5032 | 4354 | 3834 | PI Reduction (W) | 2185 | 2084 | 1926 | 1801 | 1698 | 1614 | 1543 | 1444 | 1237 | 1074 | 949
PO Reduction (W) | 14757 | 14757 | 14757 | 14757 | 14757 | 14757 | 14757 | 14757 | 14757 | 14757 | 14757 | PO Reduction (W) | 3689 | 3689 | 3690 | 3689 | 3690 | 3689 | 6690 | 3689 | 3690 | 3689 | 3690
COP Increase | 0.27337 | 0.32016 | 0.34652 | 0.37375 | 0.42692 | 0.51083 | 0.62513 | 0.74553 | 0.62291 | 0.49314 | 0.36213 | COP Increase | 0.057116 | 0.063901 | 0.067607 | 0.07543 | 0.086202 | 0.10105 | -0.0030115 | 0.14042 | 0.11889 | 0.095118 | 0.070211
PI Reduction (%) | 17.1094 | 18.3155 | 18.9657 | 19.5935 | 20.7312 | 22.3604 | 24.3597 | 26.2432 | 25.1236 | 24.2441 | 23.6915 | PI Reduction (%) | 4.2123 | 4.4414 | 4.5711 | 4.8043 | 5.1091 | 5.499 | 5.9785 | 6.4283 | 6.176 | 5.9803 | 5.8642
PO Reduction (%) | 9.5238 | 10 | 10.5263 | 11.1111 | 11.7647 | 12.5 | 13.3333 | 14.2857 | 15.3845 | 16.6667 | 18.1817 | PO Reduction (%) | 2.3808 | 2.4998 | 2.6321 | 2.7776 | 2.9418 | 3.1248 | 6.0446 | 3.5712 | 3.8469 | 4.1664 | 4.5464
Differences between 21C and 18C
Outdoor Temp. C | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
PI Reduction (W) | 12773 | 11960 | 10840 | 10266 | 9793 | 9349 | 8893 | 8284 | 7146 | 6255 | 5569
PO Reduction (W) | 22136 | 22135 | 22136 | 22135 | 22136 | 22135 | 22136 | 22135 | 22136 | 22135 | 22136
COP Increase | 0.4097 | 0.44275 | 0.44519 | 0.523 | 0.63239 | 0.77336 | 0.94587 | 1.1256 | 0.93821 | 0.74364 | 0.54595
PI Reduction (%) | 24.6241 | 25.4891 | 25.7274 | 27.3855 | 29.4659 | 31.8524 | 34.457 | 36.8784 | 35.6783 | 34.8293 | 34.4127
PO Reduction (%) | 14.286 | 14.9997 | 15.7898 | 16.6663 | 17.6474 | 18.7496 | 20.0004 | 21.4281 | 23.0773 | 24.9994 | 27.2732