## Notes
Modelling Tool for Home Heating System with 14kW Mitsubishi Ecodan ASHP Models PUZ-HWM140VHA(-BS) and PUZ-HWM140YHA(-BS).
The initial data used in the accompanying tables was obtained from document Mitsubishi Ecodan Data Book Vol.5.3 R32, the Performance Data
having been obtained from testing carried out to the requirements of EN14511-2013.
How to use the Modelling Tool.
1. Open the Initial Data sheet and set the operating parameters for the particular system under investigation. (The cells that require setting are highlighted in green).
a) In cell C1 set the the Heat Demand as derived from Heat Loss calculations carried out at the specified Ambient Air Temperature (cell E1).
b) In cell H1 set a desired Indoor Temperature.
c) In cell P1 set the value for the Total Heating Elements Output. (If the required information is not available, measure the size and type of all radiators etc. and
obtain the data from a suitable source).
Once the initial operating parameters have been set the table below will show the anticipated operating characteristics for the system.
Of particular interest may be the following:-
Column B shows various Ambient Air Temperatures.
Column C shows the corresponding calculated Heating Demand.
Column D shows the following:-
Calculated Coefficient of Performance (COP).
Calculated Leaving (Flow) Water Temperature (LWT).
Calculated Duty Cycle (Duty (%)). At higher ambient air temperatures the ASHP will not operate continuoiusly, but will cycle.
Calculated Power Input (PI). The electrical energy drawn from the power supply.
Using the Initial Data sheet it should be possible to compare the performance of a working heating system against the manufacturers specified operating criteria.
Any large discrepancies should become obvious and may lead to further investigation becoming necessary.
It will also be possible to carry out 'what if' scenarious, to investigate the effect of possible improvements that could be made to improve overall efficiency.
To see what effect lowering the Heating Demand by improved insulation would have on system operation.
To see what effect varying the Indoor Temperature would have on system operation.
To see what effect installing larger Heat Emitters would have on system operation.
Using the Playroom sheet will allow more detailed investigation of system operation over specific 24 hours periods.
The Play Area table allows hourly variations to be made to the Outdoor Temperature and Indoor Temperature experienced by the system.
This in turn allows the calculation of the following parameters:-
COP
LWT
PI
Duty Cycle %
Energy Supply
Energy Demand
Energy Balance
It should therefore be possible to see the effects of making changes to the desired indoor temperature throughout the day.
The Lookup Table contains the data necessary for the calculations to be made and should not be changed.
The Data for Graph table contains the data necessary for the production of the graph and should not be changed.
The Pretty Graph shows the calculated Input Power, Output Power and COP, for Indoor Temperatures of 19C, 21C and 23C.
The Detailed Data sheet contains 6 tables which calculate the various parameters at Indoor Temperatures from 18C to 23C.
The data within the tables has been extrapolated from the manufaturers data, to provide ambient air increments of 1C.
Cells containing Bold text or highlighted in Yellow contain formulas, and should not be changed.
Two further parameters have been added to the Detailed Data sheet, Water Temp Hyst. (C.) in cell C2 and Buffer Tank Effect (%) in cell N2.
The Water Temp Hyst. (C.) allows investigation of the possible effect of changing the point at which the ASHP would start and stop operating as the water flowing heats up and cools down.
The Buffer Tank Effect (%) allows investigation of the possible effect of changing of flow rates as pumps stop and start and valves open and close
Both of these paramaters have been set at zero for the moment.
I have now added Heat Pump DT setting and also calculated flow rate on the Initial Data sheet.
The modelling tool deals solely with heating demand and makes no allowance for hot water production and usage.
It is also impossible to take any account of changes in operation due to solar gain, human activity, wind chill and rain effect.

## Initial Data
Heating Demand (W) |  | 8000 | at Amb. | -3.2 | Indoor Temp. |  | 21 |  | Total Heating Elements Output (W) | [5 empty] | 24000 | at Delta T of 50C |  |  |  | Heat Pump DT = |  |  | 5
LWT |  |  |  |  | 25 |  |  |  | 35 |  |  |  | 40 |  |  |  | 45 |  |  |  | 50 |  |  |  | 55 |  |  |  | 60
Outdoor air temperature[℃] |  | Heating Demand | COP | CL | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP
|  |  | LWT |  |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI
|  | Flow lpm | COP: Duty (%)
Heat Out | bar: COP
14W | -10 |  | 2.0318 | max | 14600 | 2.4 | 6083.3333 | 2.7929 | 14400 | 2.25 | 6400 | 2.6281 | 14200 | 2.1 | 6761.9048 | 2.465 | 14000 | 1.9 | 7368.4211 | 2.2532 | 14000 | 1.85 | 7567.5676 | 2.0062 | 14000 | 1.75 | 8000 | 1.7508 | 14000 | 1.55 | 9032.2581 | 1.55
|  | 10247.9339 | 49.4825 | nom | 14000 | 2.8 | 5000 | 3669.3121 | 14000 | 2.5 | 5600 | 3899.3017 | 14000 | 2.2 | 6363.6364 | 4157.3868 | 14000 | 1.9 | 7368.4211 | 4548.2097 | 14000 | 1.85 | 7567.5676 | 5108.0403 | 14000 | 1.75 | 8000 | 5853.198 | 14000 | 1.55 | 9032.2581 | 6611.5702
|  | 30.8131 | 100 | mid | 11200 | 2.85 | 3929.8246 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.1 | 5333.3333 | 1 | 11200 | 1.85 | 6054.0541 | 1 | 11200 | 1.65 | 6787.8788 | 1
|  | 10260.7606 | 5050.1023 | min | 6200 | 2.55 | 2431.3725 | 0.80959 | 5900 | 2.3 | 2565.2174 | 0.82036 | 5600 | 2.05 | 2731.7073 | 0.82999 | 5300 | 1.75 | 3028.5714 | 0.83863 | 4600 | 1.45 | 3172.4138 | 0.85575 | 4000 | 1.1 | 3636.3636 | 0.86777 | 3900 | 0.85 | 4588.2353 | 0.86958
| -7 |  | 2.2088 | max | 16100 | 2.7 | 5962.963 | 3.3775 | 15900 | 2.5 | 6360 | 2.7975 | 15700 | 2.3 | 6826.087 | 2.561 | 15500 | 2.1 | 7380.9524 | 2.3245 | 14700 | 2.05 | 7170.7317 | 2.0954 | 14000 | 1.95 | 7179.4872 | 1.872 | 14000 | 1.75 | 8000 | 1.663
|  | 9256.1983 | 47.5259 | nom | 14000 | 3.05 | 4590.1639 | 2740.5778 | 14000 | 2.8 | 5000 | 3308.7149 | 14000 | 2.55 | 5490.1961 | 3614.2634 | 14000 | 2.3 | 6086.9565 | 3981.9863 | 14000 | 2.15 | 6511.6279 | 4417.4122 | 14000 | 1.95 | 7179.4872 | 4944.489 | 14000 | 1.7 | 8235.2941 | 5566.1281
|  | 27.8713 | 100 | mid | 11200 | 3.25 | 3446.1538 | 1 | 11200 | 3 | 3733.3333 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1 | 11200 | 2.1 | 5333.3333 | 1 | 11200 | 1.9 | 5894.7368 | 1
|  | 9281.1378 | 4201.9505 | min | 5100 | 3.65 | 1397.2603 | 0.68134 | 4000 | 2.25 | 1777.7778 | 0.73003 | 4000 | 2.05 | 1951.2195 | 0.73003 | 4000 | 1.85 | 2162.1622 | 0.73003 | 3600 | 1.5 | 2400 | 0.74424 | 3100 | 1.15 | 2695.6522 | 0.76002 | 3000 | 0.9 | 3333.3333 | 0.76295
| 2 |  | 2.981 | max | 16500 | 3.25 | 5076.9231 | 4.1331 | 16300 | 3 | 5433.3333 | 3.6016 | 16000 | 2.75 | 5818.1818 | 3.1122 | 15800 | 2.5 | 6320 | 2.6189 | 15100 | 2.45 | 6163.2653 | 2.2909 | 14300 | 2.35 | 6085.1064 | 1.9351 | 14300 | 2.1 | 6809.5238 | 1.6016
|  | 6280.9917 | 41.3294 | nom | 14000 | 3.4 | 4117.6471 | 1519.6744 | 14000 | 3.15 | 4444.4444 | 1743.9455 | 14000 | 2.9 | 4827.5862 | 2018.2088 | 14000 | 2.65 | 5283.0189 | 2398.3194 | 14000 | 2.55 | 5490.1961 | 2741.7225 | 14000 | 2.4 | 5833.3333 | 3245.7826 | 14000 | 2.1 | 6666.6667 | 3921.6436
|  | 18.9717 | 100 | mid | 11200 | 3.65 | 3068.4932 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 3.15 | 3555.5556 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.3 | 4869.5652 | 1
|  | 6317.5874 | 2119.2732 | min | 5600 | 4.2 | 1333.3333 | 0.12161 | 5100 | 3.65 | 1397.2603 | 0.19361 | 4700 | 3.1 | 1516.129 | 0.24323 | 4200 | 2.5 | 1680 | 0.29728 | 3700 | 2.05 | 1804.878 | 0.34413 | 3200 | 1.55 | 2064.5161 | 0.38512 | 3100 | 1.15 | 2695.6522 | 0.39272
| 7 |  | 4.0215 | max | 16800 | 4.7 | 3574.4681 | 6.5742 | 16600 | 4.25 | 3905.8824 | 4.4714 | 16400 | 3.8 | 4315.7895 | 3.6052 | 16100 | 3.3 | 4878.7879 | 2.7821 | 15400 | 2.9 | 5310.3448 | 2.3176 | 14600 | 2.5 | 5840 | 1.8412 | 14600 | 2.5 | 5840 | 1.447
|  | 4628.0992 | 37.5967 | nom | 14000 | 4.9 | 2857.1429 | 703.9802 | 14000 | 4.45 | 3146.0674 | 1035.0436 | 14000 | 4 | 3500 | 1283.7343 | 14000 | 3.5 | 4000 | 1663.5475 | 14000 | 3.15 | 4444.4444 | 1996.9626 | 14000 | 2.75 | 5090.9091 | 2513.6405 | 14000 | 2.5 | 5600 | 3198.3138
|  | 14.0597 | 100 | mid | 11200 | 5.25 | 2133.3333 | 1 | 11200 | 4.8 | 2333.3333 | 1 | 11200 | 4.35 | 2574.7126 | 1 | 11200 | 3.85 | 2909.0909 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.5 | 4480 | 1
|  | 4681.8738 | 1164.1983 | min | 4500 | 6.6 | 681.8182 | 0.019119 | 4200 | 4.45 | 943.8202 | 0.061157 | 3700 | 3.5 | 1057.1429 | 0.12375 | 3200 | 2.55 | 1254.902 | 0.17851 | 2700 | 2 | 1350 | 0.22684 | 2200 | 1.45 | 1517.2414 | 0.26979 | 2150 | 1.05 | 2047.619 | 0.27382
| 12 |  | 4.9366 | max | 17100 | 5.25 | 3257.1429 | 5.15 | 16800 | 4.9 | 3428.5714 | 4.9 | 16600 | 4.45 | 3730.3371 | 4.65 | 16400 | 4.2 | 3904.7619 | 4.35 | 15600 | 3.7 | 4216.2162 | 3.7 | 14800 | 3.2 | 4625 | 3.05 | 14800 | 2.7 | 5481.4815 | 2.5
|  | 2975.2066 | 33.5349 | nom | 14000 | 5.5 | 2545.4545 | 577.71 | 14000 | 5.15 | 2718.4466 | 607.185 | 14000 | 4.8 | 2916.6667 | 639.8294 | 14000 | 4.45 | 3146.0674 | 683.9555 | 14000 | 4 | 3500 | 804.1099 | 14000 | 3.5 | 4000 | 975.4776 | 14000 | 3 | 4666.6667 | 1190.0826
|  | 8.9373 | 47.5379 | mid | 11200 | 5.85 | 1914.5299 | 0 | 11200 | 5.55 | 2018.018 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.9 | 2285.7143 | 0 | 11200 | 4.3 | 2604.6512 | 0 | 11200 | 3.7 | 3027.027 | 0 | 11200 | 3 | 3733.3333 | 0
|  | 2976.128 | 602.8666 | min | 6600 | 5.15 | 1281.5534 | 0 | 6200 | 4.9 | 1265.3061 | 0 | 5800 | 4.65 | 1247.3118 | 0 | 5400 | 4.35 | 1241.3793 | 0 | 5200 | 3.7 | 1405.4054 | 0 | 5000 | 3.05 | 1639.3443 | 0 | 4900 | 2.5 | 1960 | 0
| 15 |  | 5.1208 | max | 18500 | 5.35 | 3457.9439 | 5.15 | 18200 | 5 | 3640 | 5.1 | 17900 | 4.75 | 3768.4211 | 5.05 | 17700 | 4.5 | 3933.3333 | 4.95 | 16900 | 4 | 4225 | 4.35 | 16000 | 3.5 | 4571.4286 | 3.7 | 16000 | 3 | 5333.3333 | 3.15
|  | 1983.4711 | 30.8461 | nom | 14000 | 5.5 | 2545.4545 | 385.14 | 14000 | 5.25 | 2666.6667 | 388.9159 | 14000 | 5 | 2800 | 392.7665 | 14000 | 4.75 | 2947.3684 | 400.7012 | 14000 | 4.3 | 3255.814 | 455.9704 | 14000 | 3.85 | 3636.3636 | 536.0733 | 14000 | 3.4 | 4117.6471 | 629.6734
|  | 5.9565 | 30.0176 | mid | 11200 | 6 | 1866.6667 | 0 | 11200 | 5.65 | 1982.3009 | 0 | 11200 | 5.45 | 2055.0459 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.65 | 2408.6022 | 0 | 11200 | 4.05 | 2765.4321 | 0 | 11200 | 3.4 | 3294.1176 | 0
|  | 1983.5169 | 387.3474 | min | 6900 | 5.15 | 1339.8058 | 0 | 6400 | 5.1 | 1254.902 | 0 | 5900 | 5.05 | 1168.3168 | 0 | 5400 | 4.95 | 1090.9091 | 0 | 5300 | 4.35 | 1218.3908 | 0 | 5200 | 3.7 | 1405.4054 | 0 | 5100 | 3.15 | 1619.0476 | 0
| 20 |  | 13.7892 | max | 21100 | 7.25 | 2910.3448 | 14 | 20800 | 6.5 | 3200 | 8 | 20500 | 5.75 | 3565.2174 | 6.65 | 20200 | 4.95 | 4080.8081 | 5.3 | 19300 | 4.4 | 4386.3636 | 4.4 | 18300 | 3.8 | 4815.7895 | 3.45 | 18300 | 3.25 | 5630.7692 | 2.7
|  | 330.5785 | 25.3513 | nom | 14000 | 7.65 | 1830.0654 | 23.6128 | 14000 | 6.85 | 2043.7956 | 41.3223 | 14000 | 6.05 | 2314.0496 | 49.7111 | 14000 | 5.25 | 2666.6667 | 62.3733 | 14000 | 4.75 | 2947.3684 | 75.1315 | 14000 | 4.2 | 3333.3333 | 95.8199 | 14000 | 3.7 | 3783.7838 | 122.4365
|  | 1.0035 | 4.5416 | mid | 11200 | 8.1 | 1382.716 | 0 | 11200 | 7.35 | 1523.8095 | 0 | 11200 | 6.6 | 1696.9697 | 0 | 11200 | 5.8 | 1931.0345 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.4 | 2545.4545 | 0 | 11200 | 3.7 | 3027.027 | 0
|  | 334.1803 | 24.2349 | min | 7300 | 14 | 521.4286 | 0 | 6700 | 8 | 837.5 | 0 | 6400 | 6.65 | 962.406 | 0 | 6000 | 5.3 | 1132.0755 | 0 | 5600 | 4.4 | 1272.7273 | 0 | 5100 | 3.45 | 1478.2609 | 0 | 5000 | 2.7 | 1851.8519 | 0
Abbreviations:
LWT: Leaving water temperature (°C )
CL: Capacity level
CAP: Total heating capacity (W)
PI: Power input (W)

## Playroom
Initial Conditions
Heating Demand (W) = |  | 8000
Heating Elements (W) = |  | 24000
Play Area.
Hour |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Indoor Temp. (18 to 23) |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
Outside Temp (-10 to 20) |  | 7 | 6 | 5 | 5 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 15 | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | Ave COP
COP |  | 4.0215 | 3.7782 | 3.5541 | 3.5541 | 3.5541 | 3.7782 | 4.0215 | 4.2532 | 4.4182 | 4.6978 | 4.8489 | 4.9366 | 5.0095 | 5.071 | 5.1208 | 5.1208 | 5.1208 | 5.071 | 5.0095 | 4.9366 | 4.8489 | 4.6978 | 4.4182 | 4.2532 | 4.2649
LWT |  | 37.5967 | 38.365 | 39.1216 | 39.1216 | 39.1216 | 38.365 | 37.5967 | 36.8156 | 36.0204 | 35.2099 | 34.3821 | 33.5349 | 32.6657 | 31.771 | 30.8461 | 30.8461 | 30.8461 | 31.771 | 32.6657 | 33.5349 | 34.3821 | 35.2099 | 36.0204 | 36.8156 | Totals
PI (W/h) |  | 1164.1983 | 1324.3066 | 1495.94 | 1495.94 | 1495.94 | 1324.3066 | 1164.1983 | 1018.9944 | 899.4849 | 774.5062 | 682.3551 | 602.8666 | 528.0507 | 456.3819 | 387.3474 | 387.3474 | 387.3474 | 456.3819 | 528.0507 | 602.8666 | 682.3551 | 774.5062 | 899.4849 | 1018.9944 | 20552.1517
Duty Cycle % |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80.857 | 67.5712 | 56.7665 | 47.5379 | 41.5311 | 35.6885 | 30.0176 | 30.0176 | 30.0176 | 35.6885 | 41.5311 | 47.5379 | 56.7665 | 67.5712 | 80.857 | 100
Energy Supply (W/h) |  | 4681.8738 | 5003.5102 | 5316.6968 | 5316.6968 | 5316.6968 | 5003.5102 | 4681.8738 | 4333.9472 | 3974.0684 | 3638.4404 | 3308.6922 | 2976.128 | 2645.2499 | 2314.3152 | 1983.5169 | 1983.5169 | 1983.5169 | 2314.3152 | 2645.2499 | 2976.128 | 3308.6922 | 3638.4404 | 3974.0684 | 4333.9472 | 87653.0922
Energy Demand (W/h) |  | 4628.0992 | 4958.6777 | 5289.2562 | 5289.2562 | 5289.2562 | 4958.6777 | 4628.0992 | 4297.5207 | 3966.9421 | 3636.3636 | 3305.7851 | 2975.2066 | 2644.6281 | 2314.0496 | 1983.4711 | 1983.4711 | 1983.4711 | 2314.0496 | 2644.6281 | 2975.2066 | 3305.7851 | 3636.3636 | 3966.9421 | 4297.5207 | 87272.7273
Energy Balance Wh |  | 53.7747 | 44.8325 | 27.4406 | 27.4406 | 27.4406 | 44.8325 | 53.7747 | 36.4266 | 7.1263 | 2.0768 | 2.9071 | 0.92142 | 0.62185 | 0.26566 | 0.045847 | 0.045847 | 0.045847 | 0.26566 | 0.62185 | 0.92142 | 2.9071 | 2.0768 | 7.1263 | 36.4266 | 380.3649
Lookup Table.
|  | Indoor | 18 |  |  |  | 19 |  |  |  | 20 |  |  |  | 21 |  |  |  | 22 |  |  |  | 23
|  | Amb. | COP | LWT | PI | Duty % | COP | LWT | PI | Duty % | COP | LWT | PI | Duty % | COP | LWT | PI | Duty % | COP | LWT | PI | Duty % | COP | LWT | PI | Duty %
|  | -10 | 2.0292 | 47.5259 | 4578.029 | 100 | 2.0301 | 48.1832 | 4737.7969 | 100 | 2.031 | 48.8354 | 4895.1503 | 100 | 2.0318 | 49.4825 | 5050.1023 | 100 | 2.0325 | 50.1249 | 5207.022 | 100 | 2.033 | 50.7626 | 5377.7513 | 100
|  | -9 | 2.0886 | 46.863 | 4287.3832 | 100 | 2.0893 | 47.5259 | 4444.8975 | 100 | 2.0907 | 48.1832 | 4598.9737 | 100 | 2.0926 | 48.8354 | 4749.6138 | 100 | 2.095 | 49.4825 | 4896.8309 | 100 | 2.098 | 50.1249 | 5044.0405 | 100 | 0
|  | -8 | 2.1484 | 46.1945 | 4010.4045 | 100 | 2.1482 | 46.863 | 4167.1991 | 100 | 2.1492 | 47.5259 | 4319.8007 | 100 | 2.1512 | 48.1832 | 4468.1864 | 100 | 2.1543 | 48.8354 | 4612.3499 | 100 | 2.1584 | 49.4825 | 4752.2987 | 100
|  | -7 | 2.2096 | 45.5201 | 3744.9032 | 100 | 2.2077 | 46.1945 | 3901.9869 | 100 | 2.2075 | 46.863 | 4054.3557 | 100 | 2.2088 | 47.5259 | 4201.9505 | 100 | 2.2116 | 48.1832 | 4344.7348 | 100 | 2.216 | 48.8354 | 4482.6912 | 100
|  | -6 | 2.2692 | 44.8394 | 3497.4996 | 100 | 2.2645 | 45.5201 | 3653.9822 | 100 | 2.2614 | 46.1945 | 3808.9313 | 100 | 2.2602 | 46.863 | 3959.2021 | 100 | 2.2608 | 47.5259 | 4104.7123 | 100 | 2.2631 | 48.1832 | 4245.4035 | 100
|  | -5 | 2.3351 | 44.1521 | 3261.6583 | 100 | 2.326 | 44.8394 | 3412.1428 | 100 | 2.3194 | 45.5201 | 3567.2849 | 100 | 2.3152 | 46.1945 | 3720.1474 | 100 | 2.313 | 46.863 | 3868.3697 | 100 | 2.3128 | 47.5259 | 4011.8474 | 100
|  | -4 | 2.4106 | 43.4578 | 3025.8151 | 100 | 2.3961 | 44.1521 | 3179.055 | 100 | 2.383 | 44.8394 | 3330.7324 | 100 | 2.3744 | 45.5201 | 3484.5225 | 100 | 2.369 | 46.1945 | 3635.3463 | 100 | 2.3658 | 46.863 | 3781.5693 | 100
|  | -3 | 2.4981 | 42.7563 | 2790.0859 | 100 | 2.4768 | 43.4578 | 2945.9506 | 100 | 2.4574 | 44.1521 | 3100.3306 | 100 | 2.44 | 44.8394 | 3252.9997 | 100 | 2.4294 | 45.5201 | 3405.4323 | 100 | 2.4228 | 46.1945 | 3554.2646 | 100
|  | -2 | 2.5996 | 42.047 | 2554.948 | 100 | 2.5701 | 42.7563 | 2713.0473 | 100 | 2.5432 | 43.4578 | 2869.9044 | 100 | 2.5189 | 44.1521 | 3025.2148 | 100 | 2.4971 | 44.8394 | 3178.6999 | 100 | 2.4845 | 45.5201 | 3329.7742 | 100
|  | -1 | 2.7177 | 41.3294 | 2321.208 | 100 | 2.6785 | 42.047 | 2480.9045 | 100 | 2.6426 | 42.7563 | 2639.7652 | 100 | 2.61 | 43.4578 | 2797.4036 | 100 | 2.5806 | 44.1521 | 2953.4621 | 100 | 2.5543 | 44.8394 | 3107.6093 | 100
|  | 0 | 2.8551 | 40.6031 | 2089.9563 | 100 | 2.8046 | 41.3294 | 2250.3881 | 100 | 2.7581 | 42.047 | 2410.5472 | 100 | 2.7157 | 42.7563 | 2569.9643 | 100 | 2.6772 | 43.4578 | 2728.2011 | 100 | 2.6425 | 44.1521 | 2884.8484 | 100
|  | 1 | 3.0146 | 39.8674 | 1865.288 | 100 | 2.9511 | 40.6031 | 2022.6243 | 100 | 2.8923 | 41.3294 | 2183.1692 | 100 | 2.8384 | 42.047 | 2343.5987 | 100 | 2.7893 | 42.7563 | 2503.3953 | 100 | 2.7447 | 43.4578 | 2662.0718 | 100
|  | 2 | 3.199 | 39.1216 | 1659.5346 | 100 | 3.1209 | 39.8674 | 1801.8259 | 100 | 3.0482 | 40.6031 | 1958.7883 | 100 | 2.981 | 41.3294 | 2119.2732 | 100 | 2.9195 | 42.047 | 2279.8085 | 100 | 2.8634 | 42.7563 | 2439.8322 | 100
|  | 3 | 3.3954 | 38.365 | 1470.3862 | 100 | 3.3097 | 39.1216 | 1604.8789 | 100 | 3.2305 | 39.8674 | 1740.8614 | 100 | 3.1581 | 40.6031 | 1891.4087 | 100 | 3.0917 | 41.3294 | 2044.9374 | 100 | 3.0309 | 42.047 | 2197.8847 | 100
|  | 4 | 3.6104 | 37.5967 | 1293.6675 | 100 | 3.5158 | 38.365 | 1421.1775 | 100 | 3.4283 | 39.1216 | 1550.1325 | 100 | 3.3477 | 39.8674 | 1680.0537 | 100 | 3.2752 | 40.6031 | 1824.5579 | 100 | 3.209 | 41.3294 | 1971.6245 | 100
|  | 5 | 3.8485 | 36.8156 | 1127.8785 | 100 | 3.7407 | 37.5967 | 1249.7159 | 100 | 3.6436 | 38.365 | 1372.3316 | 100 | 3.5541 | 39.1216 | 1495.94 | 100 | 3.4719 | 39.8674 | 1620.0863 | 100 | 3.3988 | 40.6031 | 1758.9031 | 100
|  | 6 | 4.1137 | 36.0204 | 972.2657 | 100 | 3.9877 | 36.8156 | 1089.3277 | 100 | 3.8779 | 37.5967 | 1206.4627 | 100 | 3.7782 | 38.365 | 1324.3066 | 100 | 3.6865 | 39.1216 | 1442.7911 | 100 | 3.6024 | 39.8674 | 1561.4686 | 100
|  | 7 | 4.4101 | 35.2099 | 826.4697 | 87.0149 | 4.2623 | 36.0204 | 938.8475 | 100 | 4.1327 | 36.8156 | 1051.7814 | 100 | 4.0215 | 37.5967 | 1164.1983 | 100 | 3.9191 | 38.365 | 1277.4445 | 100 | 3.8249 | 39.1216 | 1391.0459 | 100
|  | 8 | 4.6494 | 34.3821 | 715.525 | 71.5573 | 4.506 | 35.2099 | 808.2615 | 79.3991 | 4.3747 | 36.0204 | 912.5011 | 88.1144 | 4.2532 | 36.8156 | 1018.9944 | 100 | 4.15 | 37.5967 | 1124.4159 | 100 | 4.0659 | 38.365 | 1227.9344 | 100
|  | 9 | 4.8336 | 33.5349 | 620.8551 | 58.9172 | 4.7159 | 34.3821 | 703.8052 | 65.839 | 4.6019 | 35.2099 | 790.969 | 73.0092 | 4.4182 | 36.0204 | 899.4849 | 80.857 | 4.3867 | 36.8156 | 985.2145 | 88.921 | 4.2872 | 37.5967 | 1085.9045 | 100
|  | 10 | 4.9558 | 32.6657 | 537.2484 | 48.2241 | 4.868 | 33.5349 | 614.0621 | 54.5635 | 4.7824 | 34.3821 | 692.7496 | 60.9671 | 4.6978 | 35.2099 | 774.5062 | 67.5712 | 4.6118 | 36.0204 | 862.1506 | 74.7042 | 4.5275 | 36.8156 | 952.3114 | 82.0102
|  | 11 | 5.0134 | 31.771 | 463.1009 | 39.0708 | 4.9571 | 32.6657 | 534.9552 | 44.9102 | 4.9023 | 33.5349 | 608.0511 | 50.809 | 4.8489 | 34.3821 | 682.3551 | 56.7665 | 4.7936 | 35.2099 | 758.8005 | 62.8871 | 4.7304 | 36.0204 | 839.5797 | 69.4215
|  | 12 | 5.0038 | 30.8461 | 396.6276 | 31.1565 | 4.9807 | 31.771 | 464.8524 | 36.5617 | 4.9584 | 32.6657 | 533.6041 | 42.0224 | 4.9366 | 33.5349 | 602.8666 | 47.5379 | 4.9154 | 34.3821 | 672.6263 | 53.1074 | 4.8895 | 35.2099 | 743.7896 | 58.8103
|  | 13 | 5.0604 | 29.8848 | 326.7371 | 25.4749 | 5.0428 | 30.8461 | 393.4512 | 30.7674 | 5.0259 | 31.771 | 460.5603 | 36.1198 | 5.0095 | 32.6657 | 528.0507 | 41.5311 | 4.9935 | 33.5349 | 595.9106 | 47.0005 | 4.978 | 34.3821 | 664.1302 | 52.5274
|  | 14 | 5.1048 | 28.8778 | 259.0678 | 19.9774 | 5.093 | 29.8848 | 324.584 | 25.1504 | 5.0818 | 30.8461 | 390.3589 | 30.3879 | 5.071 | 31.771 | 456.3819 | 35.6885 | 5.0606 | 32.6657 | 522.6443 | 41.0512 | 5.0504 | 33.5349 | 589.1388 | 46.4752
|  | 15 | 5.1359 | 27.8102 | 193.1006 | 14.6718 | 5.1306 | 28.8778 | 257.7361 | 19.718 | 5.1256 | 29.8848 | 322.4871 | 24.834 | 5.1208 | 30.8461 | 387.3474 | 30.0176 | 5.1161 | 31.771 | 452.3128 | 35.2673 | 5.1117 | 32.6657 | 517.3793 | 40.5822
|  | 16 | 6.7147 | 26.6553 | 98.9956 | 9.5904 | 6.5715 | 27.8102 | 152.1066 | 14.5121 | 6.4392 | 28.8778 | 207.2624 | 19.5079 | 6.3143 | 29.8848 | 264.3292 | 24.5747 | 6.1951 | 30.8461 | 323.2102 | 29.7105 | 6.0804 | 31.771 | 383.8301 | 34.9137
|  | 17 | 8.6046 | 25.3513 | 38.56 | 4.695 | 8.2878 | 26.6553 | 80.9712 | 9.4849 | 8.0071 | 27.8102 | 126.573 | 14.3558 | 7.7477 | 28.8778 | 175.07 | 19.3022 | 7.503 | 29.8848 | 226.273 | 24.3208 | 7.2694 | 30.8461 | 280.0447 | 29.4096
|  | 18 | 10.46 | 23.5 | 0 | 0 | 10.3328 | 25.3513 | 32.1917 | 4.6427 | 9.8608 | 26.6553 | 68.7455 | 9.3817 | 9.4427 | 27.8102 | 108.9133 | 14.2029 | 9.0562 | 28.8778 | 152.3604 | 19.1007 | 8.6917 | 29.8848 | 198.8725 | 24.072
|  | 19 |  |  |  |  | 12.23 | 23.5 | 0 | 0 | 12.061 | 25.3513 | 27.6457 | 4.5916 | 11.4338 | 26.6553 | 59.8612 | 9.2807 | 10.8783 | 27.8102 | 95.8626 | 14.0532 | 10.3648 | 28.8778 | 135.2995 | 18.9035
|  | 20 | [8 empty] | 14 | 23.5 | 0 | 0 | 13.7892 | 25.3513 | 24.2349 | 4.5416 | 13.0068 | 26.6553 | 53.0885 | 9.1819 | 12.3139 | 27.8102 | 85.7684 | 13.9066
Data for Graph.
|  | Indoor | 19 |  |  | 21 |  |  | 23
|  | Amb. | PI (kW) | PO (kW) | COP (%) | PI (kW) | PO (kW) | COP (%) | PI (kW) | PO (kW) | COP (%)
|  | -10 | 0.048183 | 9.2897 | 100 | 0.1 | 4.8835 | 48.8354 | 0.050125 | 5.0125 | 100
|  | -9 | 0.047526 | 8.9545 | 100 | 0.1 | 4.8183 | 48.1832 | 0.049483 | 4.9483 | 100
|  | -8 | 0.046863 | 8.6161 | 100 | 0.1 | 4.7526 | 47.5259 | 0.048835 | 4.8835 | 100
|  | -7 | 0.046195 | 8.2748 | 100 | 0.1 | 4.6863 | 46.863 | 0.048183 | 4.8183 | 100
|  | -6 | 0.04552 | 7.9365 | 100 | 0.1 | 4.6195 | 46.1945 | 0.047526 | 4.7526 | 100
|  | -5 | 0.044839 | 7.6162 | 100 | 0.1 | 4.552 | 45.5201 | 0.046863 | 4.6863 | 100
|  | -4 | 0.044152 | 7.2942 | 100 | 0.1 | 4.4839 | 44.8394 | 0.046195 | 4.6195 | 100
|  | -3 | 0.043458 | 6.9698 | 100 | 0.1 | 4.4152 | 44.1521 | 0.04552 | 4.552 | 100
|  | -2 | 0.042756 | 6.6418 | 100 | 0.1 | 4.3458 | 43.4578 | 0.044839 | 4.4839 | 100
|  | -1 | 0.042047 | 6.3084 | 100 | 0.1 | 4.2756 | 42.7563 | 0.044152 | 4.4152 | 100
|  | 0 | 0.041329 | 5.9671 | 100 | 0.1 | 4.2047 | 42.047 | 0.043458 | 4.3458 | 100
|  | 1 | 0.040603 | 5.623 | 100 | 0.1 | 4.1329 | 41.3294 | 0.042756 | 4.2756 | 100
|  | 2 | 0.039867 | 5.3088 | 100 | 0.1 | 4.0603 | 40.6031 | 0.042047 | 4.2047 | 100
|  | 3 | 0.039122 | 4.9926 | 100 | 0.1 | 3.9867 | 39.8674 | 0.041329 | 4.1329 | 100
|  | 4 | 0.038365 | 4.6707 | 100 | 0.1 | 3.9122 | 39.1216 | 0.040603 | 4.0603 | 100
|  | 5 | 0.037597 | 4.3406 | 100 | 0.1 | 3.8365 | 38.365 | 0.039867 | 3.9867 | 100
|  | 6 | 0.036816 | 3.9996 | 100 | 0.1 | 3.7597 | 37.5967 | 0.039122 | 3.9122 | 100
|  | 7 | 0.03602 | 3.6448 | 87.0149 | 0.1 | 3.6816 | 36.8156 | 0.038365 | 3.8365 | 100
|  | 8 | 0.03521 | 3.3267 | 71.5573 | 0.088114 | 3.1739 | 36.0204 | 0.037597 | 3.7597 | 100
|  | 9 | 0.034382 | 3.001 | 58.9172 | 0.073009 | 2.5706 | 35.2099 | 0.036816 | 2.9768 | 80.857
|  | 10 | 0.033535 | 2.6625 | 48.2241 | 0.060967 | 2.0962 | 34.3821 | 0.03602 | 2.4339 | 67.5712
|  | 11 | 0.032666 | 2.3217 | 39.0708 | 0.050809 | 1.7039 | 33.5349 | 0.03521 | 1.9987 | 56.7665
|  | 12 | 0.031771 | 1.9847 | 31.1565 | 0.042022 | 1.3727 | 32.6657 | 0.034382 | 1.6344 | 47.5379
|  | 13 | 0.030846 | 1.6534 | 25.4749 | 0.03612 | 1.1476 | 31.771 | 0.033535 | 1.3927 | 41.5311
|  | 14 | 0.029885 | 1.3225 | 19.9774 | 0.030388 | 0.93735 | 30.8461 | 0.032666 | 1.1658 | 35.6885
|  | 15 | 0.028878 | 0.99175 | 14.6718 | 0.024834 | 0.74216 | 29.8848 | 0.031771 | 0.95369 | 30.0176
|  | 16 | 0.02781 | 0.66473 | 9.5904 | 0.019508 | 0.56334 | 28.8778 | 0.030846 | 0.75803 | 24.5747
|  | 17 | 0.026655 | 0.33179 | 4.695 | 0.014356 | 0.39924 | 27.8102 | 0.029885 | 0.57684 | 19.3022
|  | 18 | 0.025351 | 0 | 0 | 0.0093817 | 0.25007 | 26.6553 | 0.028878 | 0.41015 | 14.2029
|  | 19 | 0.0235 | 0 | 0 | 0.0045916 | 0.1164 | 25.3513 | 0.02781 | 0.2581 | 9.2807
|  | 20 | 0 | 0 | 0 | 0 | 0 | 23.5 | 0.026655 | 0.12106 | 4.5416
Pretty Graph.

## Detailed Data
Heating Demand (W) |  | 8000 | at Amb. | -3.2 |  |  |  |  | Total Heating Elements Output (W) | [5 empty] | 24000 | at Delta T of 50C
Water Temp Hyst. (C.) |  | 0 | [6 empty] | Buffer Tank Effect (%) |  |  |  | 0 | [6 empty] | Heat Pump DT = |  |  | 5
Indoor Temp. |  | 18
LWT |  |  |  |  | 25 |  |  |  | 35 |  |  |  | 40 |  |  |  | 45 |  |  |  | 50 |  |  |  | 55
Outdoor air temperature[℃] |  | Heating Demand | COP | CL | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP
|  |  | LWT |  |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI
| -10 |  | 2.0292 | max | 14600 | 2.4 | 6083.3333 | 2.7334 | 14400 | 2.25 | 6400 | 2.5533 | 14200 | 2.1 | 6761.9048 | 2.3764 | 14000 | 1.9 | 7368.4211 | 2.1523 | 14000 | 1.85 | 7567.5676 | 1.9086 | 14000 | 1.75 | 8000 | 1.6475
|  | 9256.1983 | 47.5259 | nom | 14000 | 2.8 | 5000 | 3386.3662 | 14000 | 2.5 | 5600 | 3625.1931 | 14000 | 2.2 | 6363.6364 | 3894.9748 | 14000 | 1.9 | 7368.4211 | 4300.5574 | 14000 | 1.85 | 7567.5676 | 4849.8209 | 14000 | 1.75 | 8000 | 5618.2593
|  | 27.8969 | 100 | mid | 11200 | 2.85 | 3929.8246 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.1 | 5333.3333 | 1 | 11200 | 1.85 | 6054.0541 | 1
|  | 9289.6669 | 4578.029 | min | 6200 | 2.55 | 2431.3725 | 0.61124 | 5900 | 2.3 | 2565.2174 | 0.63324 | 5600 | 2.05 | 2731.7073 | 0.65289 | 5300 | 1.75 | 3028.5714 | 0.67054 | 4600 | 1.45 | 3172.4138 | 0.70548 | 4000 | 1.1 | 3636.3636 | 0.73003
| -9 |  | 2.0886 | max | 15100 | 2.5 | 6040 | 2.9551 | 14900 | 2.3333 | 6385.7143 | 2.602 | 14700 | 2.1667 | 6784.6154 | 2.4065 | 14500 | 1.9667 | 7372.8814 | 2.1785 | 14233.3333 | 1.9167 | 7426.087 | 1.937 | 14000 | 1.8167 | 7706.422 | 1.6857
|  | 8925.6198 | 46.863 | nom | 14000 | 2.8833 | 4855.4913 | 3020.4324 | 14000 | 2.6 | 5384.6154 | 3430.3579 | 14000 | 2.3167 | 6043.1655 | 3708.9112 | 14000 | 2.0333 | 6885.2459 | 4097.0514 | 14000 | 1.95 | 7179.4872 | 4607.8614 | 14000 | 1.8167 | 7706.422 | 5294.9713
|  | 26.8903 | 100 | mid | 11200 | 2.9833 | 3754.1899 | 1 | 11200 | 2.8 | 4000 | 1 | 11200 | 2.6167 | 4280.2548 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.1667 | 5169.2308 | 1 | 11200 | 1.9333 | 5793.1034 | 1
|  | 8954.4586 | 4287.3832 | min | 5833.3333 | 2.9167 | 2000 | 0.5762 | 5266.6667 | 2.2833 | 2306.5693 | 0.61668 | 5066.6667 | 2.05 | 2471.5447 | 0.62918 | 4866.6667 | 1.7833 | 2728.972 | 0.64089 | 4266.6667 | 1.4667 | 2909.0909 | 0.67196 | 3700 | 1.1167 | 3313.4328 | 0.69675
| -8 |  | 2.1484 | max | 15600 | 2.6 | 6000 | 3.1924 | 15400 | 2.4167 | 6372.4138 | 2.6488 | 15200 | 2.2333 | 6805.9701 | 2.4359 | 15000 | 2.0333 | 7377.0492 | 2.2062 | 14466.6667 | 1.9833 | 7294.1176 | 1.9645 | 14000 | 1.8833 | 7433.6283 | 1.7217
|  | 8595.0413 | 46.1945 | nom | 14000 | 2.9667 | 4719.1011 | 2692.3513 | 14000 | 2.7 | 5185.1852 | 3244.9298 | 14000 | 2.4333 | 5753.4247 | 3528.5416 | 14000 | 2.1667 | 6461.5385 | 3895.8822 | 14000 | 2.05 | 6829.2683 | 4375.2404 | 14000 | 1.8833 | 7433.6283 | 4992.297
|  | 25.8742 | 100 | mid | 11200 | 3.1167 | 3593.5829 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.6833 | 4173.913 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.2333 | 5014.9254 | 1 | 11200 | 2.0167 | 5553.719 | 1
|  | 8616.1095 | 4010.4045 | min | 5466.6667 | 3.2833 | 1664.9746 | 0.54565 | 4633.3333 | 2.2667 | 2044.1176 | 0.60331 | 4533.3333 | 2.05 | 2211.3821 | 0.60926 | 4433.3333 | 1.8167 | 2440.367 | 0.61503 | 3933.3333 | 1.4833 | 2651.6854 | 0.64152 | 3400 | 1.1333 | 3000 | 0.66603
| -7 |  | 2.2096 | max | 16100 | 2.7 | 5962.963 | 3.4425 | 15900 | 2.5 | 6360 | 2.6942 | 15700 | 2.3 | 6826.087 | 2.4646 | 15500 | 2.1 | 7380.9524 | 2.235 | 14700 | 2.05 | 7170.7317 | 1.991 | 14000 | 1.95 | 7179.4872 | 1.7557
|  | 8264.4628 | 45.5201 | nom | 14000 | 3.05 | 4590.1639 | 2400.7194 | 14000 | 2.8 | 5000 | 3067.4847 | 14000 | 2.55 | 5490.1961 | 3353.2666 | 14000 | 2.3 | 6086.9565 | 3697.769 | 14000 | 2.15 | 6511.6279 | 4150.9187 | 14000 | 1.95 | 7179.4872 | 4707.195
|  | 24.8491 | 100 | mid | 11200 | 3.25 | 3446.1538 | 1 | 11200 | 3 | 3733.3333 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1 | 11200 | 2.1 | 5333.3333 | 1
|  | 8274.7669 | 3744.9032 | min | 5100 | 3.65 | 1397.2603 | 0.51876 | 4000 | 2.25 | 1777.7778 | 0.59229 | 4000 | 2.05 | 1951.2195 | 0.59229 | 4000 | 1.85 | 2162.1622 | 0.59229 | 3600 | 1.5 | 2400 | 0.61375 | 3100 | 1.15 | 2695.6522 | 0.63759
| -6 |  | 2.2692 | max | 16144.4444 | 2.7611 | 5847.0825 | 3.5196 | 15944.4444 | 2.5556 | 6239.1304 | 2.7496 | 15733.3333 | 2.35 | 6695.0355 | 2.5066 | 15533.3333 | 2.1444 | 7243.5233 | 2.2613 | 14744.4444 | 2.0944 | 7039.7878 | 2.0105 | 14033.3333 | 1.9944 | 7036.2117 | 1.7642
|  | 7933.8843 | 44.8394 | nom | 14000 | 3.0889 | 4532.3741 | 2254.2068 | 14000 | 2.8389 | 4931.5068 | 2885.4451 | 14000 | 2.5889 | 5407.7253 | 3165.2513 | 14000 | 2.3389 | 5985.7482 | 3508.5289 | 14000 | 2.1944 | 6379.7468 | 3946.2696 | 14000 | 2 | 7000 | 4497.2394
|  | 23.8333 | 100 | mid | 11200 | 3.2944 | 3399.6627 | 1 | 11200 | 3.0444 | 3678.8321 | 1 | 11200 | 2.7944 | 4007.9523 | 1 | 11200 | 2.5444 | 4401.7467 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.15 | 5209.3023 | 1
|  | 7936.5023 | 3497.4996 | min | 5155.5556 | 3.7111 | 1389.2216 | 0.45965 | 4122.2222 | 2.4056 | 1713.6259 | 0.53854 | 4077.7778 | 2.1667 | 1882.0513 | 0.54142 | 4022.2222 | 1.9222 | 2092.4855 | 0.54497 | 3611.1111 | 1.5611 | 2313.1673 | 0.56962 | 3111.1111 | 1.1944 | 2604.6512 | 0.59622
| -5 |  | 2.3351 | max | 16188.8889 | 2.8222 | 5736.2205 | 3.5991 | 15988.8889 | 2.6111 | 6123.4043 | 2.816 | 15766.6667 | 2.4 | 6569.4444 | 2.5552 | 15566.6667 | 2.1889 | 7111.6751 | 2.2901 | 14788.8889 | 2.1389 | 6914.2857 | 2.0308 | 14066.6667 | 2.0389 | 6899.1826 | 1.7721
|  | 7603.3058 | 44.1521 | nom | 14000 | 3.1278 | 4476.0213 | 2112.5387 | 14000 | 2.8778 | 4864.8649 | 2700.0598 | 14000 | 2.6278 | 5327.6956 | 2975.5764 | 14000 | 2.3778 | 5887.8505 | 3320.0829 | 14000 | 2.2389 | 6253.1017 | 3743.9256 | 14000 | 2.05 | 6829.2683 | 4290.6649
|  | 22.8714 | 100 | mid | 11200 | 3.3389 | 3354.4093 | 1 | 11200 | 3.0889 | 3625.8993 | 1 | 11200 | 2.8389 | 3945.2055 | 1 | 11200 | 2.5889 | 4326.1803 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.2 | 5090.9091 | 1
|  | 7616.1696 | 3261.6583 | min | 5211.1111 | 3.7722 | 1381.4433 | 0.39944 | 4244.4444 | 2.5611 | 1657.2668 | 0.4829 | 4155.5556 | 2.2833 | 1819.9513 | 0.48943 | 4044.4444 | 1.9944 | 2027.8552 | 0.49736 | 3622.2222 | 1.6222 | 2232.8767 | 0.52536 | 3122.2222 | 1.2389 | 2520.1794 | 0.55474
| -4 |  | 2.4106 | max | 16233.3333 | 2.8833 | 5630.0578 | 3.6812 | 16033.3333 | 2.6667 | 6012.5 | 2.8939 | 15800 | 2.45 | 6448.9796 | 2.6109 | 15600 | 2.2333 | 6985.0746 | 2.3214 | 14833.3333 | 2.1833 | 6793.8931 | 2.0521 | 14100 | 2.0833 | 6768 | 1.7794
|  | 7272.7273 | 43.4578 | nom | 14000 | 3.1667 | 4421.0526 | 1975.6466 | 14000 | 2.9167 | 4800 | 2513.1532 | 14000 | 2.6667 | 5250 | 2785.5602 | 14000 | 2.4167 | 5793.1034 | 3132.9681 | 14000 | 2.2833 | 6131.3869 | 3544.0716 | 14000 | 2.1 | 6666.6667 | 4087.2337
|  | 21.9044 | 100 | mid | 11200 | 3.3833 | 3310.3448 | 1 | 11200 | 3.1333 | 3574.4681 | 1 | 11200 | 2.8833 | 3884.3931 | 1 | 11200 | 2.6333 | 4253.1646 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.25 | 4977.7778 | 1
|  | 7294.1811 | 3025.8151 | min | 5266.6667 | 3.8333 | 1373.913 | 0.3381 | 4366.6667 | 2.7167 | 1607.362 | 0.42528 | 4233.3333 | 2.4 | 1763.8889 | 0.43628 | 4066.6667 | 2.0667 | 1967.7419 | 0.44945 | 3633.3333 | 1.6833 | 2158.4158 | 0.48098 | 3133.3333 | 1.2833 | 2441.5584 | 0.51315
| -3 |  | 2.4981 | max | 16277.7778 | 2.9444 | 5528.3019 | 3.7658 | 16077.7778 | 2.7222 | 5906.1224 | 2.9839 | 15833.3333 | 2.5 | 6333.3333 | 2.6737 | 15633.3333 | 2.2778 | 6863.4146 | 2.3551 | 14877.7778 | 2.2278 | 6678.3042 | 2.0742 | 14133.3333 | 2.1278 | 6642.2977 | 1.7861
|  | 6942.1488 | 42.7563 | nom | 14000 | 3.2056 | 4367.4177 | 1843.4577 | 14000 | 2.9556 | 4736.8421 | 2326.5208 | 14000 | 2.7056 | 5174.538 | 2596.4769 | 14000 | 2.4556 | 5701.3575 | 2947.6931 | 14000 | 2.3278 | 6014.3198 | 3346.8802 | 14000 | 2.15 | 6511.6279 | 3886.7172
|  | 20.9304 | 100 | mid | 11200 | 3.4278 | 3267.423 | 1 | 11200 | 3.1778 | 3524.4755 | 1 | 11200 | 2.9278 | 3825.4269 | 1 | 11200 | 2.6778 | 4182.5726 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1
|  | 6969.8264 | 2790.0859 | min | 5322.2222 | 3.8944 | 1366.6191 | 0.2756 | 4488.8889 | 2.8722 | 1562.8627 | 0.36555 | 4311.1111 | 2.5167 | 1713.0243 | 0.38192 | 4088.8889 | 2.1389 | 1911.6883 | 0.40124 | 3644.4444 | 1.7444 | 2089.172 | 0.43646 | 3144.4444 | 1.3278 | 2368.2008 | 0.47144
| -2 |  | 2.5996 | max | 16322.2222 | 3.0056 | 5430.6839 | 3.8531 | 16122.2222 | 2.7778 | 5804 | 3.0868 | 15866.6667 | 2.55 | 6222.2222 | 2.7439 | 15666.6667 | 2.3222 | 6746.4115 | 2.3914 | 14922.2222 | 2.2722 | 6567.2372 | 2.0972 | 14166.6667 | 2.1722 | 6521.7391 | 1.7923
|  | 6611.5702 | 42.047 | nom | 14000 | 3.2444 | 4315.0685 | 1715.8951 | 14000 | 2.9944 | 4675.3247 | 2141.8757 | 14000 | 2.7444 | 5101.2146 | 2409.5315 | 14000 | 2.4944 | 5612.4722 | 2764.7337 | 14000 | 2.3722 | 5901.6393 | 3152.5118 | 14000 | 2.2 | 6363.6364 | 3688.8947
|  | 19.9455 | 100 | mid | 11200 | 3.4722 | 3225.6 | 1 | 11200 | 3.2222 | 3475.8621 | 1 | 11200 | 2.9722 | 3768.2243 | 1 | 11200 | 2.7222 | 4114.2857 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1
|  | 6641.8469 | 2554.948 | min | 5377.7778 | 3.9556 | 1359.5506 | 0.21191 | 4611.1111 | 3.0278 | 1522.9358 | 0.30361 | 4388.8889 | 2.6333 | 1666.6667 | 0.32633 | 4111.1111 | 2.2111 | 1859.2965 | 0.35273 | 3655.5556 | 1.8056 | 2024.6154 | 0.39181 | 3155.5556 | 1.3722 | 2299.5951 | 0.42962
| -1 |  | 2.7177 | max | 16366.6667 | 3.0667 | 5336.9565 | 3.9432 | 16166.6667 | 2.8333 | 5705.8824 | 3.2033 | 15900 | 2.6 | 6115.3846 | 2.8219 | 15700 | 2.3667 | 6633.8028 | 2.4302 | 14966.6667 | 2.3167 | 6460.4317 | 2.1212 | 14200 | 2.2167 | 6406.015 | 1.7979
|  | 6280.9917 | 41.3294 | nom | 14000 | 3.2833 | 4263.9594 | 1592.8786 | 14000 | 3.0333 | 4615.3846 | 1960.8017 | 14000 | 2.7833 | 5029.9401 | 2225.8383 | 14000 | 2.5333 | 5526.3158 | 2584.5309 | 14000 | 2.4167 | 5793.1034 | 2961.1138 | 14000 | 2.25 | 6222.2222 | 3493.5531
|  | 18.9442 | 100 | mid | 11200 | 3.5167 | 3184.8341 | 1 | 11200 | 3.2667 | 3428.5714 | 1 | 11200 | 3.0167 | 3712.7072 | 1 | 11200 | 2.7667 | 4048.1928 | 1 | 11200 | 2.6 | 4307.6923 | 1 | 11200 | 2.4 | 4666.6667 | 1
|  | 6308.4108 | 2321.208 | min | 5433.3333 | 4.0167 | 1352.6971 | 0.14699 | 4733.3333 | 3.1833 | 1486.911 | 0.23933 | 4466.6667 | 2.75 | 1624.2424 | 0.26945 | 4133.3333 | 2.2833 | 1810.219 | 0.30391 | 3666.6667 | 1.8667 | 1964.2857 | 0.34703 | 3166.6667 | 1.4167 | 2235.2941 | 0.38768
| 0 |  | 2.8551 | max | 16411.1111 | 3.1278 | 5246.8917 | 4.036 | 16211.1111 | 2.8889 | 5611.5385 | 3.3341 | 15933.3333 | 2.65 | 6012.5786 | 2.9077 | 15733.3333 | 2.4111 | 6525.3456 | 2.4716 | 15011.1111 | 2.3611 | 6357.6471 | 2.146 | 14233.3333 | 2.2611 | 6294.8403 | 1.8029
|  | 5950.4132 | 40.6031 | nom | 14000 | 3.3222 | 4214.0468 | 1474.3251 | 14000 | 3.0722 | 4556.962 | 1784.716 | 14000 | 2.8222 | 4960.6299 | 2046.4031 | 14000 | 2.5722 | 5442.7646 | 2407.4886 | 14000 | 2.4611 | 5688.4876 | 2772.8216 | 14000 | 2.3 | 6086.9565 | 3300.4855
|  | 17.9193 | 100 | mid | 11200 | 3.5611 | 3145.0858 | 1 | 11200 | 3.3111 | 3382.5503 | 1 | 11200 | 3.0611 | 3658.8022 | 1 | 11200 | 2.8111 | 3984.1897 | 1 | 11200 | 2.65 | 4226.4151 | 1 | 11200 | 2.45 | 4571.4286 | 1
|  | 5967.1164 | 2089.9563 | min | 5488.8889 | 4.0778 | 1346.049 | 0.080812 | 4855.5556 | 3.3389 | 1454.2429 | 0.17257 | 4544.4444 | 2.8667 | 1585.2713 | 0.21125 | 4155.5556 | 2.3556 | 1764.1509 | 0.25479 | 3677.7778 | 1.9278 | 1907.781 | 0.30212 | 3177.7778 | 1.4611 | 2174.9049 | 0.34562
| 1 |  | 3.0146 | max | 16455.5556 | 3.1889 | 5160.2787 | 4.1318 | 16255.5556 | 2.9444 | 5520.7547 | 3.4801 | 15966.6667 | 2.7 | 5913.5802 | 3.0019 | 15766.6667 | 2.4556 | 6420.8145 | 2.5156 | 15055.5556 | 2.4056 | 6258.6605 | 2.1717 | 14266.6667 | 2.3056 | 6187.9518 | 1.8073
|  | 5619.8347 | 39.8674 | nom | 14000 | 3.3611 | 4165.2893 | 1360.1488 | 14000 | 3.1111 | 4500 | 1614.8427 | 14000 | 2.8611 | 4893.2039 | 1872.1113 | 14000 | 2.6111 | 5361.7021 | 2233.9719 | 14000 | 2.5056 | 5587.5831 | 2587.7579 | 14000 | 2.35 | 5957.4468 | 3109.4912
|  | 16.8859 | 100 | mid | 11200 | 3.6056 | 3106.3174 | 1 | 11200 | 3.3556 | 3337.7483 | 1 | 11200 | 3.1056 | 3606.4401 | 1 | 11200 | 2.8556 | 3922.179 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.5 | 4480 | 1
|  | 5623.0113 | 1865.288 | min | 5544.4444 | 4.1389 | 1339.5973 | 0.01333 | 4977.7778 | 3.4944 | 1424.4833 | 0.10319 | 4622.2222 | 2.9833 | 1549.3482 | 0.15166 | 4177.7778 | 2.4278 | 1720.8238 | 0.20536 | 3688.8889 | 1.9889 | 1854.7486 | 0.25708 | 3188.8889 | 1.5056 | 2118.0812 | 0.30345
14kW-Maximum heating CAP | 2 |  | 3.199 | max | 16500 | 3.25 | 5076.9231 | 4.2 | 16300 | 3 | 5433.3333 | 3.6422 | 16000 | 2.75 | 5818.1818 | 3.1045 | 15800 | 2.5 | 6320 | 2.5622 | 15100 | 2.45 | 6163.2653 | 2.1983 | 14300 | 2.35 | 6085.1064 | 1.8112
|  | 5289.2562 | 39.1216 | nom | 14000 | 3.4 | 4117.6471 | 1259.3467 | 14000 | 3.15 | 4444.4444 | 1452.1973 | 14000 | 2.9 | 4827.5862 | 1703.7205 | 14000 | 2.65 | 5283.0189 | 2064.3068 | 14000 | 2.55 | 5490.1961 | 2406.0331 | 14000 | 2.4 | 5833.3333 | 2920.3742
|  | 15.9425 | 100 | mid | 11200 | 3.65 | 3068.4932 | 0 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 3.15 | 3555.5556 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.55 | 4392.1569 | 1
|  | 5308.8416 | 1659.5346 | min | 5600 | 4.2 | 1333.3333 | 0 | 5100 | 3.65 | 1397.2603 | 0.031026 | 4700 | 3.1 | 1516.129 | 0.090655 | 4200 | 2.5 | 1680 | 0.15561 | 3700 | 2.05 | 1804.878 | 0.2119 | 3200 | 1.55 | 2064.5161 | 0.26116
| 3 |  | 3.3954 | max | 16560 | 3.54 | 4677.9661 | 4.68 | 16360 | 3.25 | 5033.8462 | 3.8092 | 16080 | 2.96 | 5432.4324 | 3.1944 | 15860 | 2.66 | 5962.406 | 2.5872 | 15160 | 2.54 | 5968.5039 | 2.1991 | 14360 | 2.38 | 6033.6134 | 1.7904
|  | 4958.6777 | 38.365 | nom | 14000 | 3.7 | 3783.7838 | 1059.5465 | 14000 | 3.41 | 4105.5718 | 1301.7638 | 14000 | 3.12 | 4487.1795 | 1552.3147 | 14000 | 2.82 | 4964.539 | 1916.5995 | 14000 | 2.67 | 5243.4457 | 2254.8377 | 14000 | 2.47 | 5668.0162 | 2769.6527
|  | 14.9927 | 100 | mid | 11200 | 3.97 | 2821.1587 | 0 | 11200 | 3.68 | 3043.4783 | 1 | 11200 | 3.39 | 3303.8348 | 1 | 11200 | 3.09 | 3624.5955 | 1 | 11200 | 2.88 | 3888.8889 | 1 | 11200 | 2.62 | 4274.8092 | 1
|  | 4992.5781 | 1470.3862 | min | 5380 | 4.68 | 1149.5726 | 0 | 4920 | 3.81 | 1291.3386 | 0.0061589 | 4500 | 3.18 | 1415.0943 | 0.068459 | 4000 | 2.51 | 1593.6255 | 0.13315 | 3500 | 2.04 | 1715.6863 | 0.18944 | 3000 | 1.53 | 1960.7843 | 0.23886
| 4 |  | 3.6104 | max | 16620 | 3.83 | 4339.4256 | 5.16 | 16420 | 3.5 | 4691.4286 | 3.97 | 16160 | 3.17 | 5097.7918 | 3.2776 | 15920 | 2.82 | 5645.3901 | 2.605 | 15220 | 2.63 | 5787.0722 | 2.1948 | 14420 | 2.41 | 5983.4025 | 1.7668
|  | 4628.0992 | 37.5967 | nom | 14000 | 4 | 3500 | 896.9184 | 14000 | 3.67 | 3814.7139 | 1165.7681 | 14000 | 3.34 | 4191.6168 | 1412.0417 | 14000 | 2.99 | 4682.2742 | 1776.5888 | 14000 | 2.79 | 5017.9211 | 2108.7121 | 14000 | 2.54 | 5511.811 | 2619.4745
|  | 14.026 | 100 | mid | 11200 | 4.29 | 2610.7226 | 0 | 11200 | 3.96 | 2828.2828 | 0 | 11200 | 3.63 | 3085.3994 | 1 | 11200 | 3.28 | 3414.6341 | 1 | 11200 | 3.01 | 3720.9302 | 1 | 11200 | 2.69 | 4163.5688 | 1
|  | 4670.6658 | 1293.6675 | min | 5160 | 5.16 | 1000 | 0 | 4740 | 3.97 | 1193.9547 | 0 | 4300 | 3.26 | 1319.0184 | 0.047551 | 3800 | 2.52 | 1507.9365 | 0.11191 | 3300 | 2.03 | 1625.6158 | 0.16811 | 2800 | 1.51 | 1854.3046 | 0.21763
| 5 |  | 3.8485 | max | 16680 | 4.12 | 4048.5437 | 5.64 | 16480 | 3.75 | 4394.6667 | 4.13 | 16240 | 3.38 | 4804.7337 | 3.3547 | 15980 | 2.98 | 5362.4161 | 2.6163 | 15280 | 2.72 | 5617.6471 | 2.1856 | 14480 | 2.44 | 5934.4262 | 1.7407
|  | 4297.5207 | 36.8156 | nom | 14000 | 4.3 | 3255.814 | 761.9717 | 14000 | 3.93 | 3562.341 | 1040.5619 | 14000 | 3.56 | 3932.5843 | 1281.0277 | 14000 | 3.16 | 4430.3797 | 1642.6122 | 14000 | 2.91 | 4810.9966 | 1966.3039 | 14000 | 2.61 | 5363.9847 | 2468.8741
|  | 13.0349 | 100 | mid | 11200 | 4.61 | 2429.5011 | 0 | 11200 | 4.24 | 2641.5094 | 0 | 11200 | 3.87 | 2894.0568 | 1 | 11200 | 3.47 | 3227.6657 | 1 | 11200 | 3.14 | 3566.879 | 1 | 11200 | 2.76 | 4057.971 | 1
|  | 4340.6331 | 1127.8785 | min | 4940 | 5.64 | 875.8865 | 0 | 4560 | 4.13 | 1104.1162 | 0 | 4100 | 3.34 | 1227.5449 | 0.02782 | 3600 | 2.53 | 1422.9249 | 0.091779 | 3100 | 2.02 | 1534.6535 | 0.14784 | 2600 | 1.49 | 1744.9664 | 0.19739
| 6 |  | 4.1137 | max | 16740 | 4.41 | 3795.9184 | 6.12 | 16540 | 4 | 4135 | 4.29 | 16320 | 3.59 | 4545.961 | 3.4263 | 16040 | 3.14 | 5108.2803 | 2.6214 | 15340 | 2.81 | 5459.0747 | 2.172 | 14540 | 2.47 | 5886.6397 | 1.7122
|  | 3966.9421 | 36.0204 | nom | 14000 | 4.6 | 3043.4783 | 648.1932 | 14000 | 4.19 | 3341.2888 | 924.6951 | 14000 | 3.78 | 3703.7037 | 1157.7826 | 14000 | 3.33 | 4204.2042 | 1513.2873 | 14000 | 3.03 | 4620.462 | 1826.4262 | 14000 | 2.68 | 5223.8806 | 2316.9174
|  | 12.0109 | 100 | mid | 11200 | 4.93 | 2271.8053 | 0 | 11200 | 4.52 | 2477.8761 | 0 | 11200 | 4.11 | 2725.0608 | 1 | 11200 | 3.66 | 3060.1093 | 1 | 11200 | 3.27 | 3425.0765 | 1 | 11200 | 2.83 | 3957.5972 | 1
|  | 3999.6424 | 972.2657 | min | 4720 | 6.12 | 771.2418 | 0 | 4380 | 4.29 | 1020.979 | 0 | 3900 | 3.42 | 1140.3509 | 0.0091702 | 3400 | 2.54 | 1338.5827 | 0.072685 | 2900 | 2.01 | 1442.7861 | 0.12855 | 2400 | 1.47 | 1632.6531 | 0.17806
| 7 |  | 4.4101 | max | 16800 | 4.7 | 3574.4681 | 6.6 | 16600 | 4.25 | 3905.8824 | 4.45 | 16400 | 3.8 | 4315.7895 | 3.5 | 16100 | 3.3 | 4878.7879 | 2.6209 | 15400 | 2.9 | 5310.3448 | 2.1542 | 14600 | 2.5 | 5840 | 1.6814
|  | 3636.3636 | 35.2099 | nom | 14000 | 4.9 | 2857.1429 | 550.9642 | 14000 | 4.45 | 3146.0674 | 817.1604 | 14000 | 4 | 3500 | 1038.961 | 14000 | 3.5 | 4000 | 1387.4436 | 14000 | 3.15 | 4444.4444 | 1688.0151 | 14000 | 2.75 | 5090.9091 | 2162.6817
|  | 10.9455 | 87.0149 | mid | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.8 | 2333.3333 | 0 | 11200 | 4.35 | 2574.7126 | 0 | 11200 | 3.85 | 2909.0909 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 2.9 | 3862.069 | 1
|  | 3644.8363 | 826.4697 | min | 4500 | 6.6 | 681.8182 | 0 | 4200 | 4.45 | 943.8202 | 0 | 3700 | 3.5 | 1057.1429 | 0 | 3200 | 2.55 | 1254.902 | 0.054545 | 2700 | 2 | 1350 | 0.11016 | 2200 | 1.45 | 1517.2414 | 0.1596
| 8 |  | 4.6494 | max | 16860 | 4.81 | 3505.1975 | 6.31 | 16640 | 4.38 | 3799.0868 | 4.54 | 16440 | 3.93 | 4183.2061 | 3.73 | 16160 | 3.48 | 4643.6782 | 2.91 | 15440 | 3.06 | 5045.7516 | 2.3564 | 14640 | 2.64 | 5545.4545 | 1.8534
|  | 3305.7851 | 34.3821 | nom | 14000 | 5.02 | 2788.8446 | 523.8962 | 14000 | 4.59 | 3050.1089 | 728.1465 | 14000 | 4.16 | 3365.3846 | 886.2695 | 14000 | 3.69 | 3794.0379 | 1136.0086 | 14000 | 3.32 | 4216.8675 | 1402.8984 | 14000 | 2.9 | 4827.5862 | 1783.6138
|  | 9.9902 | 71.5573 | mid | 11200 | 5.37 | 2085.6611 | 0 | 11200 | 4.95 | 2262.6263 | 0 | 11200 | 4.53 | 2472.4062 | 0 | 11200 | 4.06 | 2758.6207 | 0 | 11200 | 3.58 | 3128.4916 | 1 | 11200 | 3.06 | 3660.1307 | 1
|  | 3326.7446 | 715.525 | min | 4920 | 6.31 | 779.7147 | 0 | 4600 | 4.54 | 1013.2159 | 0 | 4120 | 3.73 | 1104.5576 | 0 | 3640 | 2.91 | 1250.8591 | 0 | 3200 | 2.34 | 1367.5214 | 0.013223 | 2760 | 1.77 | 1559.322 | 0.064666
| 9 |  | 4.8336 | max | 16920 | 4.92 | 3439.0244 | 6.02 | 16680 | 4.51 | 3698.4479 | 4.63 | 16480 | 4.06 | 4059.1133 | 3.96 | 16220 | 3.66 | 4431.694 | 3.27 | 15480 | 3.22 | 4807.4534 | 2.68 | 14680 | 2.78 | 5280.5755 | 2.78
|  | 2975.2066 | 33.5349 | nom | 14000 | 5.14 | 2723.7354 | 494.2204 | 14000 | 4.73 | 2959.8309 | 642.5932 | 14000 | 4.32 | 3240.7407 | 751.3148 | 14000 | 3.88 | 3608.2474 | 909.8491 | 14000 | 3.49 | 4011.4613 | 1110.1517 | 14000 | 3.05 | 4590.1639 | 1070.2182
|  | 9.012 | 58.9172 | mid | 11200 | 5.49 | 2040.0729 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.71 | 2377.9193 | 0 | 11200 | 4.27 | 2622.9508 | 0 | 11200 | 3.76 | 2978.7234 | 0 | 11200 | 3.22 | 3478.2609 | 4
|  | 3000.9957 | 620.8551 | min | 5340 | 6.02 | 887.0432 | 0 | 5000 | 4.63 | 1079.9136 | 0 | 4540 | 3.96 | 1146.4646 | 0 | 4080 | 3.27 | 1247.7064 | 0 | 3700 | 2.68 | 1380.597 | 0 | 3320 | 2.09 | 1588.5167 | 0
| 10 |  | 4.9558 | max | 16980 | 5.03 | 3375.7455 | 5.73 | 16720 | 4.64 | 3603.4483 | 4.72 | 16520 | 4.19 | 3942.7208 | 4.19 | 16280 | 3.84 | 4239.5833 | 3.63 | 15520 | 3.38 | 4591.716 | 3.02 | 14720 | 2.92 | 5041.0959 | 2.41
|  | 2644.6281 | 32.6657 | nom | 14000 | 5.26 | 2661.597 | 461.5407 | 14000 | 4.87 | 2874.7433 | 560.3026 | 14000 | 4.48 | 3125 | 631.1762 | 14000 | 4.07 | 3439.8034 | 728.5477 | 14000 | 3.66 | 3825.1366 | 875.7047 | 14000 | 3.2 | 4375 | 1097.3561
|  | 7.9954 | 48.2241 | mid | 11200 | 5.61 | 1996.4349 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.89 | 2290.3885 | 0 | 11200 | 4.48 | 2500 | 0 | 11200 | 3.94 | 2842.6396 | 0 | 11200 | 3.38 | 3313.6095 | 0
|  | 2662.4774 | 537.2484 | min | 5760 | 5.73 | 1005.2356 | 0 | 5400 | 4.72 | 1144.0678 | 0 | 4960 | 4.19 | 1183.7709 | 0 | 4520 | 3.63 | 1245.1791 | 0 | 4200 | 3.02 | 1390.7285 | 0 | 3880 | 2.41 | 1609.9585 | 0
| 11 |  | 5.0134 | max | 17040 | 5.14 | 3315.1751 | 5.44 | 16760 | 4.77 | 3513.6268 | 4.81 | 16560 | 4.32 | 3833.3333 | 4.42 | 16340 | 4.02 | 4064.6766 | 3.99 | 15560 | 3.54 | 4395.4802 | 3.36 | 14760 | 3.06 | 4823.5294 | 2.73
|  | 2314.0496 | 31.771 | nom | 14000 | 5.38 | 2602.2305 | 425.3768 | 14000 | 5.01 | 2794.4112 | 481.0914 | 14000 | 4.64 | 3017.2414 | 523.5406 | 14000 | 4.26 | 3286.385 | 579.9623 | 14000 | 3.83 | 3655.3525 | 688.7052 | 14000 | 3.35 | 4179.1045 | 847.6372
|  | 6.9721 | 39.0708 | mid | 11200 | 5.73 | 1954.6248 | 0 | 11200 | 5.4 | 2074.0741 | 0 | 11200 | 5.07 | 2209.073 | 0 | 11200 | 4.69 | 2388.0597 | 0 | 11200 | 4.12 | 2718.4466 | 0 | 11200 | 3.54 | 3163.8418 | 0
|  | 2321.7238 | 463.1009 | min | 6180 | 5.44 | 1136.0294 | 0 | 5800 | 4.81 | 1205.8212 | 0 | 5380 | 4.42 | 1217.1946 | 0 | 4960 | 3.99 | 1243.1078 | 0 | 4700 | 3.36 | 1398.8095 | 0 | 4440 | 2.73 | 1626.3736 | 0
| 12 |  | 5.0038 | max | 17100 | 5.25 | 3257.1429 | 5.15 | 16800 | 4.9 | 3428.5714 | 4.9 | 16600 | 4.45 | 3730.3371 | 4.65 | 16400 | 4.2 | 3904.7619 | 4.35 | 15600 | 3.7 | 4216.2162 | 3.7 | 14800 | 3.2 | 4625 | 3.05
|  | 1983.4711 | 30.8461 | nom | 14000 | 5.5 | 2545.4545 | 385.14 | 14000 | 5.15 | 2718.4466 | 404.79 | 14000 | 4.8 | 2916.6667 | 426.5529 | 14000 | 4.45 | 3146.0674 | 455.9704 | 14000 | 4 | 3500 | 536.0733 | 14000 | 3.5 | 4000 | 650.3184
|  | 5.96 | 31.1565 | mid | 11200 | 5.85 | 1914.5299 | 0 | 11200 | 5.55 | 2018.018 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.9 | 2285.7143 | 0 | 11200 | 4.3 | 2604.6512 | 0 | 11200 | 3.7 | 3027.027 | 0
|  | 1984.664 | 396.6276 | min | 6600 | 5.15 | 1281.5534 | 0 | 6200 | 4.9 | 1265.3061 | 0 | 5800 | 4.65 | 1247.3118 | 0 | 5400 | 4.35 | 1241.3793 | 0 | 5200 | 3.7 | 1405.4054 | 0 | 5000 | 3.05 | 1639.3443 | 0
| 13 |  | 5.0604 | max | 17566.6667 | 5.2833 | 3324.9211 | 5.15 | 17266.6667 | 4.9333 | 3500 | 4.9667 | 17033.3333 | 4.55 | 3743.5897 | 4.7833 | 16833.3333 | 4.3 | 3914.7287 | 4.55 | 16033.3333 | 3.8 | 4219.2982 | 3.9167 | 15200 | 3.3 | 4606.0606 | 3.2667
|  | 1652.8926 | 29.8848 | nom | 14000 | 5.5 | 2545.4545 | 320.95 | 14000 | 5.1833 | 2700.9646 | 332.7972 | 14000 | 4.8667 | 2876.7123 | 345.5525 | 14000 | 4.55 | 3076.9231 | 363.2731 | 14000 | 4.1 | 3414.6341 | 422.0151 | 14000 | 3.6167 | 3870.9677 | 505.9875
|  | 4.9653 | 25.4749 | mid | 11200 | 5.9 | 1898.3051 | 0 | 11200 | 5.5833 | 2005.9701 | 0 | 11200 | 5.3167 | 2106.5831 | 0 | 11200 | 5.0167 | 2232.5581 | 0 | 11200 | 4.4167 | 2535.8491 | 0 | 11200 | 3.8167 | 2934.4978 | 0
|  | 1653.4353 | 326.7371 | min | 6700 | 5.15 | 1300.9709 | 0 | 6266.6667 | 4.9667 | 1261.745 | 0 | 5833.3333 | 4.7833 | 1219.5122 | 0 | 5400 | 4.55 | 1186.8132 | 0 | 5233.3333 | 3.9167 | 1336.1702 | 0 | 5066.6667 | 3.2667 | 1551.0204 | 0
| 14 |  | 5.1048 | max | 18033.3333 | 5.3167 | 3391.8495 | 5.15 | 17733.3333 | 4.9667 | 3570.4698 | 5.0333 | 17466.6667 | 4.65 | 3756.2724 | 4.9167 | 17266.6667 | 4.4 | 3924.2424 | 4.75 | 16466.6667 | 3.9 | 4222.2222 | 4.1333 | 15600 | 3.4 | 4588.2353 | 3.4833
|  | 1322.314 | 28.8778 | nom | 14000 | 5.5 | 2545.4545 | 256.76 | 14000 | 5.2167 | 2683.7061 | 262.7114 | 14000 | 4.9333 | 2837.8378 | 268.9452 | 14000 | 4.65 | 3010.7527 | 278.3819 | 14000 | 4.2 | 3333.3333 | 319.9147 | 14000 | 3.7333 | 3750 | 379.6117
|  | 3.9714 | 19.9774 | mid | 11200 | 5.95 | 1882.3529 | 0 | 11200 | 5.6167 | 1994.0653 | 0 | 11200 | 5.3833 | 2080.4954 | 0 | 11200 | 5.1333 | 2181.8182 | 0 | 11200 | 4.5333 | 2470.5882 | 0 | 11200 | 3.9333 | 2847.4576 | 0
|  | 1322.4789 | 259.0678 | min | 6800 | 5.15 | 1320.3883 | 0 | 6333.3333 | 5.0333 | 1258.2781 | 0 | 5866.6667 | 4.9167 | 1193.2203 | 0 | 5400 | 4.75 | 1136.8421 | 0 | 5266.6667 | 4.1333 | 1274.1935 | 0 | 5133.3333 | 3.4833 | 1473.6842 | 0
| 15 |  | 5.1359 | max | 18500 | 5.35 | 3457.9439 | 5.15 | 18200 | 5 | 3640 | 5.1 | 17900 | 4.75 | 3768.4211 | 5.05 | 17700 | 4.5 | 3933.3333 | 4.95 | 16900 | 4 | 4225 | 4.35 | 16000 | 3.5 | 4571.4286 | 3.7
|  | 991.7355 | 27.8102 | nom | 14000 | 5.5 | 2545.4545 | 192.57 | 14000 | 5.25 | 2666.6667 | 194.4579 | 14000 | 5 | 2800 | 196.3833 | 14000 | 4.75 | 2947.3684 | 200.3506 | 14000 | 4.3 | 3255.814 | 227.9852 | 14000 | 3.85 | 3636.3636 | 268.0366
|  | 2.9782 | 14.6718 | mid | 11200 | 6 | 1866.6667 | 0 | 11200 | 5.65 | 1982.3009 | 0 | 11200 | 5.45 | 2055.0459 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.65 | 2408.6022 | 0 | 11200 | 4.05 | 2765.4321 | 0
|  | 991.7546 | 193.1006 | min | 6900 | 5.15 | 1339.8058 | 0 | 6400 | 5.1 | 1254.902 | 0 | 5900 | 5.05 | 1168.3168 | 0 | 5400 | 4.95 | 1090.9091 | 0 | 5300 | 4.35 | 1218.3908 | 0 | 5200 | 3.7 | 1405.4054 | 0
| 16 |  | 6.7147 | max | 19020 | 5.73 | 3319.3717 | 6.92 | 18720 | 5.3 | 3532.0755 | 5.68 | 18420 | 4.95 | 3721.2121 | 5.37 | 18200 | 4.59 | 3965.1416 | 5.02 | 17380 | 4.08 | 4259.8039 | 4.36 | 16460 | 3.56 | 4623.5955 | 3.65
|  | 661.157 | 26.6553 | nom | 14000 | 5.93 | 2360.8769 | 95.5429 | 14000 | 5.57 | 2513.465 | 116.4009 | 14000 | 5.21 | 2687.1401 | 123.1205 | 14000 | 4.85 | 2886.5979 | 131.7046 | 14000 | 4.39 | 3189.0661 | 151.6415 | 14000 | 3.92 | 3571.4286 | 181.1389
|  | 1.9962 | 9.5904 | mid | 11200 | 6.42 | 1744.5483 | 0 | 11200 | 5.99 | 1869.783 | 0 | 11200 | 5.68 | 1971.831 | 0 | 11200 | 5.36 | 2089.5522 | 0 | 11200 | 4.74 | 2362.8692 | 0 | 11200 | 4.12 | 2718.4466 | 0
|  | 664.7296 | 98.9956 | min | 6980 | 6.92 | 1008.6705 | 0 | 6460 | 5.68 | 1137.3239 | 0 | 6000 | 5.37 | 1117.3184 | 0 | 5520 | 5.02 | 1099.6016 | 0 | 5360 | 4.36 | 1229.3578 | 0 | 5180 | 3.65 | 1419.1781 | 0
| 17 |  | 8.6046 | max | 19540 | 6.11 | 3198.036 | 8.69 | 19240 | 5.6 | 3435.7143 | 6.26 | 18940 | 5.15 | 3677.6699 | 5.69 | 18700 | 4.68 | 3995.7265 | 5.09 | 17860 | 4.16 | 4293.2692 | 4.37 | 16920 | 3.62 | 4674.0331 | 3.6
|  | 330.5785 | 25.3513 | nom | 14000 | 6.36 | 2201.2579 | 38.0413 | 14000 | 5.89 | 2376.91 | 52.8081 | 14000 | 5.42 | 2583.0258 | 58.0982 | 14000 | 4.95 | 2828.2828 | 64.9467 | 14000 | 4.48 | 3125 | 75.6473 | 14000 | 3.99 | 3508.7719 | 91.8274
|  | 0.99638 | 4.695 | mid | 11200 | 6.84 | 1637.4269 | 0 | 11200 | 6.33 | 1769.3523 | 0 | 11200 | 5.91 | 1895.0931 | 0 | 11200 | 5.47 | 2047.532 | 0 | 11200 | 4.83 | 2318.8406 | 0 | 11200 | 4.19 | 2673.031 | 0
|  | 331.7949 | 38.56 | min | 7060 | 8.69 | 812.4281 | 0 | 6520 | 6.26 | 1041.5335 | 0 | 6100 | 5.69 | 1072.0562 | 0 | 5640 | 5.09 | 1108.055 | 0 | 5420 | 4.37 | 1240.2746 | 0 | 5160 | 3.6 | 1433.3333 | 0
| 18 |  | 10.46 | max | 20060 | 6.49 | 3090.9091 | 10.46 | 19760 | 5.9 | 3349.1525 | 6.84 | 19460 | 5.35 | 3637.3832 | 6.01 | 19200 | 4.77 | 4025.1572 | 5.16 | 18340 | 4.24 | 4325.4717 | 4.38 | 17380 | 3.68 | 4722.8261 | 3.55
|  | 0 | 23.5 | nom | 14000 | 6.79 | 2061.8557 | 0 | 14000 | 6.21 | 2254.4283 | 0 | 14000 | 5.63 | 2486.6785 | 0 | 14000 | 5.05 | 2772.2772 | 0 | 14000 | 4.57 | 3063.4573 | 0 | 14000 | 4.06 | 3448.2759 | 0
|  | 0 | 0 | mid | 11200 | 7.26 | 1542.6997 | 0 | 11200 | 6.67 | 1679.1604 | 0 | 11200 | 6.14 | 1824.1042 | 0 | 11200 | 5.58 | 2007.1685 | 0 | 11200 | 4.92 | 2276.4228 | 0 | 11200 | 4.26 | 2629.108 | 0
|  | 0 | 0 | min | 7140 | 10.46 | 682.6004 | 0 | 6580 | 6.84 | 961.9883 | 0 | 6200 | 6.01 | 1031.614 | 0 | 5760 | 5.16 | 1116.2791 | 0 | 5480 | 4.38 | 1251.1416 | 0 | 5140 | 3.55 | 1447.8873 | 0
| 19 |  | #NUM! | max | 20580 | 6.87 | 2995.6332 | 12.23 | 20280 | 6.2 | 3270.9677 | 7.42 | 19980 | 5.55 | 3600 | 6.33 | 19700 | 4.86 | 4053.4979 | 5.23 | 18820 | 4.32 | 4356.4815 | 4.39 | 17840 | 3.74 | 4770.0535 | 3.5
|  | -330.5785 | #NUM! | nom | 14000 | 7.22 | 1939.0582 | -27.0301 | 14000 | 6.53 | 2143.951 | -44.5524 | 14000 | 5.84 | 2397.2603 | -52.2241 | 14000 | 5.15 | 2718.4466 | -63.2081 | 14000 | 4.66 | 3004.2918 | -75.3026 | 14000 | 4.13 | 3389.8305 | -94.451
|  |  | #NUM! | mid | 11200 | 7.68 | 1458.3333 | 0 | 11200 | 7.01 | 1597.7175 | 0 | 11200 | 6.37 | 1758.2418 | 0 | 11200 | 5.69 | 1968.3656 | 0 | 11200 | 5.01 | 2235.5289 | 0 | 11200 | 4.33 | 2586.6051 | 0
|  |  | #NUM! | min | 7220 | 12.23 | 590.3516 | 0 | 6640 | 7.42 | 894.8787 | 0 | 6300 | 6.33 | 995.2607 | 0 | 5880 | 5.23 | 1124.283 | 0 | 5540 | 4.39 | 1261.959 | 0 | 5120 | 3.5 | 1462.8571 | 0
| 20 |  | #NUM! | max | 21100 | 7.25 | 2910.3448 | 14 | 20800 | 6.5 | 3200 | 8 | 20500 | 5.75 | 3565.2174 | 6.65 | 20200 | 4.95 | 4080.8081 | 5.3 | 19300 | 4.4 | 4386.3636 | 4.4 | 18300 | 3.8 | 4815.7895 | 3.45
|  | -661.157 | #NUM! | nom | 14000 | 7.65 | 1830.0654 | -47.2255 | 14000 | 6.85 | 2043.7956 | -82.6446 | 14000 | 6.05 | 2314.0496 | -99.4221 | 14000 | 5.25 | 2666.6667 | -124.7466 | 14000 | 4.75 | 2947.3684 | -150.263 | 14000 | 4.2 | 3333.3333 | -191.6397
|  |  | #NUM! | mid | 11200 | 8.1 | 1382.716 | 0 | 11200 | 7.35 | 1523.8095 | 0 | 11200 | 6.6 | 1696.9697 | 0 | 11200 | 5.8 | 1931.0345 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.4 | 2545.4545 | 0
|  |  | #NUM! | min | 7300 | 14 | 521.4286 | 0 | 6700 | 8 | 837.5 | 0 | 6400 | 6.65 | 962.406 | 0 | 6000 | 5.3 | 1132.0755 | 0 | 5600 | 4.4 | 1272.7273 | 0 | 5100 | 3.45 | 1478.2609 | 0
Indoor Temp. |  | 19
LWT |  |  | 25 CAP: 25; 35 CAP: 35; 40 CAP: 40; 45 CAP: 45; 50 CAP: 50; 55 CAP: 55
Outdoor air temperature[℃] |  | Heating Demand | COP | CL | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP
|  |  | LWT |  |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI
| -10 |  | 2.0301 | max | 14600 | 2.4 | 6083.3333 | 2.7532 | 14400 | 2.25 | 6400 | 2.5782 | 14200 | 2.1 | 6761.9048 | 2.406 | 14000 | 1.9 | 7368.4211 | 2.1859 | 14000 | 1.85 | 7567.5676 | 1.9411 | 14000 | 1.75 | 8000 | 1.682
|  | 9586.7769 | 48.1832 | nom | 14000 | 2.8 | 5000 | 3482.0405 | 14000 | 2.5 | 5600 | 3718.331 | 14000 | 2.2 | 6363.6364 | 3984.5916 | 14000 | 1.9 | 7368.4211 | 4385.6473 | 14000 | 1.85 | 7567.5676 | 4938.7813 | 14000 | 1.75 | 8000 | 5699.7789
|  | 28.8832 | 100 | mid | 11200 | 2.85 | 3929.8246 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.1 | 5333.3333 | 1 | 11200 | 1.85 | 6054.0541 | 1
|  | 9618.1031 | 4737.7969 | min | 6200 | 2.55 | 2431.3725 | 0.67736 | 5900 | 2.3 | 2565.2174 | 0.69562 | 5600 | 2.05 | 2731.7073 | 0.71192 | 5300 | 1.75 | 3028.5714 | 0.72657 | 4600 | 1.45 | 3172.4138 | 0.75557 | 4000 | 1.1 | 3636.3636 | 0.77594
| -9 |  | 2.0893 | max | 15100 | 2.5 | 6040 | 2.9592 | 14900 | 2.3333 | 6385.7143 | 2.6307 | 14700 | 2.1667 | 6784.6154 | 2.4371 | 14500 | 1.9667 | 7372.8814 | 2.2107 | 14233.3333 | 1.9167 | 7426.087 | 1.9704 | 14000 | 1.8167 | 7706.422 | 1.7217
|  | 9256.1983 | 47.5259 | nom | 14000 | 2.8833 | 4855.4913 | 3127.9535 | 14000 | 2.6 | 5384.6154 | 3518.4819 | 14000 | 2.3167 | 6043.1655 | 3798.0749 | 14000 | 2.0333 | 6885.2459 | 4186.9324 | 14000 | 1.95 | 7179.4872 | 4697.5824 | 14000 | 1.8167 | 7706.422 | 5376.2753
|  | 27.8885 | 100 | mid | 11200 | 2.9833 | 3754.1899 | 1 | 11200 | 2.8 | 4000 | 1 | 11200 | 2.6167 | 4280.2548 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.1667 | 5169.2308 | 1 | 11200 | 1.9333 | 5793.1034 | 1
|  | 9286.8746 | 4444.8975 | min | 5833.3333 | 2.9167 | 2000 | 0.6378 | 5266.6667 | 2.2833 | 2306.5693 | 0.67239 | 5066.6667 | 2.05 | 2471.5447 | 0.68308 | 4866.6667 | 1.7833 | 2728.972 | 0.69308 | 4266.6667 | 1.4667 | 2909.0909 | 0.71964 | 3700 | 1.1167 | 3313.4328 | 0.74083
| -8 |  | 2.1482 | max | 15600 | 2.6 | 6000 | 3.1828 | 15400 | 2.4167 | 6372.4138 | 2.6806 | 15200 | 2.2333 | 6805.9701 | 2.4673 | 15000 | 2.0333 | 7377.0492 | 2.2371 | 14466.6667 | 1.9833 | 7294.1176 | 1.9986 | 14000 | 1.8833 | 7433.6283 | 1.7591
|  | 8925.6198 | 46.863 | nom | 14000 | 2.9667 | 4719.1011 | 2804.345 | 14000 | 2.7 | 5185.1852 | 3329.6556 | 14000 | 2.4333 | 5753.4247 | 3617.6138 | 14000 | 2.1667 | 6461.5385 | 3989.769 | 14000 | 2.05 | 6829.2683 | 4465.9534 | 14000 | 1.8833 | 7433.6283 | 5073.9754
|  | 26.8834 | 100 | mid | 11200 | 3.1167 | 3593.5829 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.6833 | 4173.913 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.2333 | 5014.9254 | 1 | 11200 | 2.0167 | 5553.719 | 1
|  | 8952.1731 | 4167.1991 | min | 5466.6667 | 3.2833 | 1664.9746 | 0.60331 | 4633.3333 | 2.2667 | 2044.1176 | 0.65365 | 4533.3333 | 2.05 | 2211.3821 | 0.65884 | 4433.3333 | 1.8167 | 2440.367 | 0.66388 | 3933.3333 | 1.4833 | 2651.6854 | 0.68701 | 3400 | 1.1333 | 3000 | 0.70841
| -7 |  | 2.2077 | max | 16100 | 2.7 | 5962.963 | 3.4208 | 15900 | 2.5 | 6360 | 2.7287 | 15700 | 2.3 | 6826.087 | 2.4967 | 15500 | 2.1 | 7380.9524 | 2.2648 | 14700 | 2.05 | 7170.7317 | 2.0258 | 14000 | 1.95 | 7179.4872 | 1.7945
|  | 8595.0413 | 46.1945 | nom | 14000 | 3.05 | 4590.1639 | 2512.5698 | 14000 | 2.8 | 5000 | 3149.9243 | 14000 | 2.55 | 5490.1961 | 3442.5054 | 14000 | 2.3 | 6086.9565 | 3795.0049 | 14000 | 2.15 | 6511.6279 | 4242.8016 | 14000 | 1.95 | 7179.4872 | 4789.711
|  | 25.8694 | 100 | mid | 11200 | 3.25 | 3446.1538 | 1 | 11200 | 3 | 3733.3333 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1 | 11200 | 2.1 | 5333.3333 | 1
|  | 8614.5044 | 3901.9869 | min | 5100 | 3.65 | 1397.2603 | 0.57296 | 4000 | 2.25 | 1777.7778 | 0.6382 | 4000 | 2.05 | 1951.2195 | 0.6382 | 4000 | 1.85 | 2162.1622 | 0.6382 | 3600 | 1.5 | 2400 | 0.65724 | 3100 | 1.15 | 2695.6522 | 0.6784
| -6 |  | 2.2645 | max | 16144.4444 | 2.7611 | 5847.0825 | 3.4968 | 15944.4444 | 2.5556 | 6239.1304 | 2.7795 | 15733.3333 | 2.35 | 6695.0355 | 2.5357 | 15533.3333 | 2.1444 | 7243.5233 | 2.29 | 14744.4444 | 2.0944 | 7039.7878 | 2.0448 | 14033.3333 | 1.9944 | 7036.2117 | 1.8032
|  | 8264.4628 | 45.5201 | nom | 14000 | 3.0889 | 4532.3741 | 2363.4344 | 14000 | 2.8389 | 4931.5068 | 2973.4031 | 14000 | 2.5889 | 5407.7253 | 3259.2485 | 14000 | 2.3389 | 5985.7482 | 3608.982 | 14000 | 2.1944 | 6379.7468 | 4041.615 | 14000 | 2 | 7000 | 4583.1707
|  | 24.8479 | 100 | mid | 11200 | 3.2944 | 3399.6627 | 1 | 11200 | 3.0444 | 3678.8321 | 1 | 11200 | 2.7944 | 4007.9523 | 1 | 11200 | 2.5444 | 4401.7467 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.15 | 5209.3023 | 1
|  | 8274.3463 | 3653.9822 | min | 5155.5556 | 3.7111 | 1389.2216 | 0.51434 | 4122.2222 | 2.4056 | 1713.6259 | 0.58525 | 4077.7778 | 2.1667 | 1882.0513 | 0.58783 | 4022.2222 | 1.9222 | 2092.4855 | 0.59102 | 3611.1111 | 1.5611 | 2313.1673 | 0.61318 | 3111.1111 | 1.1944 | 2604.6512 | 0.63709
| -5 |  | 2.326 | max | 16188.8889 | 2.8222 | 5736.2205 | 3.5752 | 15988.8889 | 2.6111 | 6123.4043 | 2.8411 | 15766.6667 | 2.4 | 6569.4444 | 2.5813 | 15566.6667 | 2.1889 | 7111.6751 | 2.3176 | 14788.8889 | 2.1389 | 6914.2857 | 2.0648 | 14066.6667 | 2.0389 | 6899.1826 | 1.8114
|  | 7933.8843 | 44.8394 | nom | 14000 | 3.1278 | 4476.0213 | 2219.1363 | 14000 | 2.8778 | 4864.8649 | 2792.5783 | 14000 | 2.6278 | 5327.6956 | 3073.5898 | 14000 | 2.3778 | 5887.8505 | 3423.3813 | 14000 | 2.2389 | 6253.1017 | 3842.5061 | 14000 | 2.05 | 6829.2683 | 4379.9963
|  | 23.8341 | 100 | mid | 11200 | 3.3389 | 3354.4093 | 1 | 11200 | 3.0889 | 3625.8993 | 1 | 11200 | 2.8389 | 3945.2055 | 1 | 11200 | 2.5889 | 4326.1803 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.2 | 5090.9091 | 1
|  | 7936.7532 | 3412.1428 | min | 5211.1111 | 3.7722 | 1381.4433 | 0.45464 | 4244.4444 | 2.5611 | 1657.2668 | 0.53043 | 4155.5556 | 2.2833 | 1819.9513 | 0.53636 | 4044.4444 | 1.9944 | 2027.8552 | 0.54356 | 3622.2222 | 1.6222 | 2232.8767 | 0.56899 | 3122.2222 | 1.2389 | 2520.1794 | 0.59567
| -4 |  | 2.3961 | max | 16233.3333 | 2.8833 | 5630.0578 | 3.6561 | 16033.3333 | 2.6667 | 6012.5 | 2.914 | 15800 | 2.45 | 6448.9796 | 2.6338 | 15600 | 2.2333 | 6985.0746 | 2.3476 | 14833.3333 | 2.1833 | 6793.8931 | 2.0856 | 14100 | 2.0833 | 6768 | 1.819
|  | 7603.3058 | 44.1521 | nom | 14000 | 3.1667 | 4421.0526 | 2079.6127 | 14000 | 2.9167 | 4800 | 2609.2129 | 14000 | 2.6667 | 5250 | 2886.8176 | 14000 | 2.4167 | 5793.1034 | 3238.7367 | 14000 | 2.2833 | 6131.3869 | 3645.6601 | 14000 | 2.1 | 6666.6667 | 4179.9575
|  | 22.8753 | 100 | mid | 11200 | 3.3833 | 3310.3448 | 1 | 11200 | 3.1333 | 3574.4681 | 1 | 11200 | 2.8833 | 3884.3931 | 1 | 11200 | 2.6333 | 4253.1646 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.25 | 4977.7778 | 1
|  | 7617.4893 | 3179.055 | min | 5266.6667 | 3.8333 | 1373.913 | 0.39382 | 4366.6667 | 2.7167 | 1607.362 | 0.47365 | 4233.3333 | 2.4 | 1763.8889 | 0.48373 | 4066.6667 | 2.0667 | 1967.7419 | 0.49579 | 3633.3333 | 1.6833 | 2158.4158 | 0.52467 | 3133.3333 | 1.2833 | 2441.5584 | 0.55413
| -3 |  | 2.4768 | max | 16277.7778 | 2.9444 | 5528.3019 | 3.7396 | 16077.7778 | 2.7222 | 5906.1224 | 2.999 | 15833.3333 | 2.5 | 6333.3333 | 2.6934 | 15633.3333 | 2.2778 | 6863.4146 | 2.3802 | 14877.7778 | 2.2278 | 6678.3042 | 2.1073 | 14133.3333 | 2.1278 | 6642.2977 | 1.826
|  | 7272.7273 | 43.4578 | nom | 14000 | 3.2056 | 4367.4177 | 1944.7958 | 14000 | 2.9556 | 4736.8421 | 2425.0752 | 14000 | 2.7056 | 5174.538 | 2700.1949 | 14000 | 2.4556 | 5701.3575 | 3055.557 | 14000 | 2.3278 | 6014.3198 | 3451.2511 | 14000 | 2.15 | 6511.6279 | 3982.8326
|  | 21.9113 | 100 | mid | 11200 | 3.4278 | 3267.423 | 1 | 11200 | 3.1778 | 3524.4755 | 1 | 11200 | 2.9278 | 3825.4269 | 1 | 11200 | 2.6778 | 4182.5726 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1
|  | 7296.4711 | 2945.9506 | min | 5322.2222 | 3.8944 | 1366.6191 | 0.33184 | 4488.8889 | 2.8722 | 1562.8627 | 0.41481 | 4311.1111 | 2.5167 | 1713.0243 | 0.42991 | 4088.8889 | 2.1389 | 1911.6883 | 0.44773 | 3644.4444 | 1.7444 | 2089.172 | 0.48021 | 3144.4444 | 1.3278 | 2368.2008 | 0.51248
| -2 |  | 2.5701 | max | 16322.2222 | 3.0056 | 5430.6839 | 3.8257 | 16122.2222 | 2.7778 | 5804 | 3.0966 | 15866.6667 | 2.55 | 6222.2222 | 2.7604 | 15666.6667 | 2.3222 | 6746.4115 | 2.4152 | 14922.2222 | 2.2722 | 6567.2372 | 2.1299 | 14166.6667 | 2.1722 | 6521.7391 | 1.8325
|  | 6942.1488 | 42.7563 | nom | 14000 | 3.2444 | 4315.0685 | 1814.614 | 14000 | 2.9944 | 4675.3247 | 2241.8841 | 14000 | 2.7444 | 5101.2146 | 2514.9327 | 14000 | 2.4944 | 5612.4722 | 2874.3222 | 14000 | 2.3722 | 5901.6393 | 3259.4412 | 14000 | 2.2 | 6363.6364 | 3788.4083
|  | 20.9394 | 100 | mid | 11200 | 3.4722 | 3225.6 | 1 | 11200 | 3.2222 | 3475.8621 | 1 | 11200 | 2.9722 | 3768.2243 | 1 | 11200 | 2.7222 | 4114.2857 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1
|  | 6972.833 | 2713.0473 | min | 5377.7778 | 3.9556 | 1359.5506 | 0.26869 | 4611.1111 | 3.0278 | 1522.9358 | 0.35378 | 4388.8889 | 2.6333 | 1666.6667 | 0.37487 | 4111.1111 | 2.2111 | 1859.2965 | 0.39936 | 3655.5556 | 1.8056 | 2024.6154 | 0.43563 | 3155.5556 | 1.3722 | 2299.5951 | 0.47071
| -1 |  | 2.6785 | max | 16366.6667 | 3.0667 | 5336.9565 | 3.9145 | 16166.6667 | 2.8333 | 5705.8824 | 3.2075 | 15900 | 2.6 | 6115.3846 | 2.8349 | 15700 | 2.3667 | 6633.8028 | 2.4528 | 14966.6667 | 2.3167 | 6460.4317 | 2.1533 | 14200 | 2.2167 | 6406.015 | 1.8383
|  | 6611.5702 | 42.047 | nom | 14000 | 3.2833 | 4263.9594 | 1688.9916 | 14000 | 3.0333 | 4615.3846 | 2061.2605 | 14000 | 2.7833 | 5029.9401 | 2332.1674 | 14000 | 2.5333 | 5526.3158 | 2695.4806 | 14000 | 2.4167 | 5793.1034 | 3070.381 | 14000 | 2.25 | 6222.2222 | 3596.4781
|  | 19.9554 | 100 | mid | 11200 | 3.5167 | 3184.8341 | 1 | 11200 | 3.2667 | 3428.5714 | 1 | 11200 | 3.0167 | 3712.7072 | 1 | 11200 | 2.7667 | 4048.1928 | 1 | 11200 | 2.6 | 4307.6923 | 1 | 11200 | 2.4 | 4666.6667 | 1
|  | 6645.137 | 2480.9045 | min | 5433.3333 | 4.0167 | 1352.6971 | 0.20432 | 4733.3333 | 3.1833 | 1486.911 | 0.29045 | 4466.6667 | 2.75 | 1624.2424 | 0.31855 | 4133.3333 | 2.2833 | 1810.219 | 0.35069 | 3666.6667 | 1.8667 | 1964.2857 | 0.39092 | 3166.6667 | 1.4167 | 2235.2941 | 0.42883
| 0 |  | 2.8046 | max | 16411.1111 | 3.1278 | 5246.8917 | 4.0061 | 16211.1111 | 2.8889 | 5611.5385 | 3.3326 | 15933.3333 | 2.65 | 6012.5786 | 2.9174 | 15733.3333 | 2.4111 | 6525.3456 | 2.493 | 15011.1111 | 2.3611 | 6357.6471 | 2.1777 | 14233.3333 | 2.2611 | 6294.8403 | 1.8436
|  | 6280.9917 | 41.3294 | nom | 14000 | 3.3222 | 4214.0468 | 1567.8496 | 14000 | 3.0722 | 4556.962 | 1884.6851 | 14000 | 2.8222 | 4960.6299 | 2152.9412 | 14000 | 2.5722 | 5442.7646 | 2519.4462 | 14000 | 2.4611 | 5688.4876 | 2884.2092 | 14000 | 2.3 | 6086.9565 | 3406.8424
|  | 18.953 | 100 | mid | 11200 | 3.5611 | 3145.0858 | 1 | 11200 | 3.3111 | 3382.5503 | 1 | 11200 | 3.0611 | 3658.8022 | 1 | 11200 | 2.8111 | 3984.1897 | 1 | 11200 | 2.65 | 4226.4151 | 1 | 11200 | 2.45 | 4571.4286 | 1
|  | 6311.352 | 2250.3881 | min | 5488.8889 | 4.0778 | 1346.049 | 0.1387 | 4855.5556 | 3.3389 | 1454.2429 | 0.22467 | 4544.4444 | 2.8667 | 1585.2713 | 0.26092 | 4155.5556 | 2.3556 | 1764.1509 | 0.30172 | 3677.7778 | 1.9278 | 1907.781 | 0.34607 | 3177.7778 | 1.4611 | 2174.9049 | 0.38683
| 1 |  | 2.9511 | max | 16455.5556 | 3.1889 | 5160.2787 | 4.1006 | 16255.5556 | 2.9444 | 5520.7547 | 3.4727 | 15966.6667 | 2.7 | 5913.5802 | 3.008 | 15766.6667 | 2.4556 | 6420.8145 | 2.5358 | 15055.5556 | 2.4056 | 6258.6605 | 2.203 | 14266.6667 | 2.3056 | 6187.9518 | 1.8484
|  | 5950.4132 | 40.6031 | nom | 14000 | 3.3611 | 4165.2893 | 1451.1062 | 14000 | 3.1111 | 4500 | 1713.4665 | 14000 | 2.8611 | 4893.2039 | 1978.1876 | 14000 | 2.6111 | 5361.7021 | 2346.597 | 14000 | 2.5056 | 5587.5831 | 2701.0529 | 14000 | 2.35 | 5957.4468 | 3219.3069
|  | 17.9245 | 100 | mid | 11200 | 3.6056 | 3106.3174 | 1 | 11200 | 3.3556 | 3337.7483 | 1 | 11200 | 3.1056 | 3606.4401 | 1 | 11200 | 2.8556 | 3922.179 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.5 | 4480 | 1
|  | 5968.8672 | 2022.6243 | min | 5544.4444 | 4.1389 | 1339.5973 | 0.071782 | 4977.7778 | 3.4944 | 1424.4833 | 0.15632 | 4622.2222 | 2.9833 | 1549.3482 | 0.20192 | 4177.7778 | 2.4278 | 1720.8238 | 0.25243 | 3688.8889 | 1.9889 | 1854.7486 | 0.30109 | 3188.8889 | 1.5056 | 2118.0812 | 0.34471
14kW-Maximum heating CAP | 2 |  | 3.1209 | max | 16500 | 3.25 | 5076.9231 | 4.1981 | 16300 | 3 | 5433.3333 | 3.6287 | 16000 | 2.75 | 5818.1818 | 3.1071 | 15800 | 2.5 | 6320 | 2.5811 | 15100 | 2.45 | 6163.2653 | 2.2292 | 14300 | 2.35 | 6085.1064 | 1.8525
|  | 5619.8347 | 39.8674 | nom | 14000 | 3.4 | 4117.6471 | 1338.6768 | 14000 | 3.15 | 4444.4444 | 1548.7205 | 14000 | 2.9 | 4827.5862 | 1808.7216 | 14000 | 2.65 | 5283.0189 | 2177.274 | 14000 | 2.55 | 5490.1961 | 2521.0271 | 14000 | 2.4 | 5833.3333 | 3033.6828
|  | 16.8869 | 100 | mid | 11200 | 3.65 | 3068.4932 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 3.15 | 3555.5556 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.55 | 4392.1569 | 1
|  | 5623.3362 | 1801.8259 | min | 5600 | 4.2 | 1333.3333 | 0.0035419 | 5100 | 3.65 | 1397.2603 | 0.085219 | 4700 | 3.1 | 1516.129 | 0.14151 | 4200 | 2.5 | 1680 | 0.20283 | 3700 | 2.05 | 1804.878 | 0.25598 | 3200 | 1.55 | 2064.5161 | 0.30248
| 3 |  | 3.3097 | max | 16560 | 3.54 | 4677.9661 | 4.68 | 16360 | 3.25 | 5033.8462 | 3.8024 | 16080 | 2.96 | 5432.4324 | 3.2047 | 15860 | 2.66 | 5962.406 | 2.6139 | 15160 | 2.54 | 5968.5039 | 2.2352 | 14360 | 2.38 | 6033.6134 | 1.8343
|  | 5289.2562 | 39.1216 | nom | 14000 | 3.7 | 3783.7838 | 1130.1829 | 14000 | 3.41 | 4105.5718 | 1391.047 | 14000 | 3.12 | 4487.1795 | 1650.4489 | 14000 | 2.82 | 4964.539 | 2023.5448 | 14000 | 2.67 | 5243.4457 | 2366.3547 | 14000 | 2.47 | 5668.0162 | 2883.5228
|  | 15.9511 | 100 | mid | 11200 | 3.97 | 2821.1587 | 0 | 11200 | 3.68 | 3043.4783 | 1 | 11200 | 3.39 | 3303.8348 | 1 | 11200 | 3.09 | 3624.5955 | 1 | 11200 | 2.88 | 3888.8889 | 1 | 11200 | 2.62 | 4274.8092 | 1
|  | 5311.7055 | 1604.8789 | min | 5380 | 4.68 | 1149.5726 | 0 | 4920 | 3.81 | 1291.3386 | 0.058799 | 4500 | 3.18 | 1415.0943 | 0.1178 | 4000 | 2.51 | 1593.6255 | 0.17906 | 3500 | 2.04 | 1715.6863 | 0.23237 | 3000 | 1.53 | 1960.7843 | 0.27918
| 4 |  | 3.5158 | max | 16620 | 3.83 | 4339.4256 | 5.16 | 16420 | 3.5 | 4691.4286 | 3.9697 | 16160 | 3.17 | 5097.7918 | 3.2953 | 15920 | 2.82 | 5645.3901 | 2.639 | 15220 | 2.63 | 5787.0722 | 2.2358 | 14420 | 2.41 | 5983.4025 | 1.8132
|  | 4958.6777 | 38.365 | nom | 14000 | 4 | 3500 | 960.984 | 14000 | 3.67 | 3814.7139 | 1249.1437 | 14000 | 3.34 | 4191.6168 | 1504.7634 | 14000 | 2.99 | 4682.2742 | 1878.9992 | 14000 | 2.79 | 5017.9211 | 2217.8935 | 14000 | 2.54 | 5511.811 | 2734.7014
|  | 15.0048 | 100 | mid | 11200 | 4.29 | 2610.7226 | 0 | 11200 | 3.96 | 2828.2828 | 1 | 11200 | 3.63 | 3085.3994 | 1 | 11200 | 3.28 | 3414.6341 | 1 | 11200 | 3.01 | 3720.9302 | 1 | 11200 | 2.69 | 4163.5688 | 1
|  | 4996.612 | 1421.1775 | min | 5160 | 5.16 | 1000 | 0 | 4740 | 3.97 | 1193.9547 | 0.033851 | 4300 | 3.26 | 1319.0184 | 0.095461 | 3800 | 2.52 | 1507.9365 | 0.15658 | 3300 | 2.03 | 1625.6158 | 0.20996 | 2800 | 1.51 | 1854.3046 | 0.25699
| 5 |  | 3.7407 | max | 16680 | 4.12 | 4048.5437 | 5.64 | 16480 | 3.75 | 4394.6667 | 4.1311 | 16240 | 3.38 | 4804.7337 | 3.3794 | 15980 | 2.98 | 5362.4161 | 2.6572 | 15280 | 2.72 | 5617.6471 | 2.2313 | 14480 | 2.44 | 5934.4262 | 1.7895
|  | 4628.0992 | 37.5967 | nom | 14000 | 4.3 | 3255.814 | 820.585 | 14000 | 3.93 | 3562.341 | 1120.2991 | 14000 | 3.56 | 3932.5843 | 1369.4945 | 14000 | 3.16 | 4430.3797 | 1741.7468 | 14000 | 2.91 | 4810.9966 | 2074.1784 | 14000 | 2.61 | 5363.9847 | 2586.255
|  | 14.0386 | 100 | mid | 11200 | 4.61 | 2429.5011 | 0 | 11200 | 4.24 | 2641.5094 | 1 | 11200 | 3.87 | 2894.0568 | 1 | 11200 | 3.47 | 3227.6657 | 1 | 11200 | 3.14 | 3566.879 | 1 | 11200 | 2.76 | 4057.971 | 1
|  | 4674.8596 | 1249.7159 | min | 4940 | 5.64 | 875.8865 | 0 | 4560 | 4.13 | 1104.1162 | 0.010256 | 4100 | 3.34 | 1227.5449 | 0.07438 | 3600 | 2.53 | 1422.9249 | 0.13528 | 3100 | 2.02 | 1534.6535 | 0.18865 | 2600 | 1.49 | 1744.9664 | 0.23583
| 6 |  | 3.9877 | max | 16740 | 4.41 | 3795.9184 | 6.12 | 16540 | 4 | 4135 | 4.29 | 16320 | 3.59 | 4545.961 | 3.4576 | 16040 | 3.14 | 5108.2803 | 2.6689 | 15340 | 2.81 | 5459.0747 | 2.2222 | 14540 | 2.47 | 5886.6397 | 1.7633
|  | 4297.5207 | 36.8156 | nom | 14000 | 4.6 | 3043.4783 | 702.2093 | 14000 | 4.19 | 3341.2888 | 1001.7531 | 14000 | 3.78 | 3703.7037 | 1242.9295 | 14000 | 3.33 | 4204.2042 | 1610.2369 | 14000 | 3.03 | 4620.462 | 1933.9439 | 14000 | 2.68 | 5223.8806 | 2437.268
|  | 13.0449 | 100 | mid | 11200 | 4.93 | 2271.8053 | 0 | 11200 | 4.52 | 2477.8761 | 0 | 11200 | 4.11 | 2725.0608 | 1 | 11200 | 3.66 | 3060.1093 | 1 | 11200 | 3.27 | 3425.0765 | 1 | 11200 | 2.83 | 3957.5972 | 1
|  | 4343.9492 | 1089.3277 | min | 4720 | 6.12 | 771.2418 | 0 | 4380 | 4.29 | 1020.979 | 0 | 3900 | 3.42 | 1140.3509 | 0.054455 | 3400 | 2.54 | 1338.5827 | 0.11507 | 2900 | 2.01 | 1442.7861 | 0.16838 | 2400 | 1.47 | 1632.6531 | 0.21563
| 7 |  | 4.2623 | max | 16800 | 4.7 | 3574.4681 | 6.6 | 16600 | 4.25 | 3905.8824 | 4.45 | 16400 | 3.8 | 4315.7895 | 3.5303 | 16100 | 3.3 | 4878.7879 | 2.6746 | 15400 | 2.9 | 5310.3448 | 2.2087 | 14600 | 2.5 | 5840 | 1.7347
|  | 3966.9421 | 36.0204 | nom | 14000 | 4.9 | 2857.1429 | 601.0518 | 14000 | 4.45 | 3146.0674 | 891.4477 | 14000 | 4 | 3500 | 1123.699 | 14000 | 3.5 | 4000 | 1483.1752 | 14000 | 3.15 | 4444.4444 | 1796.075 | 14000 | 2.75 | 5090.9091 | 2286.8517
|  | 12.0169 | 100 | mid | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.8 | 2333.3333 | 0 | 11200 | 4.35 | 2574.7126 | 1 | 11200 | 3.85 | 2909.0909 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 2.9 | 3862.069 | 1
|  | 4001.6406 | 938.8475 | min | 4500 | 6.6 | 681.8182 | 0 | 4200 | 4.45 | 943.8202 | 0 | 3700 | 3.5 | 1057.1429 | 0.035592 | 3200 | 2.55 | 1254.902 | 0.095868 | 2700 | 2 | 1350 | 0.14905 | 2200 | 1.45 | 1517.2414 | 0.19633
| 8 |  | 4.506 | max | 16860 | 4.81 | 3505.1975 | 6.31 | 16640 | 4.38 | 3799.0868 | 4.54 | 16440 | 3.93 | 4183.2061 | 3.73 | 16160 | 3.48 | 4643.6782 | 2.91 | 15440 | 3.06 | 5045.7516 | 2.4076 | 14640 | 2.64 | 5545.4545 | 1.9039
|  | 3636.3636 | 35.2099 | nom | 14000 | 5.02 | 2788.8446 | 576.2858 | 14000 | 4.59 | 3050.1089 | 800.9612 | 14000 | 4.16 | 3365.3846 | 974.8964 | 14000 | 3.69 | 3794.0379 | 1249.6095 | 14000 | 3.32 | 4216.8675 | 1510.3459 | 14000 | 2.9 | 4827.5862 | 1909.9084
|  | 10.937 | 79.3991 | mid | 11200 | 5.37 | 2085.6611 | 0 | 11200 | 4.95 | 2262.6263 | 0 | 11200 | 4.53 | 2472.4062 | 0 | 11200 | 4.06 | 2758.6207 | 0 | 11200 | 3.58 | 3128.4916 | 1 | 11200 | 3.06 | 3660.1307 | 1
|  | 3642.0287 | 808.2615 | min | 4920 | 6.31 | 779.7147 | 0 | 4600 | 4.54 | 1013.2159 | 0 | 4120 | 3.73 | 1104.5576 | 0 | 3640 | 2.91 | 1250.8591 | 0 | 3200 | 2.34 | 1367.5214 | 0.054545 | 2760 | 1.77 | 1559.322 | 0.10383
| 9 |  | 4.7159 | max | 16920 | 4.92 | 3439.0244 | 6.02 | 16680 | 4.51 | 3698.4479 | 4.63 | 16480 | 4.06 | 4059.1133 | 3.96 | 16220 | 3.66 | 4431.694 | 3.27 | 15480 | 3.22 | 4807.4534 | 2.68 | 14680 | 2.78 | 5280.5755 | 2.78
|  | 3305.7851 | 34.3821 | nom | 14000 | 5.14 | 2723.7354 | 549.1337 | 14000 | 4.73 | 2959.8309 | 713.9925 | 14000 | 4.32 | 3240.7407 | 834.7942 | 14000 | 3.88 | 3608.2474 | 1010.9435 | 14000 | 3.49 | 4011.4613 | 1233.5019 | 14000 | 3.05 | 4590.1639 | 1189.1313
|  | 9.9672 | 65.839 | mid | 11200 | 5.49 | 2040.0729 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.71 | 2377.9193 | 0 | 11200 | 4.27 | 2622.9508 | 0 | 11200 | 3.76 | 2978.7234 | 0 | 11200 | 3.22 | 3478.2609 | 4
|  | 3319.0704 | 703.8052 | min | 5340 | 6.02 | 887.0432 | 0 | 5000 | 4.63 | 1079.9136 | 0 | 4540 | 3.96 | 1146.4646 | 0 | 4080 | 3.27 | 1247.7064 | 0 | 3700 | 2.68 | 1380.597 | 0 | 3320 | 2.09 | 1588.5167 | 0
| 10 |  | 4.868 | max | 16980 | 5.03 | 3375.7455 | 5.73 | 16720 | 4.64 | 3603.4483 | 4.72 | 16520 | 4.19 | 3942.7208 | 4.19 | 16280 | 3.84 | 4239.5833 | 3.63 | 15520 | 3.38 | 4591.716 | 3.02 | 14720 | 2.92 | 5041.0959 | 2.41
|  | 2975.2066 | 33.5349 | nom | 14000 | 5.26 | 2661.597 | 519.2333 | 14000 | 4.87 | 2874.7433 | 630.3404 | 14000 | 4.48 | 3125 | 710.0732 | 14000 | 4.07 | 3439.8034 | 819.6161 | 14000 | 3.66 | 3825.1366 | 985.1678 | 14000 | 3.2 | 4375 | 1234.5256
|  | 8.9767 | 54.5635 | mid | 11200 | 5.61 | 1996.4349 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.89 | 2290.3885 | 0 | 11200 | 4.48 | 2500 | 0 | 11200 | 3.94 | 2842.6396 | 0 | 11200 | 3.38 | 3313.6095 | 0
|  | 2989.2389 | 614.0621 | min | 5760 | 5.73 | 1005.2356 | 0 | 5400 | 4.72 | 1144.0678 | 0 | 4960 | 4.19 | 1183.7709 | 0 | 4520 | 3.63 | 1245.1791 | 0 | 4200 | 3.02 | 1390.7285 | 0 | 3880 | 2.41 | 1609.9585 | 0
| 11 |  | 4.9571 | max | 17040 | 5.14 | 3315.1751 | 5.44 | 16760 | 4.77 | 3513.6268 | 4.81 | 16560 | 4.32 | 3833.3333 | 4.42 | 16340 | 4.02 | 4064.6766 | 3.99 | 15560 | 3.54 | 4395.4802 | 3.36 | 14760 | 3.06 | 4823.5294 | 2.73
|  | 2644.6281 | 32.6657 | nom | 14000 | 5.38 | 2602.2305 | 486.1449 | 14000 | 5.01 | 2794.4112 | 549.8187 | 14000 | 4.64 | 3017.2414 | 598.3321 | 14000 | 4.26 | 3286.385 | 662.8141 | 14000 | 3.83 | 3655.3525 | 787.0917 | 14000 | 3.35 | 4179.1045 | 968.7282
|  | 7.9634 | 44.9102 | mid | 11200 | 5.73 | 1954.6248 | 0 | 11200 | 5.4 | 2074.0741 | 0 | 11200 | 5.07 | 2209.073 | 0 | 11200 | 4.69 | 2388.0597 | 0 | 11200 | 4.12 | 2718.4466 | 0 | 11200 | 3.54 | 3163.8418 | 0
|  | 2651.8062 | 534.9552 | min | 6180 | 5.44 | 1136.0294 | 0 | 5800 | 4.81 | 1205.8212 | 0 | 5380 | 4.42 | 1217.1946 | 0 | 4960 | 3.99 | 1243.1078 | 0 | 4700 | 3.36 | 1398.8095 | 0 | 4440 | 2.73 | 1626.3736 | 0
| 12 |  | 4.9807 | max | 17100 | 5.25 | 3257.1429 | 5.15 | 16800 | 4.9 | 3428.5714 | 4.9 | 16600 | 4.45 | 3730.3371 | 4.65 | 16400 | 4.2 | 3904.7619 | 4.35 | 15600 | 3.7 | 4216.2162 | 3.7 | 14800 | 3.2 | 4625 | 3.05
|  | 2314.0496 | 31.771 | nom | 14000 | 5.5 | 2545.4545 | 449.33 | 14000 | 5.15 | 2718.4466 | 472.255 | 14000 | 4.8 | 2916.6667 | 497.6451 | 14000 | 4.45 | 3146.0674 | 531.9654 | 14000 | 4 | 3500 | 625.4188 | 14000 | 3.5 | 4000 | 758.7048
|  | 6.9529 | 36.5617 | mid | 11200 | 5.85 | 1914.5299 | 0 | 11200 | 5.55 | 2018.018 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.9 | 2285.7143 | 0 | 11200 | 4.3 | 2604.6512 | 0 | 11200 | 3.7 | 3027.027 | 0
|  | 2315.3027 | 464.8524 | min | 6600 | 5.15 | 1281.5534 | 0 | 6200 | 4.9 | 1265.3061 | 0 | 5800 | 4.65 | 1247.3118 | 0 | 5400 | 4.35 | 1241.3793 | 0 | 5200 | 3.7 | 1405.4054 | 0 | 5000 | 3.05 | 1639.3443 | 0
| 13 |  | 5.0428 | max | 17566.6667 | 5.2833 | 3324.9211 | 5.15 | 17266.6667 | 4.9333 | 3500 | 4.9667 | 17033.3333 | 4.55 | 3743.5897 | 4.7833 | 16833.3333 | 4.3 | 3914.7287 | 4.55 | 16033.3333 | 3.8 | 4219.2982 | 3.9167 | 15200 | 3.3 | 4606.0606 | 3.2667
|  | 1983.4711 | 30.8461 | nom | 14000 | 5.5 | 2545.4545 | 385.14 | 14000 | 5.1833 | 2700.9646 | 399.3566 | 14000 | 4.8667 | 2876.7123 | 414.6629 | 14000 | 4.55 | 3076.9231 | 435.9277 | 14000 | 4.1 | 3414.6341 | 506.4181 | 14000 | 3.6167 | 3870.9677 | 607.185
|  | 5.9583 | 30.7674 | mid | 11200 | 5.9 | 1898.3051 | 0 | 11200 | 5.5833 | 2005.9701 | 0 | 11200 | 5.3167 | 2106.5831 | 0 | 11200 | 5.0167 | 2232.5581 | 0 | 11200 | 4.4167 | 2535.8491 | 0 | 11200 | 3.8167 | 2934.4978 | 0
|  | 1984.104 | 393.4512 | min | 6700 | 5.15 | 1300.9709 | 0 | 6266.6667 | 4.9667 | 1261.745 | 0 | 5833.3333 | 4.7833 | 1219.5122 | 0 | 5400 | 4.55 | 1186.8132 | 0 | 5233.3333 | 3.9167 | 1336.1702 | 0 | 5066.6667 | 3.2667 | 1551.0204 | 0
| 14 |  | 5.093 | max | 18033.3333 | 5.3167 | 3391.8495 | 5.15 | 17733.3333 | 4.9667 | 3570.4698 | 5.0333 | 17466.6667 | 4.65 | 3756.2724 | 4.9167 | 17266.6667 | 4.4 | 3924.2424 | 4.75 | 16466.6667 | 3.9 | 4222.2222 | 4.1333 | 15600 | 3.4 | 4588.2353 | 3.4833
|  | 1652.8926 | 29.8848 | nom | 14000 | 5.5 | 2545.4545 | 320.95 | 14000 | 5.2167 | 2683.7061 | 328.3893 | 14000 | 4.9333 | 2837.8378 | 336.1815 | 14000 | 4.65 | 3010.7527 | 347.9774 | 14000 | 4.2 | 3333.3333 | 399.8934 | 14000 | 3.7333 | 3750 | 474.5146
|  | 4.9643 | 25.1504 | mid | 11200 | 5.95 | 1882.3529 | 0 | 11200 | 5.6167 | 1994.0653 | 0 | 11200 | 5.3833 | 2080.4954 | 0 | 11200 | 5.1333 | 2181.8182 | 0 | 11200 | 4.5333 | 2470.5882 | 0 | 11200 | 3.9333 | 2847.4576 | 0
|  | 1653.1094 | 324.584 | min | 6800 | 5.15 | 1320.3883 | 0 | 6333.3333 | 5.0333 | 1258.2781 | 0 | 5866.6667 | 4.9167 | 1193.2203 | 0 | 5400 | 4.75 | 1136.8421 | 0 | 5266.6667 | 4.1333 | 1274.1935 | 0 | 5133.3333 | 3.4833 | 1473.6842 | 0
| 15 |  | 5.1306 | max | 18500 | 5.35 | 3457.9439 | 5.15 | 18200 | 5 | 3640 | 5.1 | 17900 | 4.75 | 3768.4211 | 5.05 | 17700 | 4.5 | 3933.3333 | 4.95 | 16900 | 4 | 4225 | 4.35 | 16000 | 3.5 | 4571.4286 | 3.7
|  | 1322.314 | 28.8778 | nom | 14000 | 5.5 | 2545.4545 | 256.76 | 14000 | 5.25 | 2666.6667 | 259.2773 | 14000 | 5 | 2800 | 261.8444 | 14000 | 4.75 | 2947.3684 | 267.1342 | 14000 | 4.3 | 3255.814 | 303.9802 | 14000 | 3.85 | 3636.3636 | 357.3822
|  | 3.971 | 19.718 | mid | 11200 | 6 | 1866.6667 | 0 | 11200 | 5.65 | 1982.3009 | 0 | 11200 | 5.45 | 2055.0459 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.65 | 2408.6022 | 0 | 11200 | 4.05 | 2765.4321 | 0
|  | 1322.3439 | 257.7361 | min | 6900 | 5.15 | 1339.8058 | 0 | 6400 | 5.1 | 1254.902 | 0 | 5900 | 5.05 | 1168.3168 | 0 | 5400 | 4.95 | 1090.9091 | 0 | 5300 | 4.35 | 1218.3908 | 0 | 5200 | 3.7 | 1405.4054 | 0
| 16 |  | 6.5715 | max | 19020 | 5.73 | 3319.3717 | 6.92 | 18720 | 5.3 | 3532.0755 | 5.68 | 18420 | 4.95 | 3721.2121 | 5.37 | 18200 | 4.59 | 3965.1416 | 5.02 | 17380 | 4.08 | 4259.8039 | 4.36 | 16460 | 3.56 | 4623.5955 | 3.65
|  | 991.7355 | 27.8102 | nom | 14000 | 5.93 | 2360.8769 | 143.3144 | 14000 | 5.57 | 2513.465 | 174.6013 | 14000 | 5.21 | 2687.1401 | 184.6807 | 14000 | 4.85 | 2886.5979 | 197.5569 | 14000 | 4.39 | 3189.0661 | 227.4623 | 14000 | 3.92 | 3571.4286 | 271.7084
|  | 3.0017 | 14.5121 | mid | 11200 | 6.42 | 1744.5483 | 0 | 11200 | 5.99 | 1869.783 | 0 | 11200 | 5.68 | 1971.831 | 0 | 11200 | 5.36 | 2089.5522 | 0 | 11200 | 4.74 | 2362.8692 | 0 | 11200 | 4.12 | 2718.4466 | 0
|  | 999.5741 | 152.1066 | min | 6980 | 6.92 | 1008.6705 | 0 | 6460 | 5.68 | 1137.3239 | 0 | 6000 | 5.37 | 1117.3184 | 0 | 5520 | 5.02 | 1099.6016 | 0 | 5360 | 4.36 | 1229.3578 | 0 | 5180 | 3.65 | 1419.1781 | 0
| 17 |  | 8.2878 | max | 19540 | 6.11 | 3198.036 | 8.69 | 19240 | 5.6 | 3435.7143 | 6.26 | 18940 | 5.15 | 3677.6699 | 5.69 | 18700 | 4.68 | 3995.7265 | 5.09 | 17860 | 4.16 | 4293.2692 | 4.37 | 16920 | 3.62 | 4674.0331 | 3.6
|  | 661.157 | 26.6553 | nom | 14000 | 6.36 | 2201.2579 | 76.0825 | 14000 | 5.89 | 2376.91 | 105.6161 | 14000 | 5.42 | 2583.0258 | 116.1963 | 14000 | 4.95 | 2828.2828 | 129.8933 | 14000 | 4.48 | 3125 | 151.2945 | 14000 | 3.99 | 3508.7719 | 183.6547
|  | 2.0152 | 9.4849 | mid | 11200 | 6.84 | 1637.4269 | 0 | 11200 | 6.33 | 1769.3523 | 0 | 11200 | 5.91 | 1895.0931 | 0 | 11200 | 5.47 | 2047.532 | 0 | 11200 | 4.83 | 2318.8406 | 0 | 11200 | 4.19 | 2673.031 | 0
|  | 671.0702 | 80.9712 | min | 7060 | 8.69 | 812.4281 | 0 | 6520 | 6.26 | 1041.5335 | 0 | 6100 | 5.69 | 1072.0562 | 0 | 5640 | 5.09 | 1108.055 | 0 | 5420 | 4.37 | 1240.2746 | 0 | 5160 | 3.6 | 1433.3333 | 0
| 18 |  | 10.3328 | max | 20060 | 6.49 | 3090.9091 | 10.46 | 19760 | 5.9 | 3349.1525 | 6.84 | 19460 | 5.35 | 3637.3832 | 6.01 | 19200 | 4.77 | 4025.1572 | 5.16 | 18340 | 4.24 | 4325.4717 | 4.38 | 17380 | 3.68 | 4722.8261 | 3.55
|  | 330.5785 | 25.3513 | nom | 14000 | 6.79 | 2061.8557 | 31.6041 | 14000 | 6.21 | 2254.4283 | 48.3302 | 14000 | 5.63 | 2486.6785 | 55.0047 | 14000 | 5.05 | 2772.2772 | 64.0656 | 14000 | 4.57 | 3063.4573 | 75.4745 | 14000 | 4.06 | 3448.2759 | 93.1207
|  | 0.99889 | 4.6427 | mid | 11200 | 7.26 | 1542.6997 | 0 | 11200 | 6.67 | 1679.1604 | 0 | 11200 | 6.14 | 1824.1042 | 0 | 11200 | 5.58 | 2007.1685 | 0 | 11200 | 4.92 | 2276.4228 | 0 | 11200 | 4.26 | 2629.108 | 0
|  | 332.6309 | 32.1917 | min | 7140 | 10.46 | 682.6004 | 0 | 6580 | 6.84 | 961.9883 | 0 | 6200 | 6.01 | 1031.614 | 0 | 5760 | 5.16 | 1116.2791 | 0 | 5480 | 4.38 | 1251.1416 | 0 | 5140 | 3.55 | 1447.8873 | 0
| 19 |  | 12.23 | max | 20580 | 6.87 | 2995.6332 | 12.23 | 20280 | 6.2 | 3270.9677 | 7.42 | 19980 | 5.55 | 3600 | 6.33 | 19700 | 4.86 | 4053.4979 | 5.23 | 18820 | 4.32 | 4356.4815 | 4.39 | 17840 | 3.74 | 4770.0535 | 3.5
|  | 0 | 23.5 | nom | 14000 | 7.22 | 1939.0582 | 0 | 14000 | 6.53 | 2143.951 | 0 | 14000 | 5.84 | 2397.2603 | 0 | 14000 | 5.15 | 2718.4466 | 0 | 14000 | 4.66 | 3004.2918 | 0 | 14000 | 4.13 | 3389.8305 | 0
|  | 0 | 0 | mid | 11200 | 7.68 | 1458.3333 | 0 | 11200 | 7.01 | 1597.7175 | 0 | 11200 | 6.37 | 1758.2418 | 0 | 11200 | 5.69 | 1968.3656 | 0 | 11200 | 5.01 | 2235.5289 | 0 | 11200 | 4.33 | 2586.6051 | 0
|  | 0 | 0 | min | 7220 | 12.23 | 590.3516 | 0 | 6640 | 7.42 | 894.8787 | 0 | 6300 | 6.33 | 995.2607 | 0 | 5880 | 5.23 | 1124.283 | 0 | 5540 | 4.39 | 1261.959 | 0 | 5120 | 3.5 | 1462.8571 | 0
| 20 |  | #NUM! | max | 21100 | 7.25 | 2910.3448 | 14 | 20800 | 6.5 | 3200 | 8 | 20500 | 5.75 | 3565.2174 | 6.65 | 20200 | 4.95 | 4080.8081 | 5.3 | 19300 | 4.4 | 4386.3636 | 4.4 | 18300 | 3.8 | 4815.7895 | 3.45
|  | -330.5785 | #NUM! | nom | 14000 | 7.65 | 1830.0654 | -23.6128 | 14000 | 6.85 | 2043.7956 | -41.3223 | 14000 | 6.05 | 2314.0496 | -49.7111 | 14000 | 5.25 | 2666.6667 | -62.3733 | 14000 | 4.75 | 2947.3684 | -75.1315 | 14000 | 4.2 | 3333.3333 | -95.8199
|  | #NUM! | #NUM! | mid | 11200 | 8.1 | 1382.716 | 0 | 11200 | 7.35 | 1523.8095 | 0 | 11200 | 6.6 | 1696.9697 | 0 | 11200 | 5.8 | 1931.0345 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.4 | 2545.4545 | 0
|  | #NUM! | #NUM! | min | 7300 | 14 | 521.4286 | 0 | 6700 | 8 | 837.5 | 0 | 6400 | 6.65 | 962.406 | 0 | 6000 | 5.3 | 1132.0755 | 0 | 5600 | 4.4 | 1272.7273 | 0 | 5100 | 3.45 | 1478.2609 | 0
Indoor Temp. |  | 20
LWT |  |  | 25 CAP: 25; 35 CAP: 35; 40 CAP: 40; 45 CAP: 45; 50 CAP: 50; 55 CAP: 55
Outdoor air temperature[℃] |  | Heating Demand | COP | CL | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP
|  |  | LWT |  |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI
| -10 |  | 2.031 | max | 14600 | 2.4 | 6083.3333 | 2.773 | 14400 | 2.25 | 6400 | 2.6032 | 14200 | 2.1 | 6761.9048 | 2.4355 | 14000 | 1.9 | 7368.4211 | 2.2196 | 14000 | 1.85 | 7567.5676 | 1.9737 | 14000 | 1.75 | 8000 | 1.7164
|  | 9917.3554 | 48.8354 | nom | 14000 | 2.8 | 5000 | 3576.346 | 14000 | 2.5 | 5600 | 3809.6835 | 14000 | 2.2 | 6363.6364 | 4072.0363 | 14000 | 1.9 | 7368.4211 | 4468.1596 | 14000 | 1.85 | 7567.5676 | 5024.8068 | 14000 | 1.75 | 8000 | 5778.0274
|  | 29.8553 | 100 | mid | 11200 | 2.85 | 3929.8246 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.1 | 5333.3333 | 1 | 11200 | 1.85 | 6054.0541 | 1
|  | 9941.81 | 4895.1503 | min | 6200 | 2.55 | 2431.3725 | 0.74347 | 5900 | 2.3 | 2565.2174 | 0.75799 | 5600 | 2.05 | 2731.7073 | 0.77096 | 5300 | 1.75 | 3028.5714 | 0.7826 | 4600 | 1.45 | 3172.4138 | 0.80566 | 4000 | 1.1 | 3636.3636 | 0.82185
| -9 |  | 2.0907 | max | 15100 | 2.5 | 6040 | 2.9633 | 14900 | 2.3333 | 6385.7143 | 2.6595 | 14700 | 2.1667 | 6784.6154 | 2.4676 | 14500 | 1.9667 | 7372.8814 | 2.2429 | 14233.3333 | 1.9167 | 7426.087 | 2.0038 | 14000 | 1.8167 | 7706.422 | 1.7577
|  | 9586.7769 | 48.1832 | nom | 14000 | 2.8833 | 4855.4913 | 3235.1765 | 14000 | 2.6 | 5384.6154 | 3604.6983 | 14000 | 2.3167 | 6043.1655 | 3885.0314 | 14000 | 2.0333 | 6885.2459 | 4274.2336 | 14000 | 1.95 | 7179.4872 | 4784.3146 | 14000 | 1.8167 | 7706.422 | 5454.2491
|  | 28.8739 | 100 | mid | 11200 | 2.9833 | 3754.1899 | 1 | 11200 | 2.8 | 4000 | 1 | 11200 | 2.6167 | 4280.2548 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.1667 | 5169.2308 | 1 | 11200 | 1.9333 | 5793.1034 | 1
|  | 9614.9933 | 4598.9737 | min | 5833.3333 | 2.9167 | 2000 | 0.6994 | 5266.6667 | 2.2833 | 2306.5693 | 0.72811 | 5066.6667 | 2.05 | 2471.5447 | 0.73697 | 4866.6667 | 1.7833 | 2728.972 | 0.74528 | 4266.6667 | 1.4667 | 2909.0909 | 0.76732 | 3700 | 1.1167 | 3313.4328 | 0.7849
| -8 |  | 2.1492 | max | 15600 | 2.6 | 6000 | 3.1732 | 15400 | 2.4167 | 6372.4138 | 2.7125 | 15200 | 2.2333 | 6805.9701 | 2.4987 | 15000 | 2.0333 | 7377.0492 | 2.2681 | 14466.6667 | 1.9833 | 7294.1176 | 2.0327 | 14000 | 1.8833 | 7433.6283 | 1.7965
|  | 9256.1983 | 47.5259 | nom | 14000 | 2.9667 | 4719.1011 | 2917.017 | 14000 | 2.7 | 5185.1852 | 3412.3897 | 14000 | 2.4333 | 5753.4247 | 3704.4469 | 14000 | 2.1667 | 6461.5385 | 4081.0942 | 14000 | 2.05 | 6829.2683 | 4553.6211 | 14000 | 1.8833 | 7433.6283 | 5152.2497
|  | 27.8799 | 100 | mid | 11200 | 3.1167 | 3593.5829 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.6833 | 4173.913 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.2333 | 5014.9254 | 1 | 11200 | 2.0167 | 5553.719 | 1
|  | 9283.9984 | 4319.8007 | min | 5466.6667 | 3.2833 | 1664.9746 | 0.66096 | 4633.3333 | 2.2667 | 2044.1176 | 0.70399 | 4533.3333 | 2.05 | 2211.3821 | 0.70843 | 4433.3333 | 1.8167 | 2440.367 | 0.71274 | 3933.3333 | 1.4833 | 2651.6854 | 0.7325 | 3400 | 1.1333 | 3000 | 0.75079
| -7 |  | 2.2075 | max | 16100 | 2.7 | 5962.963 | 3.3991 | 15900 | 2.5 | 6360 | 2.7631 | 15700 | 2.3 | 6826.087 | 2.5289 | 15500 | 2.1 | 7380.9524 | 2.2947 | 14700 | 2.05 | 7170.7317 | 2.0606 | 14000 | 1.95 | 7179.4872 | 1.8333
|  | 8925.6198 | 46.863 | nom | 14000 | 3.05 | 4590.1639 | 2625.8467 | 14000 | 2.8 | 5000 | 3230.3091 | 14000 | 2.55 | 5490.1961 | 3529.4758 | 14000 | 2.3 | 6086.9565 | 3889.7115 | 14000 | 2.15 | 6511.6279 | 4331.5813 | 14000 | 1.95 | 7179.4872 | 4868.7367
|  | 26.8763 | 100 | mid | 11200 | 3.25 | 3446.1538 | 1 | 11200 | 3 | 3733.3333 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1 | 11200 | 2.1 | 5333.3333 | 1
|  | 8949.7997 | 4054.3557 | min | 5100 | 3.65 | 1397.2603 | 0.62715 | 4000 | 2.25 | 1777.7778 | 0.68411 | 4000 | 2.05 | 1951.2195 | 0.68411 | 4000 | 1.85 | 2162.1622 | 0.68411 | 3600 | 1.5 | 2400 | 0.70074 | 3100 | 1.15 | 2695.6522 | 0.71921
| -6 |  | 2.2614 | max | 16144.4444 | 2.7611 | 5847.0825 | 3.474 | 15944.4444 | 2.5556 | 6239.1304 | 2.8093 | 15733.3333 | 2.35 | 6695.0355 | 2.5648 | 15533.3333 | 2.1444 | 7243.5233 | 2.3186 | 14744.4444 | 2.0944 | 7039.7878 | 2.0792 | 14033.3333 | 1.9944 | 7036.2117 | 1.8423
|  | 8595.0413 | 46.1945 | nom | 14000 | 3.0889 | 4532.3741 | 2474.095 | 14000 | 2.8389 | 4931.5068 | 3059.4925 | 14000 | 2.5889 | 5407.7253 | 3351.1099 | 14000 | 2.3389 | 5985.7482 | 3706.9521 | 14000 | 2.1944 | 6379.7468 | 4133.8087 | 14000 | 2 | 7000 | 4665.4589
|  | 25.8667 | 100 | mid | 11200 | 3.2944 | 3399.6627 | 1 | 11200 | 3.0444 | 3678.8321 | 1 | 11200 | 2.7944 | 4007.9523 | 1 | 11200 | 2.5444 | 4401.7467 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.15 | 5209.3023 | 1
|  | 8613.6242 | 3808.9313 | min | 5155.5556 | 3.7111 | 1389.2216 | 0.56903 | 4122.2222 | 2.4056 | 1713.6259 | 0.63195 | 4077.7778 | 2.1667 | 1882.0513 | 0.63425 | 4022.2222 | 1.9222 | 2092.4855 | 0.63708 | 3611.1111 | 1.5611 | 2313.1673 | 0.65674 | 3111.1111 | 1.1944 | 2604.6512 | 0.67796
| -5 |  | 2.3194 | max | 16188.8889 | 2.8222 | 5736.2205 | 3.5513 | 15988.8889 | 2.6111 | 6123.4043 | 2.8661 | 15766.6667 | 2.4 | 6569.4444 | 2.6074 | 15566.6667 | 2.1889 | 7111.6751 | 2.345 | 14788.8889 | 2.1389 | 6914.2857 | 2.0987 | 14066.6667 | 2.0389 | 6899.1826 | 1.8507
|  | 8264.4628 | 45.5201 | nom | 14000 | 3.1278 | 4476.0213 | 2327.1699 | 14000 | 2.8778 | 4864.8649 | 2883.4774 | 14000 | 2.6278 | 5327.6956 | 3169.6431 | 14000 | 2.3778 | 5887.8505 | 3524.2604 | 14000 | 2.2389 | 6253.1017 | 3937.899 | 14000 | 2.05 | 6829.2683 | 4465.5306
|  | 24.8467 | 100 | mid | 11200 | 3.3389 | 3354.4093 | 1 | 11200 | 3.0889 | 3625.8993 | 1 | 11200 | 2.8389 | 3945.2055 | 1 | 11200 | 2.5889 | 4326.1803 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.2 | 5090.9091 | 1
|  | 8273.9584 | 3567.2849 | min | 5211.1111 | 3.7722 | 1381.4433 | 0.50984 | 4244.4444 | 2.5611 | 1657.2668 | 0.57796 | 4155.5556 | 2.2833 | 1819.9513 | 0.58328 | 4044.4444 | 1.9944 | 2027.8552 | 0.58975 | 3622.2222 | 1.6222 | 2232.8767 | 0.61261 | 3122.2222 | 1.2389 | 2520.1794 | 0.63659
| -4 |  | 2.383 | max | 16233.3333 | 2.8833 | 5630.0578 | 3.631 | 16033.3333 | 2.6667 | 6012.5 | 2.9342 | 15800 | 2.45 | 6448.9796 | 2.6567 | 15600 | 2.2333 | 6985.0746 | 2.3739 | 14833.3333 | 2.1833 | 6793.8931 | 2.1191 | 14100 | 2.0833 | 6768 | 1.8586
|  | 7933.8843 | 44.8394 | nom | 14000 | 3.1667 | 4421.0526 | 2185.0144 | 14000 | 2.9167 | 4800 | 2703.9529 | 14000 | 2.6667 | 5250 | 2986.3268 | 14000 | 2.4167 | 5793.1034 | 3342.1652 | 14000 | 2.2833 | 6131.3869 | 3744.0372 | 14000 | 2.1 | 6666.6667 | 4268.7285
|  | 23.8349 | 100 | mid | 11200 | 3.3833 | 3310.3448 | 1 | 11200 | 3.1333 | 3574.4681 | 1 | 11200 | 2.8833 | 3884.3931 | 1 | 11200 | 2.6333 | 4253.1646 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.25 | 4977.7778 | 1
|  | 7937.0143 | 3330.7324 | min | 5266.6667 | 3.8333 | 1373.913 | 0.44953 | 4366.6667 | 2.7167 | 1607.362 | 0.52203 | 4233.3333 | 2.4 | 1763.8889 | 0.53118 | 4066.6667 | 2.0667 | 1967.7419 | 0.54213 | 3633.3333 | 1.6833 | 2158.4158 | 0.56835 | 3133.3333 | 1.2833 | 2441.5584 | 0.59511
| -3 |  | 2.4574 | max | 16277.7778 | 2.9444 | 5528.3019 | 3.7133 | 16077.7778 | 2.7222 | 5906.1224 | 3.014 | 15833.3333 | 2.5 | 6333.3333 | 2.7131 | 15633.3333 | 2.2778 | 6863.4146 | 2.4052 | 14877.7778 | 2.2278 | 6678.3042 | 2.1403 | 14133.3333 | 2.1278 | 6642.2977 | 1.8659
|  | 7603.3058 | 44.1521 | nom | 14000 | 3.2056 | 4367.4177 | 2047.5665 | 14000 | 2.9556 | 4736.8421 | 2522.6453 | 14000 | 2.7056 | 5174.538 | 2802.4046 | 14000 | 2.4556 | 5701.3575 | 3161.1741 | 14000 | 2.3278 | 6014.3198 | 3552.3979 | 14000 | 2.15 | 6511.6279 | 4074.8377
|  | 22.8795 | 100 | mid | 11200 | 3.4278 | 3267.423 | 1 | 11200 | 3.1778 | 3524.4755 | 1 | 11200 | 2.9278 | 3825.4269 | 1 | 11200 | 2.6778 | 4182.5726 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1
|  | 7618.8635 | 3100.3306 | min | 5322.2222 | 3.8944 | 1366.6191 | 0.38809 | 4488.8889 | 2.8722 | 1562.8627 | 0.46407 | 4311.1111 | 2.5167 | 1713.0243 | 0.4779 | 4088.8889 | 2.1389 | 1911.6883 | 0.49421 | 3644.4444 | 1.7444 | 2089.172 | 0.52397 | 3144.4444 | 1.3278 | 2368.2008 | 0.55351
| -2 |  | 2.5432 | max | 16322.2222 | 3.0056 | 5430.6839 | 3.7982 | 16122.2222 | 2.7778 | 5804 | 3.1063 | 15866.6667 | 2.55 | 6222.2222 | 2.7768 | 15666.6667 | 2.3222 | 6746.4115 | 2.4391 | 14922.2222 | 2.2722 | 6567.2372 | 2.1625 | 14166.6667 | 2.1722 | 6521.7391 | 1.8727
|  | 7272.7273 | 43.4578 | nom | 14000 | 3.2444 | 4315.0685 | 1914.7595 | 14000 | 2.9944 | 4675.3247 | 2341.2644 | 14000 | 2.7444 | 5101.2146 | 2619.0853 | 14000 | 2.4944 | 5612.4722 | 2981.769 | 14000 | 2.3722 | 5901.6393 | 3363.1447 | 14000 | 2.2 | 6363.6364 | 3883.6514
|  | 21.9185 | 100 | mid | 11200 | 3.4722 | 3225.6 | 1 | 11200 | 3.2222 | 3475.8621 | 1 | 11200 | 2.9722 | 3768.2243 | 1 | 11200 | 2.7222 | 4114.2857 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1
|  | 7298.8565 | 2869.9044 | min | 5377.7778 | 3.9556 | 1359.5506 | 0.32547 | 4611.1111 | 3.0278 | 1522.9358 | 0.40396 | 4388.8889 | 2.6333 | 1666.6667 | 0.4234 | 4111.1111 | 2.2111 | 1859.2965 | 0.446 | 3655.5556 | 1.8056 | 2024.6154 | 0.47945 | 3155.5556 | 1.3722 | 2299.5951 | 0.5118
| -1 |  | 2.6426 | max | 16366.6667 | 3.0667 | 5336.9565 | 3.8858 | 16166.6667 | 2.8333 | 5705.8824 | 3.2118 | 15900 | 2.6 | 6115.3846 | 2.848 | 15700 | 2.3667 | 6633.8028 | 2.4754 | 14966.6667 | 2.3167 | 6460.4317 | 2.1855 | 14200 | 2.2167 | 6406.015 | 1.8788
|  | 6942.1488 | 42.7563 | nom | 14000 | 3.2833 | 4263.9594 | 1786.5225 | 14000 | 3.0333 | 4615.3846 | 2161.4529 | 14000 | 2.7833 | 5029.9401 | 2437.5189 | 14000 | 2.5333 | 5526.3158 | 2804.4036 | 14000 | 2.4167 | 5793.1034 | 3176.4304 | 14000 | 2.25 | 6222.2222 | 3694.9697
|  | 20.9488 | 100 | mid | 11200 | 3.5167 | 3184.8341 | 1 | 11200 | 3.2667 | 3428.5714 | 1 | 11200 | 3.0167 | 3712.7072 | 1 | 11200 | 2.7667 | 4048.1928 | 1 | 11200 | 2.6 | 4307.6923 | 1 | 11200 | 2.4 | 4666.6667 | 1
|  | 6975.9643 | 2639.7652 | min | 5433.3333 | 4.0167 | 1352.6971 | 0.26164 | 4733.3333 | 3.1833 | 1486.911 | 0.34157 | 4466.6667 | 2.75 | 1624.2424 | 0.36765 | 4133.3333 | 2.2833 | 1810.219 | 0.39747 | 3666.6667 | 1.8667 | 1964.2857 | 0.4348 | 3166.6667 | 1.4167 | 2235.2941 | 0.46998
| 0 |  | 2.7581 | max | 16411.1111 | 3.1278 | 5246.8917 | 3.9762 | 16211.1111 | 2.8889 | 5611.5385 | 3.3312 | 15933.3333 | 2.65 | 6012.5786 | 2.9271 | 15733.3333 | 2.4111 | 6525.3456 | 2.5144 | 15011.1111 | 2.3611 | 6357.6471 | 2.2095 | 14233.3333 | 2.2611 | 6294.8403 | 1.8844
|  | 6611.5702 | 42.047 | nom | 14000 | 3.3222 | 4214.0468 | 1662.781 | 14000 | 3.0722 | 4556.962 | 1984.741 | 14000 | 2.8222 | 4960.6299 | 2258.7763 | 14000 | 2.5722 | 5442.7646 | 2629.5001 | 14000 | 2.4611 | 5688.4876 | 2992.3966 | 14000 | 2.3 | 6086.9565 | 3508.5993
|  | 19.9656 | 100 | mid | 11200 | 3.5611 | 3145.0858 | 1 | 11200 | 3.3111 | 3382.5503 | 1 | 11200 | 3.0611 | 3658.8022 | 1 | 11200 | 2.8111 | 3984.1897 | 1 | 11200 | 2.65 | 4226.4151 | 1 | 11200 | 2.45 | 4571.4286 | 1
|  | 6648.5614 | 2410.5472 | min | 5488.8889 | 4.0778 | 1346.049 | 0.19658 | 4855.5556 | 3.3389 | 1454.2429 | 0.27678 | 4544.4444 | 2.8667 | 1585.2713 | 0.31059 | 4155.5556 | 2.3556 | 1764.1509 | 0.34865 | 3677.7778 | 1.9278 | 1907.781 | 0.39002 | 3177.7778 | 1.4611 | 2174.9049 | 0.42804
| 1 |  | 2.8923 | max | 16455.5556 | 3.1889 | 5160.2787 | 4.0694 | 16255.5556 | 2.9444 | 5520.7547 | 3.4654 | 15966.6667 | 2.7 | 5913.5802 | 3.0142 | 15766.6667 | 2.4556 | 6420.8145 | 2.5559 | 15055.5556 | 2.4056 | 6258.6605 | 2.2343 | 14266.6667 | 2.3056 | 6187.9518 | 1.8894
|  | 6280.9917 | 41.3294 | nom | 14000 | 3.3611 | 4165.2893 | 1543.4571 | 14000 | 3.1111 | 4500 | 1812.5104 | 14000 | 2.8611 | 4893.2039 | 2083.8317 | 14000 | 2.6111 | 5361.7021 | 2457.4474 | 14000 | 2.5056 | 5587.5831 | 2811.1738 | 14000 | 2.35 | 5957.4468 | 3324.3525
|  | 18.9622 | 100 | mid | 11200 | 3.6056 | 3106.3174 | 1 | 11200 | 3.3556 | 3337.7483 | 1 | 11200 | 3.1056 | 3606.4401 | 1 | 11200 | 2.8556 | 3922.179 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.5 | 4480 | 1
|  | 6314.4102 | 2183.1692 | min | 5544.4444 | 4.1389 | 1339.5973 | 0.13023 | 4977.7778 | 3.4944 | 1424.4833 | 0.20945 | 4622.2222 | 2.9833 | 1549.3482 | 0.25218 | 4177.7778 | 2.4278 | 1720.8238 | 0.29951 | 3688.8889 | 1.9889 | 1854.7486 | 0.3451 | 3188.8889 | 1.5056 | 2118.0812 | 0.38598
14kW-Maximum heating CAP | 2 |  | 3.0482 | max | 16500 | 3.25 | 5076.9231 | 4.1656 | 16300 | 3 | 5433.3333 | 3.6151 | 16000 | 2.75 | 5818.1818 | 3.1096 | 15800 | 2.5 | 6320 | 2.6 | 15100 | 2.45 | 6163.2653 | 2.26 | 14300 | 2.35 | 6085.1064 | 1.8938
|  | 5950.4132 | 40.6031 | nom | 14000 | 3.4 | 4117.6471 | 1428.4702 | 14000 | 3.15 | 4444.4444 | 1645.9672 | 14000 | 2.9 | 4827.5862 | 1913.5508 | 14000 | 2.65 | 5283.0189 | 2288.5997 | 14000 | 2.55 | 5490.1961 | 2632.8813 | 14000 | 2.4 | 5833.3333 | 3142.0467
|  | 17.93 | 100 | mid | 11200 | 3.65 | 3068.4932 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 3.15 | 3555.5556 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.55 | 4392.1569 | 1
|  | 5970.6854 | 1958.7883 | min | 5600 | 4.2 | 1333.3333 | 0.062574 | 5100 | 3.65 | 1397.2603 | 0.13941 | 4700 | 3.1 | 1516.129 | 0.19237 | 4200 | 2.5 | 1680 | 0.25006 | 3700 | 2.05 | 1804.878 | 0.30006 | 3200 | 1.55 | 2064.5161 | 0.3438
| 3 |  | 3.2305 | max | 16560 | 3.54 | 4677.9661 | 4.6507 | 16360 | 3.25 | 5033.8462 | 3.7955 | 16080 | 2.96 | 5432.4324 | 3.2151 | 15860 | 2.66 | 5962.406 | 2.6405 | 15160 | 2.54 | 5968.5039 | 2.2713 | 14360 | 2.38 | 6033.6134 | 1.8782
|  | 5619.8347 | 39.8674 | nom | 14000 | 3.7 | 3783.7838 | 1208.3738 | 14000 | 3.41 | 4105.5718 | 1480.6522 | 14000 | 3.12 | 4487.1795 | 1747.9506 | 14000 | 2.82 | 4964.539 | 2128.3329 | 14000 | 2.67 | 5243.4457 | 2474.3305 | 14000 | 2.47 | 5668.0162 | 2992.0648
|  | 16.8884 | 100 | mid | 11200 | 3.97 | 2821.1587 | 1 | 11200 | 3.68 | 3043.4783 | 1 | 11200 | 3.39 | 3303.8348 | 1 | 11200 | 3.09 | 3624.5955 | 1 | 11200 | 2.88 | 3888.8889 | 1 | 11200 | 2.62 | 4274.8092 | 1
|  | 5623.8403 | 1740.8614 | min | 5380 | 4.68 | 1149.5726 | 0.041209 | 4920 | 3.81 | 1291.3386 | 0.11144 | 4500 | 3.18 | 1415.0943 | 0.16714 | 4000 | 2.51 | 1593.6255 | 0.22498 | 3500 | 2.04 | 1715.6863 | 0.2753 | 3000 | 1.53 | 1960.7843 | 0.31949
| 4 |  | 3.4283 | max | 16620 | 3.83 | 4339.4256 | 5.1414 | 16420 | 3.5 | 4691.4286 | 3.9691 | 16160 | 3.17 | 5097.7918 | 3.313 | 15920 | 2.82 | 5645.3901 | 2.673 | 15220 | 2.63 | 5787.0722 | 2.2768 | 14420 | 2.41 | 5983.4025 | 1.8597
|  | 5289.2562 | 39.1216 | nom | 14000 | 4 | 3500 | 1028.7616 | 14000 | 3.67 | 3814.7139 | 1332.5917 | 14000 | 3.34 | 4191.6168 | 1596.4929 | 14000 | 2.99 | 4682.2742 | 1978.808 | 14000 | 2.79 | 5017.9211 | 2323.1419 | 14000 | 2.54 | 5511.811 | 2844.1736
|  | 15.9589 | 100 | mid | 11200 | 4.29 | 2610.7226 | 1 | 11200 | 3.96 | 2828.2828 | 1 | 11200 | 3.63 | 3085.3994 | 1 | 11200 | 3.28 | 3414.6341 | 1 | 11200 | 3.01 | 3720.9302 | 1 | 11200 | 2.69 | 4163.5688 | 1
|  | 5314.3299 | 1550.1325 | min | 5160 | 5.16 | 1000 | 0.0214 | 4740 | 3.97 | 1193.9547 | 0.085024 | 4300 | 3.26 | 1319.0184 | 0.14337 | 3800 | 2.52 | 1507.9365 | 0.20125 | 3300 | 2.03 | 1625.6158 | 0.2518 | 2800 | 1.51 | 1854.3046 | 0.29634
| 5 |  | 3.6436 | max | 16680 | 4.12 | 4048.5437 | 5.6369 | 16480 | 3.75 | 4394.6667 | 4.1366 | 16240 | 3.38 | 4804.7337 | 3.4041 | 15980 | 2.98 | 5362.4161 | 2.698 | 15280 | 2.72 | 5617.6471 | 2.277 | 14480 | 2.44 | 5934.4262 | 1.8383
|  | 4958.6777 | 38.365 | nom | 14000 | 4.3 | 3255.814 | 879.6775 | 14000 | 3.93 | 3562.341 | 1198.7314 | 14000 | 3.56 | 3932.5843 | 1456.6787 | 14000 | 3.16 | 4430.3797 | 1837.8767 | 14000 | 2.91 | 4810.9966 | 2177.7218 | 14000 | 2.61 | 5363.9847 | 2697.4017
|  | 15.0158 | 100 | mid | 11200 | 4.61 | 2429.5011 | 1 | 11200 | 4.24 | 2641.5094 | 1 | 11200 | 3.87 | 2894.0568 | 1 | 11200 | 3.47 | 3227.6657 | 1 | 11200 | 3.14 | 3566.879 | 1 | 11200 | 2.76 | 4057.971 | 1
|  | 5000.2592 | 1372.3316 | min | 4940 | 5.64 | 875.8865 | 0.0029837 | 4560 | 4.13 | 1104.1162 | 0.060042 | 4100 | 3.34 | 1227.5449 | 0.12094 | 3600 | 2.53 | 1422.9249 | 0.17877 | 3100 | 2.02 | 1534.6535 | 0.22947 | 2600 | 1.49 | 1744.9664 | 0.27426
| 6 |  | 3.8779 | max | 16740 | 4.41 | 3795.9184 | 6.12 | 16540 | 4 | 4135 | 4.2984 | 16320 | 3.59 | 4545.961 | 3.4888 | 16040 | 3.14 | 5108.2803 | 2.7163 | 15340 | 2.81 | 5459.0747 | 2.2723 | 14540 | 2.47 | 5886.6397 | 1.8143
|  | 4628.0992 | 37.5967 | nom | 14000 | 4.6 | 3043.4783 | 756.2254 | 14000 | 4.19 | 3341.2888 | 1076.711 | 14000 | 3.78 | 3703.7037 | 1326.5513 | 14000 | 3.33 | 4204.2042 | 1703.7981 | 14000 | 3.03 | 4620.462 | 2036.7125 | 14000 | 2.68 | 5223.8806 | 2550.8408
|  | 14.0498 | 100 | mid | 11200 | 4.93 | 2271.8053 | 0 | 11200 | 4.52 | 2477.8761 | 1 | 11200 | 4.11 | 2725.0608 | 1 | 11200 | 3.66 | 3060.1093 | 1 | 11200 | 3.27 | 3425.0765 | 1 | 11200 | 2.83 | 3957.5972 | 1
|  | 4678.5879 | 1206.4627 | min | 4720 | 6.12 | 771.2418 | 0 | 4380 | 4.29 | 1020.979 | 0.036378 | 3900 | 3.42 | 1140.3509 | 0.09974 | 3400 | 2.54 | 1338.5827 | 0.15745 | 2900 | 2.01 | 1442.7861 | 0.2082 | 2400 | 1.47 | 1632.6531 | 0.25319
| 7 |  | 4.1327 | max | 16800 | 4.7 | 3574.4681 | 6.6 | 16600 | 4.25 | 3905.8824 | 4.4549 | 16400 | 3.8 | 4315.7895 | 3.5677 | 16100 | 3.3 | 4878.7879 | 2.7283 | 15400 | 2.9 | 5310.3448 | 2.2631 | 14600 | 2.5 | 5840 | 1.7879
|  | 4297.5207 | 36.8156 | nom | 14000 | 4.9 | 2857.1429 | 651.1395 | 14000 | 4.45 | 3146.0674 | 964.6779 | 14000 | 4 | 3500 | 1204.5569 | 14000 | 3.5 | 4000 | 1575.1371 | 14000 | 3.15 | 4444.4444 | 1898.9354 | 14000 | 2.75 | 5090.9091 | 2403.6239
|  | 13.0533 | 100 | mid | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.8 | 2333.3333 | 1 | 11200 | 4.35 | 2574.7126 | 1 | 11200 | 3.85 | 2909.0909 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 2.9 | 3862.069 | 1
|  | 4346.7357 | 1051.7814 | min | 4500 | 6.6 | 681.8182 | 0 | 4200 | 4.45 | 943.8202 | 0.013932 | 3700 | 3.5 | 1057.1429 | 0.079669 | 3200 | 2.55 | 1254.902 | 0.13719 | 2700 | 2 | 1350 | 0.18794 | 2200 | 1.45 | 1517.2414 | 0.23306
| 8 |  | 4.3747 | max | 16860 | 4.81 | 3505.1975 | 6.31 | 16640 | 4.38 | 3799.0868 | 4.54 | 16440 | 3.93 | 4183.2061 | 3.73 | 16160 | 3.48 | 4643.6782 | 2.9597 | 15440 | 3.06 | 5045.7516 | 2.4589 | 14640 | 2.64 | 5545.4545 | 1.9545
|  | 3966.9421 | 36.0204 | nom | 14000 | 5.02 | 2788.8446 | 628.6755 | 14000 | 4.59 | 3050.1089 | 873.7758 | 14000 | 4.16 | 3365.3846 | 1063.5234 | 14000 | 3.69 | 3794.0379 | 1340.3039 | 14000 | 3.32 | 4216.8675 | 1613.3152 | 14000 | 2.9 | 4827.5862 | 2029.6731
|  | 11.9877 | 88.1144 | mid | 11200 | 5.37 | 2085.6611 | 0 | 11200 | 4.95 | 2262.6263 | 0 | 11200 | 4.53 | 2472.4062 | 0 | 11200 | 4.06 | 2758.6207 | 1 | 11200 | 3.58 | 3128.4916 | 1 | 11200 | 3.06 | 3660.1307 | 1
|  | 3991.9079 | 912.5011 | min | 4920 | 6.31 | 779.7147 | 0 | 4600 | 4.54 | 1013.2159 | 0 | 4120 | 3.73 | 1104.5576 | 0 | 3640 | 2.91 | 1250.8591 | 0.043246 | 3200 | 2.34 | 1367.5214 | 0.095868 | 2760 | 1.77 | 1559.322 | 0.143
| 9 |  | 4.6019 | max | 16920 | 4.92 | 3439.0244 | 6.02 | 16680 | 4.51 | 3698.4479 | 4.63 | 16480 | 4.06 | 4059.1133 | 3.96 | 16220 | 3.66 | 4431.694 | 3.27 | 15480 | 3.22 | 4807.4534 | 2.68 | 14680 | 2.78 | 5280.5755 | 2.78
|  | 3636.3636 | 35.2099 | nom | 14000 | 5.14 | 2723.7354 | 604.0471 | 14000 | 4.73 | 2959.8309 | 785.3917 | 14000 | 4.32 | 3240.7407 | 918.2736 | 14000 | 3.88 | 3608.2474 | 1112.0378 | 14000 | 3.49 | 4011.4613 | 1356.8521 | 14000 | 3.05 | 4590.1639 | 1308.0445
|  | 10.9308 | 73.0092 | mid | 11200 | 5.49 | 2040.0729 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.71 | 2377.9193 | 0 | 11200 | 4.27 | 2622.9508 | 0 | 11200 | 3.76 | 2978.7234 | 0 | 11200 | 3.22 | 3478.2609 | 4
|  | 3639.9436 | 790.969 | min | 5340 | 6.02 | 887.0432 | 0 | 5000 | 4.63 | 1079.9136 | 0 | 4540 | 3.96 | 1146.4646 | 0 | 4080 | 3.27 | 1247.7064 | 0 | 3700 | 2.68 | 1380.597 | 0 | 3320 | 2.09 | 1588.5167 | 0
| 10 |  | 4.7824 | max | 16980 | 5.03 | 3375.7455 | 5.73 | 16720 | 4.64 | 3603.4483 | 4.72 | 16520 | 4.19 | 3942.7208 | 4.19 | 16280 | 3.84 | 4239.5833 | 3.63 | 15520 | 3.38 | 4591.716 | 3.02 | 14720 | 2.92 | 5041.0959 | 2.41
|  | 3305.7851 | 34.3821 | nom | 14000 | 5.26 | 2661.597 | 576.9259 | 14000 | 4.87 | 2874.7433 | 700.3782 | 14000 | 4.48 | 3125 | 788.9702 | 14000 | 4.07 | 3439.8034 | 910.6846 | 14000 | 3.66 | 3825.1366 | 1094.6308 | 14000 | 3.2 | 4375 | 1371.6951
|  | 9.949 | 60.9671 | mid | 11200 | 5.61 | 1996.4349 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.89 | 2290.3885 | 0 | 11200 | 4.48 | 2500 | 0 | 11200 | 3.94 | 2842.6396 | 0 | 11200 | 3.38 | 3313.6095 | 0
|  | 3313.0139 | 692.7496 | min | 5760 | 5.73 | 1005.2356 | 0 | 5400 | 4.72 | 1144.0678 | 0 | 4960 | 4.19 | 1183.7709 | 0 | 4520 | 3.63 | 1245.1791 | 0 | 4200 | 3.02 | 1390.7285 | 0 | 3880 | 2.41 | 1609.9585 | 0
| 11 |  | 4.9023 | max | 17040 | 5.14 | 3315.1751 | 5.44 | 16760 | 4.77 | 3513.6268 | 4.81 | 16560 | 4.32 | 3833.3333 | 4.42 | 16340 | 4.02 | 4064.6766 | 3.99 | 15560 | 3.54 | 4395.4802 | 3.36 | 14760 | 3.06 | 4823.5294 | 2.73
|  | 2975.2066 | 33.5349 | nom | 14000 | 5.38 | 2602.2305 | 546.913 | 14000 | 5.01 | 2794.4112 | 618.5461 | 14000 | 4.64 | 3017.2414 | 673.1237 | 14000 | 4.26 | 3286.385 | 745.6658 | 14000 | 3.83 | 3655.3525 | 885.4782 | 14000 | 3.35 | 4179.1045 | 1089.8193
|  | 8.9515 | 50.809 | mid | 11200 | 5.73 | 1954.6248 | 0 | 11200 | 5.4 | 2074.0741 | 0 | 11200 | 5.07 | 2209.073 | 0 | 11200 | 4.69 | 2388.0597 | 0 | 11200 | 4.12 | 2718.4466 | 0 | 11200 | 3.54 | 3163.8418 | 0
|  | 2980.8497 | 608.0511 | min | 6180 | 5.44 | 1136.0294 | 0 | 5800 | 4.81 | 1205.8212 | 0 | 5380 | 4.42 | 1217.1946 | 0 | 4960 | 3.99 | 1243.1078 | 0 | 4700 | 3.36 | 1398.8095 | 0 | 4440 | 2.73 | 1626.3736 | 0
| 12 |  | 4.9584 | max | 17100 | 5.25 | 3257.1429 | 5.15 | 16800 | 4.9 | 3428.5714 | 4.9 | 16600 | 4.45 | 3730.3371 | 4.65 | 16400 | 4.2 | 3904.7619 | 4.35 | 15600 | 3.7 | 4216.2162 | 3.7 | 14800 | 3.2 | 4625 | 3.05
|  | 2644.6281 | 32.6657 | nom | 14000 | 5.5 | 2545.4545 | 513.52 | 14000 | 5.15 | 2718.4466 | 539.72 | 14000 | 4.8 | 2916.6667 | 568.7372 | 14000 | 4.45 | 3146.0674 | 607.9605 | 14000 | 4 | 3500 | 714.7644 | 14000 | 3.5 | 4000 | 867.0912
|  | 7.9453 | 42.0224 | mid | 11200 | 5.85 | 1914.5299 | 0 | 11200 | 5.55 | 2018.018 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.9 | 2285.7143 | 0 | 11200 | 4.3 | 2604.6512 | 0 | 11200 | 3.7 | 3027.027 | 0
|  | 2645.8002 | 533.6041 | min | 6600 | 5.15 | 1281.5534 | 0 | 6200 | 4.9 | 1265.3061 | 0 | 5800 | 4.65 | 1247.3118 | 0 | 5400 | 4.35 | 1241.3793 | 0 | 5200 | 3.7 | 1405.4054 | 0 | 5000 | 3.05 | 1639.3443 | 0
| 13 |  | 5.0259 | max | 17566.6667 | 5.2833 | 3324.9211 | 5.15 | 17266.6667 | 4.9333 | 3500 | 4.9667 | 17033.3333 | 4.55 | 3743.5897 | 4.7833 | 16833.3333 | 4.3 | 3914.7287 | 4.55 | 16033.3333 | 3.8 | 4219.2982 | 3.9167 | 15200 | 3.3 | 4606.0606 | 3.2667
|  | 2314.0496 | 31.771 | nom | 14000 | 5.5 | 2545.4545 | 449.33 | 14000 | 5.1833 | 2700.9646 | 465.916 | 14000 | 4.8667 | 2876.7123 | 483.7734 | 14000 | 4.55 | 3076.9231 | 508.5823 | 14000 | 4.1 | 3414.6341 | 590.8212 | 14000 | 3.6167 | 3870.9677 | 708.3825
|  | 6.9511 | 36.1198 | mid | 11200 | 5.9 | 1898.3051 | 0 | 11200 | 5.5833 | 2005.9701 | 0 | 11200 | 5.3167 | 2106.5831 | 0 | 11200 | 5.0167 | 2232.5581 | 0 | 11200 | 4.4167 | 2535.8491 | 0 | 11200 | 3.8167 | 2934.4978 | 0
|  | 2314.7144 | 460.5603 | min | 6700 | 5.15 | 1300.9709 | 0 | 6266.6667 | 4.9667 | 1261.745 | 0 | 5833.3333 | 4.7833 | 1219.5122 | 0 | 5400 | 4.55 | 1186.8132 | 0 | 5233.3333 | 3.9167 | 1336.1702 | 0 | 5066.6667 | 3.2667 | 1551.0204 | 0
| 14 |  | 5.0818 | max | 18033.3333 | 5.3167 | 3391.8495 | 5.15 | 17733.3333 | 4.9667 | 3570.4698 | 5.0333 | 17466.6667 | 4.65 | 3756.2724 | 4.9167 | 17266.6667 | 4.4 | 3924.2424 | 4.75 | 16466.6667 | 3.9 | 4222.2222 | 4.1333 | 15600 | 3.4 | 4588.2353 | 3.4833
|  | 1983.4711 | 30.8461 | nom | 14000 | 5.5 | 2545.4545 | 385.14 | 14000 | 5.2167 | 2683.7061 | 394.0671 | 14000 | 4.9333 | 2837.8378 | 403.4178 | 14000 | 4.65 | 3010.7527 | 417.5729 | 14000 | 4.2 | 3333.3333 | 479.872 | 14000 | 3.7333 | 3750 | 569.4175
|  | 5.9571 | 30.3879 | mid | 11200 | 5.95 | 1882.3529 | 0 | 11200 | 5.6167 | 1994.0653 | 0 | 11200 | 5.3833 | 2080.4954 | 0 | 11200 | 5.1333 | 2181.8182 | 0 | 11200 | 4.5333 | 2470.5882 | 0 | 11200 | 3.9333 | 2847.4576 | 0
|  | 1983.724 | 390.3589 | min | 6800 | 5.15 | 1320.3883 | 0 | 6333.3333 | 5.0333 | 1258.2781 | 0 | 5866.6667 | 4.9167 | 1193.2203 | 0 | 5400 | 4.75 | 1136.8421 | 0 | 5266.6667 | 4.1333 | 1274.1935 | 0 | 5133.3333 | 3.4833 | 1473.6842 | 0
| 15 |  | 5.1256 | max | 18500 | 5.35 | 3457.9439 | 5.15 | 18200 | 5 | 3640 | 5.1 | 17900 | 4.75 | 3768.4211 | 5.05 | 17700 | 4.5 | 3933.3333 | 4.95 | 16900 | 4 | 4225 | 4.35 | 16000 | 3.5 | 4571.4286 | 3.7
|  | 1652.8926 | 29.8848 | nom | 14000 | 5.5 | 2545.4545 | 320.95 | 14000 | 5.25 | 2666.6667 | 324.0966 | 14000 | 5 | 2800 | 327.3055 | 14000 | 4.75 | 2947.3684 | 333.9177 | 14000 | 4.3 | 3255.814 | 379.9753 | 14000 | 3.85 | 3636.3636 | 446.7277
|  | 4.9638 | 24.834 | mid | 11200 | 6 | 1866.6667 | 0 | 11200 | 5.65 | 1982.3009 | 0 | 11200 | 5.45 | 2055.0459 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.65 | 2408.6022 | 0 | 11200 | 4.05 | 2765.4321 | 0
|  | 1652.9319 | 322.4871 | min | 6900 | 5.15 | 1339.8058 | 0 | 6400 | 5.1 | 1254.902 | 0 | 5900 | 5.05 | 1168.3168 | 0 | 5400 | 4.95 | 1090.9091 | 0 | 5300 | 4.35 | 1218.3908 | 0 | 5200 | 3.7 | 1405.4054 | 0
| 16 |  | 6.4392 | max | 19020 | 5.73 | 3319.3717 | 6.92 | 18720 | 5.3 | 3532.0755 | 5.68 | 18420 | 4.95 | 3721.2121 | 5.37 | 18200 | 4.59 | 3965.1416 | 5.02 | 17380 | 4.08 | 4259.8039 | 4.36 | 16460 | 3.56 | 4623.5955 | 3.65
|  | 1322.314 | 28.8778 | nom | 14000 | 5.93 | 2360.8769 | 191.0858 | 14000 | 5.57 | 2513.465 | 232.8018 | 14000 | 5.21 | 2687.1401 | 246.241 | 14000 | 4.85 | 2886.5979 | 263.4092 | 14000 | 4.39 | 3189.0661 | 303.283 | 14000 | 3.92 | 3571.4286 | 362.2778
|  | 4.0078 | 19.5079 | mid | 11200 | 6.42 | 1744.5483 | 0 | 11200 | 5.99 | 1869.783 | 0 | 11200 | 5.68 | 1971.831 | 0 | 11200 | 5.36 | 2089.5522 | 0 | 11200 | 4.74 | 2362.8692 | 0 | 11200 | 4.12 | 2718.4466 | 0
|  | 1334.5945 | 207.2624 | min | 6980 | 6.92 | 1008.6705 | 0 | 6460 | 5.68 | 1137.3239 | 0 | 6000 | 5.37 | 1117.3184 | 0 | 5520 | 5.02 | 1099.6016 | 0 | 5360 | 4.36 | 1229.3578 | 0 | 5180 | 3.65 | 1419.1781 | 0
| 17 |  | 8.0071 | max | 19540 | 6.11 | 3198.036 | 8.69 | 19240 | 5.6 | 3435.7143 | 6.26 | 18940 | 5.15 | 3677.6699 | 5.69 | 18700 | 4.68 | 3995.7265 | 5.09 | 17860 | 4.16 | 4293.2692 | 4.37 | 16920 | 3.62 | 4674.0331 | 3.6
|  | 991.7355 | 27.8102 | nom | 14000 | 6.36 | 2201.2579 | 114.1238 | 14000 | 5.89 | 2376.91 | 158.4242 | 14000 | 5.42 | 2583.0258 | 174.2945 | 14000 | 4.95 | 2828.2828 | 194.84 | 14000 | 4.48 | 3125 | 226.9418 | 14000 | 3.99 | 3508.7719 | 275.4821
|  | 3.0435 | 14.3558 | mid | 11200 | 6.84 | 1637.4269 | 0 | 11200 | 6.33 | 1769.3523 | 0 | 11200 | 5.91 | 1895.0931 | 0 | 11200 | 5.47 | 2047.532 | 0 | 11200 | 4.83 | 2318.8406 | 0 | 11200 | 4.19 | 2673.031 | 0
|  | 1013.486 | 126.573 | min | 7060 | 8.69 | 812.4281 | 0 | 6520 | 6.26 | 1041.5335 | 0 | 6100 | 5.69 | 1072.0562 | 0 | 5640 | 5.09 | 1108.055 | 0 | 5420 | 4.37 | 1240.2746 | 0 | 5160 | 3.6 | 1433.3333 | 0
| 18 |  | 9.8608 | max | 20060 | 6.49 | 3090.9091 | 10.46 | 19760 | 5.9 | 3349.1525 | 6.84 | 19460 | 5.35 | 3637.3832 | 6.01 | 19200 | 4.77 | 4025.1572 | 5.16 | 18340 | 4.24 | 4325.4717 | 4.38 | 17380 | 3.68 | 4722.8261 | 3.55
|  | 661.157 | 26.6553 | nom | 14000 | 6.79 | 2061.8557 | 63.2081 | 14000 | 6.21 | 2254.4283 | 96.6604 | 14000 | 5.63 | 2486.6785 | 110.0095 | 14000 | 5.05 | 2772.2772 | 128.1312 | 14000 | 4.57 | 3063.4573 | 150.9491 | 14000 | 4.06 | 3448.2759 | 186.2414
|  | 2.0357 | 9.3817 | mid | 11200 | 7.26 | 1542.6997 | 0 | 11200 | 6.67 | 1679.1604 | 0 | 11200 | 6.14 | 1824.1042 | 0 | 11200 | 5.58 | 2007.1685 | 0 | 11200 | 4.92 | 2276.4228 | 0 | 11200 | 4.26 | 2629.108 | 0
|  | 677.8842 | 68.7455 | min | 7140 | 10.46 | 682.6004 | 0 | 6580 | 6.84 | 961.9883 | 0 | 6200 | 6.01 | 1031.614 | 0 | 5760 | 5.16 | 1116.2791 | 0 | 5480 | 4.38 | 1251.1416 | 0 | 5140 | 3.55 | 1447.8873 | 0
| 19 |  | 12.061 | max | 20580 | 6.87 | 2995.6332 | 12.23 | 20280 | 6.2 | 3270.9677 | 7.42 | 19980 | 5.55 | 3600 | 6.33 | 19700 | 4.86 | 4053.4979 | 5.23 | 18820 | 4.32 | 4356.4815 | 4.39 | 17840 | 3.74 | 4770.0535 | 3.5
|  | 330.5785 | 25.3513 | nom | 14000 | 7.22 | 1939.0582 | 27.0301 | 14000 | 6.53 | 2143.951 | 44.5524 | 14000 | 5.84 | 2397.2603 | 52.2241 | 14000 | 5.15 | 2718.4466 | 63.2081 | 14000 | 4.66 | 3004.2918 | 75.3026 | 14000 | 4.13 | 3389.8305 | 94.451
|  | 1.0013 | 4.5916 | mid | 11200 | 7.68 | 1458.3333 | 0 | 11200 | 7.01 | 1597.7175 | 0 | 11200 | 6.37 | 1758.2418 | 0 | 11200 | 5.69 | 1968.3656 | 0 | 11200 | 5.01 | 2235.5289 | 0 | 11200 | 4.33 | 2586.6051 | 0
|  | 333.4354 | 27.6457 | min | 7220 | 12.23 | 590.3516 | 0 | 6640 | 7.42 | 894.8787 | 0 | 6300 | 6.33 | 995.2607 | 0 | 5880 | 5.23 | 1124.283 | 0 | 5540 | 4.39 | 1261.959 | 0 | 5120 | 3.5 | 1462.8571 | 0
| 20 |  | 14 | max | 21100 | 7.25 | 2910.3448 | 14 | 20800 | 6.5 | 3200 | 8 | 20500 | 5.75 | 3565.2174 | 6.65 | 20200 | 4.95 | 4080.8081 | 5.3 | 19300 | 4.4 | 4386.3636 | 4.4 | 18300 | 3.8 | 4815.7895 | 3.45
|  | 0 | 23.5 | nom | 14000 | 7.65 | 1830.0654 | 0 | 14000 | 6.85 | 2043.7956 | 0 | 14000 | 6.05 | 2314.0496 | 0 | 14000 | 5.25 | 2666.6667 | 0 | 14000 | 4.75 | 2947.3684 | 0 | 14000 | 4.2 | 3333.3333 | 0
|  | 0 | 0 | mid | 11200 | 8.1 | 1382.716 | 0 | 11200 | 7.35 | 1523.8095 | 0 | 11200 | 6.6 | 1696.9697 | 0 | 11200 | 5.8 | 1931.0345 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.4 | 2545.4545 | 0
|  | 0 | 0 | min | 7300 | 14 | 521.4286 | 0 | 6700 | 8 | 837.5 | 0 | 6400 | 6.65 | 962.406 | 0 | 6000 | 5.3 | 1132.0755 | 0 | 5600 | 4.4 | 1272.7273 | 0 | 5100 | 3.45 | 1478.2609 | 0
Indoor Temp. |  | 21
LWT |  |  | 25 CAP: 25; 35 CAP: 35; 40 CAP: 40; 45 CAP: 45; 50 CAP: 50; 55 CAP: 55
Outdoor air temperature[℃] |  | Heating Demand | COP | CL | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP
|  |  | LWT |  |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI
| -10 |  | 2.0318 | max | 14600 | 2.4 | 6083.3333 | 2.7929 | 14400 | 2.25 | 6400 | 2.6281 | 14200 | 2.1 | 6761.9048 | 2.465 | 14000 | 1.9 | 7368.4211 | 2.2532 | 14000 | 1.85 | 7567.5676 | 2.0062 | 14000 | 1.75 | 8000 | 1.7508
|  | 10247.9339 | 49.4825 | nom | 14000 | 2.8 | 5000 | 3669.3121 | 14000 | 2.5 | 5600 | 3899.3017 | 14000 | 2.2 | 6363.6364 | 4157.3868 | 14000 | 1.9 | 7368.4211 | 4548.2097 | 14000 | 1.85 | 7567.5676 | 5108.0403 | 14000 | 1.75 | 8000 | 5853.198
|  | 30.8131 | 100 | mid | 11200 | 2.85 | 3929.8246 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.1 | 5333.3333 | 1 | 11200 | 1.85 | 6054.0541 | 1
|  | 10260.7606 | 5050.1023 | min | 6200 | 2.55 | 2431.3725 | 0.80959 | 5900 | 2.3 | 2565.2174 | 0.82036 | 5600 | 2.05 | 2731.7073 | 0.82999 | 5300 | 1.75 | 3028.5714 | 0.83863 | 4600 | 1.45 | 3172.4138 | 0.85575 | 4000 | 1.1 | 3636.3636 | 0.86777
| -9 |  | 2.0926 | max | 15100 | 2.5 | 6040 | 2.9674 | 14900 | 2.3333 | 6385.7143 | 2.6883 | 14700 | 2.1667 | 6784.6154 | 2.4982 | 14500 | 1.9667 | 7372.8814 | 2.2751 | 14233.3333 | 1.9167 | 7426.087 | 2.0372 | 14000 | 1.8167 | 7706.422 | 1.7937
|  | 9917.3554 | 48.8354 | nom | 14000 | 2.8833 | 4855.4913 | 3342.1028 | 14000 | 2.6 | 5384.6154 | 3689.0682 | 14000 | 2.3167 | 6043.1655 | 3969.8617 | 14000 | 2.0333 | 6885.2459 | 4359.0646 | 14000 | 1.95 | 7179.4872 | 4868.2048 | 14000 | 1.8167 | 7706.422 | 5529.0933
|  | 29.8468 | 100 | mid | 11200 | 2.9833 | 3754.1899 | 1 | 11200 | 2.8 | 4000 | 1 | 11200 | 2.6167 | 4280.2548 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.1667 | 5169.2308 | 1 | 11200 | 1.9333 | 5793.1034 | 1
|  | 9939.0006 | 4749.6138 | min | 5833.3333 | 2.9167 | 2000 | 0.761 | 5266.6667 | 2.2833 | 2306.5693 | 0.78382 | 5066.6667 | 2.05 | 2471.5447 | 0.79087 | 4866.6667 | 1.7833 | 2728.972 | 0.79748 | 4266.6667 | 1.4667 | 2909.0909 | 0.815 | 3700 | 1.1167 | 3313.4328 | 0.82898
| -8 |  | 2.1512 | max | 15600 | 2.6 | 6000 | 3.1636 | 15400 | 2.4167 | 6372.4138 | 2.7444 | 15200 | 2.2333 | 6805.9701 | 2.5301 | 15000 | 2.0333 | 7377.0492 | 2.299 | 14466.6667 | 1.9833 | 7294.1176 | 2.0668 | 14000 | 1.8833 | 7433.6283 | 1.834
|  | 9586.7769 | 48.1832 | nom | 14000 | 2.9667 | 4719.1011 | 3030.3736 | 14000 | 2.7 | 5185.1852 | 3493.2015 | 14000 | 2.4333 | 5753.4247 | 3789.1243 | 14000 | 2.1667 | 6461.5385 | 4169.9612 | 14000 | 2.05 | 6829.2683 | 4638.3943 | 14000 | 1.8833 | 7433.6283 | 5227.3283
|  | 28.8647 | 100 | mid | 11200 | 3.1167 | 3593.5829 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.6833 | 4173.913 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.2333 | 5014.9254 | 1 | 11200 | 2.0167 | 5553.719 | 1
|  | 9611.9361 | 4468.1864 | min | 5466.6667 | 3.2833 | 1664.9746 | 0.71862 | 4633.3333 | 2.2667 | 2044.1176 | 0.75433 | 4533.3333 | 2.05 | 2211.3821 | 0.75802 | 4433.3333 | 1.8167 | 2440.367 | 0.76159 | 3933.3333 | 1.4833 | 2651.6854 | 0.778 | 3400 | 1.1333 | 3000 | 0.79318
| -7 |  | 2.2088 | max | 16100 | 2.7 | 5962.963 | 3.3775 | 15900 | 2.5 | 6360 | 2.7975 | 15700 | 2.3 | 6826.087 | 2.561 | 15500 | 2.1 | 7380.9524 | 2.3245 | 14700 | 2.05 | 7170.7317 | 2.0954 | 14000 | 1.95 | 7179.4872 | 1.872
|  | 9256.1983 | 47.5259 | nom | 14000 | 3.05 | 4590.1639 | 2740.5778 | 14000 | 2.8 | 5000 | 3308.7149 | 14000 | 2.55 | 5490.1961 | 3614.2634 | 14000 | 2.3 | 6086.9565 | 3981.9863 | 14000 | 2.15 | 6511.6279 | 4417.4122 | 14000 | 1.95 | 7179.4872 | 4944.489
|  | 27.8713 | 100 | mid | 11200 | 3.25 | 3446.1538 | 1 | 11200 | 3 | 3733.3333 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1 | 11200 | 2.1 | 5333.3333 | 1
|  | 9281.1378 | 4201.9505 | min | 5100 | 3.65 | 1397.2603 | 0.68134 | 4000 | 2.25 | 1777.7778 | 0.73003 | 4000 | 2.05 | 1951.2195 | 0.73003 | 4000 | 1.85 | 2162.1622 | 0.73003 | 3600 | 1.5 | 2400 | 0.74424 | 3100 | 1.15 | 2695.6522 | 0.76002
| -6 |  | 2.2602 | max | 16144.4444 | 2.7611 | 5847.0825 | 3.4512 | 15944.4444 | 2.5556 | 6239.1304 | 2.8391 | 15733.3333 | 2.35 | 6695.0355 | 2.594 | 15533.3333 | 2.1444 | 7243.5233 | 2.3473 | 14744.4444 | 2.0944 | 7039.7878 | 2.1136 | 14033.3333 | 1.9944 | 7036.2117 | 1.8813
|  | 8925.6198 | 46.863 | nom | 14000 | 3.0889 | 4532.3741 | 2586.217 | 14000 | 2.8389 | 4931.5068 | 3143.7723 | 14000 | 2.5889 | 5407.7253 | 3440.9076 | 14000 | 2.3389 | 5985.7482 | 3802.53 | 14000 | 2.1944 | 6379.7468 | 4223.0045 | 14000 | 2 | 7000 | 4744.3309
|  | 26.8727 | 100 | mid | 11200 | 3.2944 | 3399.6627 | 1 | 11200 | 3.0444 | 3678.8321 | 1 | 11200 | 2.7944 | 4007.9523 | 1 | 11200 | 2.5444 | 4401.7467 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.15 | 5209.3023 | 1
|  | 8948.5927 | 3959.2021 | min | 5155.5556 | 3.7111 | 1389.2216 | 0.62372 | 4122.2222 | 2.4056 | 1713.6259 | 0.67866 | 4077.7778 | 2.1667 | 1882.0513 | 0.68066 | 4022.2222 | 1.9222 | 2092.4855 | 0.68314 | 3611.1111 | 1.5611 | 2313.1673 | 0.7003 | 3111.1111 | 1.1944 | 2604.6512 | 0.71883
| -5 |  | 2.3152 | max | 16188.8889 | 2.8222 | 5736.2205 | 3.5274 | 15988.8889 | 2.6111 | 6123.4043 | 2.8912 | 15766.6667 | 2.4 | 6569.4444 | 2.6335 | 15566.6667 | 2.1889 | 7111.6751 | 2.3725 | 14788.8889 | 2.1389 | 6914.2857 | 2.1326 | 14066.6667 | 2.0389 | 6899.1826 | 1.8901
|  | 8595.0413 | 46.1945 | nom | 14000 | 3.1278 | 4476.0213 | 2436.6687 | 14000 | 2.8778 | 4864.8649 | 2972.7993 | 14000 | 2.6278 | 5327.6956 | 3263.7945 | 14000 | 2.3778 | 5887.8505 | 3622.8039 | 14000 | 2.2389 | 6253.1017 | 4030.2565 | 14000 | 2.05 | 6829.2683 | 4547.505
|  | 25.8643 | 100 | mid | 11200 | 3.3389 | 3354.4093 | 1 | 11200 | 3.0889 | 3625.8993 | 1 | 11200 | 2.8389 | 3945.2055 | 1 | 11200 | 2.5889 | 4326.1803 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.2 | 5090.9091 | 1
|  | 8612.8115 | 3720.1474 | min | 5211.1111 | 3.7722 | 1381.4433 | 0.56503 | 4244.4444 | 2.5611 | 1657.2668 | 0.62549 | 4155.5556 | 2.2833 | 1819.9513 | 0.63021 | 4044.4444 | 1.9944 | 2027.8552 | 0.63595 | 3622.2222 | 1.6222 | 2232.8767 | 0.65624 | 3122.2222 | 1.2389 | 2520.1794 | 0.67752
| -4 |  | 2.3744 | max | 16233.3333 | 2.8833 | 5630.0578 | 3.606 | 16033.3333 | 2.6667 | 6012.5 | 2.9543 | 15800 | 2.45 | 6448.9796 | 2.6797 | 15600 | 2.2333 | 6985.0746 | 2.4001 | 14833.3333 | 2.1833 | 6793.8931 | 2.1526 | 14100 | 2.0833 | 6768 | 1.8982
|  | 8264.4628 | 45.5201 | nom | 14000 | 3.1667 | 4421.0526 | 2291.8819 | 14000 | 2.9167 | 4800 | 2797.4 | 14000 | 2.6667 | 5250 | 3084.1326 | 14000 | 2.4167 | 5793.1034 | 3443.3304 | 14000 | 2.2833 | 6131.3869 | 3839.3527 | 14000 | 2.1 | 6666.6667 | 4353.7944
|  | 24.8456 | 100 | mid | 11200 | 3.3833 | 3310.3448 | 1 | 11200 | 3.1333 | 3574.4681 | 1 | 11200 | 2.8833 | 3884.3931 | 1 | 11200 | 2.6333 | 4253.1646 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.25 | 4977.7778 | 1
|  | 8273.6 | 3484.5225 | min | 5266.6667 | 3.8333 | 1373.913 | 0.50525 | 4366.6667 | 2.7167 | 1607.362 | 0.57041 | 4233.3333 | 2.4 | 1763.8889 | 0.57863 | 4066.6667 | 2.0667 | 1967.7419 | 0.58848 | 3633.3333 | 1.6833 | 2158.4158 | 0.61204 | 3133.3333 | 1.2833 | 2441.5584 | 0.63609
| -3 |  | 2.44 | max | 16277.7778 | 2.9444 | 5528.3019 | 3.6871 | 16077.7778 | 2.7222 | 5906.1224 | 3.0291 | 15833.3333 | 2.5 | 6333.3333 | 2.7329 | 15633.3333 | 2.2778 | 6863.4146 | 2.4303 | 14877.7778 | 2.2278 | 6678.3042 | 2.1734 | 14133.3333 | 2.1278 | 6642.2977 | 1.9058
|  | 7933.8843 | 44.8394 | nom | 14000 | 3.2056 | 4367.4177 | 2151.8003 | 14000 | 2.9556 | 4736.8421 | 2619.2457 | 14000 | 2.7056 | 5174.538 | 2903.1386 | 14000 | 2.4556 | 5701.3575 | 3264.6137 | 14000 | 2.3278 | 6014.3198 | 3650.4677 | 14000 | 2.15 | 6511.6279 | 4162.9907
|  | 23.8357 | 100 | mid | 11200 | 3.4278 | 3267.423 | 1 | 11200 | 3.1778 | 3524.4755 | 1 | 11200 | 2.9278 | 3825.4269 | 1 | 11200 | 2.6778 | 4182.5726 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1
|  | 7937.2857 | 3252.9997 | min | 5322.2222 | 3.8944 | 1366.6191 | 0.44433 | 4488.8889 | 2.8722 | 1562.8627 | 0.51333 | 4311.1111 | 2.5167 | 1713.0243 | 0.52589 | 4088.8889 | 2.1389 | 1911.6883 | 0.5407 | 3644.4444 | 1.7444 | 2089.172 | 0.56772 | 3144.4444 | 1.3278 | 2368.2008 | 0.59455
| -2 |  | 2.5189 | max | 16322.2222 | 3.0056 | 5430.6839 | 3.7708 | 16122.2222 | 2.7778 | 5804 | 3.1161 | 15866.6667 | 2.55 | 6222.2222 | 2.7933 | 15666.6667 | 2.3222 | 6746.4115 | 2.4629 | 14922.2222 | 2.2722 | 6567.2372 | 2.1951 | 14166.6667 | 2.1722 | 6521.7391 | 1.9128
|  | 7603.3058 | 44.1521 | nom | 14000 | 3.2444 | 4315.0685 | 2016.3626 | 14000 | 2.9944 | 4675.3247 | 2440.0224 | 14000 | 2.7444 | 5101.2146 | 2722.0112 | 14000 | 2.4944 | 5612.4722 | 3087.1361 | 14000 | 2.3722 | 5901.6393 | 3463.7661 | 14000 | 2.2 | 6363.6364 | 3974.8932
|  | 22.8838 | 100 | mid | 11200 | 3.4722 | 3225.6 | 1 | 11200 | 3.2222 | 3475.8621 | 1 | 11200 | 2.9722 | 3768.2243 | 1 | 11200 | 2.7222 | 4114.2857 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1
|  | 7620.2933 | 3025.2148 | min | 5377.7778 | 3.9556 | 1359.5506 | 0.38225 | 4611.1111 | 3.0278 | 1522.9358 | 0.45413 | 4388.8889 | 2.6333 | 1666.6667 | 0.47194 | 4111.1111 | 2.2111 | 1859.2965 | 0.49263 | 3655.5556 | 1.8056 | 2024.6154 | 0.52327 | 3155.5556 | 1.3722 | 2299.5951 | 0.5529
| -1 |  | 2.61 | max | 16366.6667 | 3.0667 | 5336.9565 | 3.8572 | 16166.6667 | 2.8333 | 5705.8824 | 3.2161 | 15900 | 2.6 | 6115.3846 | 2.8611 | 15700 | 2.3667 | 6633.8028 | 2.4981 | 14966.6667 | 2.3167 | 6460.4317 | 2.2177 | 14200 | 2.2167 | 6406.015 | 1.9193
|  | 7272.7273 | 43.4578 | nom | 14000 | 3.2833 | 4263.9594 | 1885.5029 | 14000 | 3.0333 | 4615.3846 | 2261.3798 | 14000 | 2.7833 | 5029.9401 | 2541.9063 | 14000 | 2.5333 | 5526.3158 | 2911.3547 | 14000 | 2.4167 | 5793.1034 | 3279.4022 | 14000 | 2.25 | 6222.2222 | 3789.3082
|  | 21.9259 | 100 | mid | 11200 | 3.5167 | 3184.8341 | 1 | 11200 | 3.2667 | 3428.5714 | 1 | 11200 | 3.0167 | 3712.7072 | 1 | 11200 | 2.7667 | 4048.1928 | 1 | 11200 | 2.6 | 4307.6923 | 1 | 11200 | 2.4 | 4666.6667 | 1
|  | 7301.3392 | 2797.4036 | min | 5433.3333 | 4.0167 | 1352.6971 | 0.31897 | 4733.3333 | 3.1833 | 1486.911 | 0.39269 | 4466.6667 | 2.75 | 1624.2424 | 0.41674 | 4133.3333 | 2.2833 | 1810.219 | 0.44425 | 3666.6667 | 1.8667 | 1964.2857 | 0.47868 | 3166.6667 | 1.4167 | 2235.2941 | 0.51113
| 0 |  | 2.7157 | max | 16411.1111 | 3.1278 | 5246.8917 | 3.9463 | 16211.1111 | 2.8889 | 5611.5385 | 3.3298 | 15933.3333 | 2.65 | 6012.5786 | 2.9367 | 15733.3333 | 2.4111 | 6525.3456 | 2.5358 | 15011.1111 | 2.3611 | 6357.6471 | 2.2412 | 14233.3333 | 2.2611 | 6294.8403 | 1.9251
|  | 6942.1488 | 42.7563 | nom | 14000 | 3.3222 | 4214.0468 | 1759.1512 | 14000 | 3.0722 | 4556.962 | 2084.8839 | 14000 | 2.8222 | 4960.6299 | 2363.9152 | 14000 | 2.5722 | 5442.7646 | 2737.6983 | 14000 | 2.4611 | 5688.4876 | 3097.5197 | 14000 | 2.3 | 6086.9565 | 3606.0484
|  | 20.9586 | 100 | mid | 11200 | 3.5611 | 3145.0858 | 1 | 11200 | 3.3111 | 3382.5503 | 1 | 11200 | 3.0611 | 3658.8022 | 1 | 11200 | 2.8111 | 3984.1897 | 1 | 11200 | 2.65 | 4226.4151 | 1 | 11200 | 2.45 | 4571.4286 | 1
|  | 6979.2226 | 2569.9643 | min | 5488.8889 | 4.0778 | 1346.049 | 0.25446 | 4855.5556 | 3.3389 | 1454.2429 | 0.32889 | 4544.4444 | 2.8667 | 1585.2713 | 0.36026 | 4155.5556 | 2.3556 | 1764.1509 | 0.39557 | 3677.7778 | 1.9278 | 1907.781 | 0.43396 | 3177.7778 | 1.4611 | 2174.9049 | 0.46924
| 1 |  | 2.8384 | max | 16455.5556 | 3.1889 | 5160.2787 | 4.0383 | 16255.5556 | 2.9444 | 5520.7547 | 3.458 | 15966.6667 | 2.7 | 5913.5802 | 3.0203 | 15766.6667 | 2.4556 | 6420.8145 | 2.576 | 15055.5556 | 2.4056 | 6258.6605 | 2.2656 | 14266.6667 | 2.3056 | 6187.9518 | 1.9304
|  | 6611.5702 | 42.047 | nom | 14000 | 3.3611 | 4165.2893 | 1637.234 | 14000 | 3.1111 | 4500 | 1911.977 | 14000 | 2.8611 | 4893.2039 | 2189.046 | 14000 | 2.6111 | 5361.7021 | 2566.5646 | 14000 | 2.5056 | 5587.5831 | 2918.2522 | 14000 | 2.35 | 5957.4468 | 3424.9321
|  | 19.9763 | 100 | mid | 11200 | 3.6056 | 3106.3174 | 1 | 11200 | 3.3556 | 3337.7483 | 1 | 11200 | 3.1056 | 3606.4401 | 1 | 11200 | 2.8556 | 3922.179 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.5 | 4480 | 1
|  | 6652.1223 | 2343.5987 | min | 5544.4444 | 4.1389 | 1339.5973 | 0.18869 | 4977.7778 | 3.4944 | 1424.4833 | 0.26257 | 4622.2222 | 2.9833 | 1549.3482 | 0.30243 | 4177.7778 | 2.4278 | 1720.8238 | 0.34658 | 3688.8889 | 1.9889 | 1854.7486 | 0.38911 | 3188.8889 | 1.5056 | 2118.0812 | 0.42724
14kW-Maximum heating CAP | 2 |  | 2.981 | max | 16500 | 3.25 | 5076.9231 | 4.1331 | 16300 | 3 | 5433.3333 | 3.6016 | 16000 | 2.75 | 5818.1818 | 3.1122 | 15800 | 2.5 | 6320 | 2.6189 | 15100 | 2.45 | 6163.2653 | 2.2909 | 14300 | 2.35 | 6085.1064 | 1.9351
|  | 6280.9917 | 41.3294 | nom | 14000 | 3.4 | 4117.6471 | 1519.6744 | 14000 | 3.15 | 4444.4444 | 1743.9455 | 14000 | 2.9 | 4827.5862 | 2018.2088 | 14000 | 2.65 | 5283.0189 | 2398.3194 | 14000 | 2.55 | 5490.1961 | 2741.7225 | 14000 | 2.4 | 5833.3333 | 3245.7826
|  | 18.9717 | 100 | mid | 11200 | 3.65 | 3068.4932 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 3.15 | 3555.5556 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.55 | 4392.1569 | 1
|  | 6317.5874 | 2119.2732 | min | 5600 | 4.2 | 1333.3333 | 0.12161 | 5100 | 3.65 | 1397.2603 | 0.19361 | 4700 | 3.1 | 1516.129 | 0.24323 | 4200 | 2.5 | 1680 | 0.29728 | 3700 | 2.05 | 1804.878 | 0.34413 | 3200 | 1.55 | 2064.5161 | 0.38512
| 3 |  | 3.1581 | max | 16560 | 3.54 | 4677.9661 | 4.6104 | 16360 | 3.25 | 5033.8462 | 3.7887 | 16080 | 2.96 | 5432.4324 | 3.2255 | 15860 | 2.66 | 5962.406 | 2.6671 | 15160 | 2.54 | 5968.5039 | 2.3073 | 14360 | 2.38 | 6033.6134 | 1.9222
|  | 5950.4132 | 40.6031 | nom | 14000 | 3.7 | 3783.7838 | 1290.6463 | 14000 | 3.41 | 4105.5718 | 1570.5811 | 14000 | 3.12 | 4487.1795 | 1844.8258 | 14000 | 2.82 | 4964.539 | 2231.0285 | 14000 | 2.67 | 5243.4457 | 2578.9309 | 14000 | 2.47 | 5668.0162 | 3095.6441
|  | 17.9378 | 100 | mid | 11200 | 3.97 | 2821.1587 | 1 | 11200 | 3.68 | 3043.4783 | 1 | 11200 | 3.39 | 3303.8348 | 1 | 11200 | 3.09 | 3624.5955 | 1 | 11200 | 2.88 | 3888.8889 | 1 | 11200 | 2.62 | 4274.8092 | 1
|  | 5973.2853 | 1891.4087 | min | 5380 | 4.68 | 1149.5726 | 0.098009 | 4920 | 3.81 | 1291.3386 | 0.16408 | 4500 | 3.18 | 1415.0943 | 0.21648 | 4000 | 2.51 | 1593.6255 | 0.27089 | 3500 | 2.04 | 1715.6863 | 0.31824 | 3000 | 1.53 | 1960.7843 | 0.35981
| 4 |  | 3.3477 | max | 16620 | 3.83 | 4339.4256 | 5.0938 | 16420 | 3.5 | 4691.4286 | 3.9686 | 16160 | 3.17 | 5097.7918 | 3.3308 | 15920 | 2.82 | 5645.3901 | 2.7069 | 15220 | 2.63 | 5787.0722 | 2.3178 | 14420 | 2.41 | 5983.4025 | 1.9061
|  | 5619.8347 | 39.8674 | nom | 14000 | 4 | 3500 | 1103.2771 | 14000 | 3.67 | 3814.7139 | 1416.0613 | 14000 | 3.34 | 4191.6168 | 1687.246 | 14000 | 2.99 | 4682.2742 | 2076.1131 | 14000 | 2.79 | 5017.9211 | 2424.6659 | 14000 | 2.54 | 5511.811 | 2948.3116
|  | 16.8898 | 100 | mid | 11200 | 4.29 | 2610.7226 | 1 | 11200 | 3.96 | 2828.2828 | 1 | 11200 | 3.63 | 3085.3994 | 1 | 11200 | 3.28 | 3414.6341 | 1 | 11200 | 3.01 | 3720.9302 | 1 | 11200 | 2.69 | 4163.5688 | 1
|  | 5624.3007 | 1680.0537 | min | 5160 | 5.16 | 1000 | 0.076132 | 4740 | 3.97 | 1193.9547 | 0.1362 | 4300 | 3.26 | 1319.0184 | 0.19128 | 3800 | 2.52 | 1507.9365 | 0.24592 | 3300 | 2.03 | 1625.6158 | 0.29365 | 2800 | 1.51 | 1854.3046 | 0.33569
| 5 |  | 3.5541 | max | 16680 | 4.12 | 4048.5437 | 5.5825 | 16480 | 3.75 | 4394.6667 | 4.1421 | 16240 | 3.38 | 4804.7337 | 3.4288 | 15980 | 2.98 | 5362.4161 | 2.7389 | 15280 | 2.72 | 5617.6471 | 2.3227 | 14480 | 2.44 | 5934.4262 | 1.8871
|  | 5289.2562 | 39.1216 | nom | 14000 | 4.3 | 3255.814 | 947.465 | 14000 | 3.93 | 3562.341 | 1276.9562 | 14000 | 3.56 | 3932.5843 | 1542.6079 | 14000 | 3.16 | 4430.3797 | 1931.1366 | 14000 | 2.91 | 4810.9966 | 2277.1899 | 14000 | 2.61 | 5363.9847 | 2802.7979
|  | 15.9661 | 100 | mid | 11200 | 4.61 | 2429.5011 | 1 | 11200 | 4.24 | 2641.5094 | 1 | 11200 | 3.87 | 2894.0568 | 1 | 11200 | 3.47 | 3227.6657 | 1 | 11200 | 3.14 | 3566.879 | 1 | 11200 | 2.76 | 4057.971 | 1
|  | 5316.6968 | 1495.94 | min | 4940 | 5.64 | 875.8865 | 0.055792 | 4560 | 4.13 | 1104.1162 | 0.10983 | 4100 | 3.34 | 1227.5449 | 0.1675 | 3600 | 2.53 | 1422.9249 | 0.22227 | 3100 | 2.02 | 1534.6535 | 0.27028 | 2600 | 1.49 | 1744.9664 | 0.3127
| 6 |  | 3.7782 | max | 16740 | 4.41 | 3795.9184 | 6.0762 | 16540 | 4 | 4135 | 4.3095 | 16320 | 3.59 | 4545.961 | 3.5201 | 16040 | 3.14 | 5108.2803 | 2.7638 | 15340 | 2.81 | 5459.0747 | 2.3225 | 14540 | 2.47 | 5886.6397 | 1.8654
|  | 4958.6777 | 38.365 | nom | 14000 | 4.6 | 3043.4783 | 816.0862 | 14000 | 4.19 | 3341.2888 | 1150.6346 | 14000 | 3.78 | 3703.7037 | 1408.6885 | 14000 | 3.33 | 4204.2042 | 1794.1456 | 14000 | 3.03 | 4620.462 | 2135.04 | 14000 | 2.68 | 5223.8806 | 2658.1927
|  | 15.0256 | 100 | mid | 11200 | 4.93 | 2271.8053 | 1 | 11200 | 4.52 | 2477.8761 | 1 | 11200 | 4.11 | 2725.0608 | 1 | 11200 | 3.66 | 3060.1093 | 1 | 11200 | 3.27 | 3425.0765 | 1 | 11200 | 2.83 | 3957.5972 | 1
|  | 5003.5102 | 1324.3066 | min | 4720 | 6.12 | 771.2418 | 0.036833 | 4380 | 4.29 | 1020.979 | 0.08485 | 3900 | 3.42 | 1140.3509 | 0.14502 | 3400 | 2.54 | 1338.5827 | 0.19983 | 2900 | 2.01 | 1442.7861 | 0.24803 | 2400 | 1.47 | 1632.6531 | 0.29076
| 7 |  | 4.0215 | max | 16800 | 4.7 | 3574.4681 | 6.5742 | 16600 | 4.25 | 3905.8824 | 4.4714 | 16400 | 3.8 | 4315.7895 | 3.6052 | 16100 | 3.3 | 4878.7879 | 2.7821 | 15400 | 2.9 | 5310.3448 | 2.3176 | 14600 | 2.5 | 5840 | 1.8412
|  | 4628.0992 | 37.5967 | nom | 14000 | 4.9 | 2857.1429 | 703.9802 | 14000 | 4.45 | 3146.0674 | 1035.0436 | 14000 | 4 | 3500 | 1283.7343 | 14000 | 3.5 | 4000 | 1663.5475 | 14000 | 3.15 | 4444.4444 | 1996.9626 | 14000 | 2.75 | 5090.9091 | 2513.6405
|  | 14.0597 | 100 | mid | 11200 | 5.25 | 2133.3333 | 1 | 11200 | 4.8 | 2333.3333 | 1 | 11200 | 4.35 | 2574.7126 | 1 | 11200 | 3.85 | 2909.0909 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 2.9 | 3862.069 | 1
|  | 4681.8738 | 1164.1983 | min | 4500 | 6.6 | 681.8182 | 0.019119 | 4200 | 4.45 | 943.8202 | 0.061157 | 3700 | 3.5 | 1057.1429 | 0.12375 | 3200 | 2.55 | 1254.902 | 0.17851 | 2700 | 2 | 1350 | 0.22684 | 2200 | 1.45 | 1517.2414 | 0.26979
| 8 |  | 4.2532 | max | 16860 | 4.81 | 3505.1975 | 6.31 | 16640 | 4.38 | 3799.0868 | 4.54 | 16440 | 3.93 | 4183.2061 | 3.7501 | 16160 | 3.48 | 4643.6782 | 3.01 | 15440 | 3.06 | 5045.7516 | 2.5101 | 14640 | 2.64 | 5545.4545 | 2.005
|  | 4297.5207 | 36.8156 | nom | 14000 | 5.02 | 2788.8446 | 681.0651 | 14000 | 4.59 | 3050.1089 | 946.5905 | 14000 | 4.16 | 3365.3846 | 1145.9875 | 14000 | 3.69 | 3794.0379 | 1427.7384 | 14000 | 3.32 | 4216.8675 | 1712.0807 | 14000 | 2.9 | 4827.5862 | 2143.4016
|  | 13.0149 | 100 | mid | 11200 | 5.37 | 2085.6611 | 0 | 11200 | 4.95 | 2262.6263 | 0 | 11200 | 4.53 | 2472.4062 | 1 | 11200 | 4.06 | 2758.6207 | 1 | 11200 | 3.58 | 3128.4916 | 1 | 11200 | 3.06 | 3660.1307 | 1
|  | 4333.9472 | 1018.9944 | min | 4920 | 6.31 | 779.7147 | 0 | 4600 | 4.54 | 1013.2159 | 0 | 4120 | 3.73 | 1104.5576 | 0.025074 | 3640 | 2.91 | 1250.8591 | 0.086974 | 3200 | 2.34 | 1367.5214 | 0.13719 | 2760 | 1.77 | 1559.322 | 0.18217
| 9 |  | 4.4182 | max | 16920 | 4.92 | 3439.0244 | 4.92 | 16680 | 4.51 | 3698.4479 | 4.51 | 16480 | 4.06 | 4059.1133 | 4.06 | 16220 | 3.66 | 4431.694 | 3.66 | 15480 | 3.22 | 4807.4534 | 3.22 | 14680 | 2.78 | 5280.5755 | 2.78
|  | 3966.9421 | 36.0204 | nom | 14000 | 5.14 | 2723.7354 | 806.2891 | 14000 | 4.73 | 2959.8309 | 879.5881 | 14000 | 4.32 | 3240.7407 | 977.0793 | 14000 | 3.88 | 3608.2474 | 1083.864 | 14000 | 3.49 | 4011.4613 | 1231.9696 | 14000 | 3.05 | 4590.1639 | 1426.9576
|  | 11.9341 | 80.857 | mid | 11200 | 5.49 | 2040.0729 | 4 | 11200 | 5.1 | 2196.0784 | 4 | 11200 | 4.71 | 2377.9193 | 4 | 11200 | 4.27 | 2622.9508 | 4 | 11200 | 3.76 | 2978.7234 | 4 | 11200 | 3.22 | 3478.2609 | 4
|  | 3974.0684 | 899.4849 | min | 5340 | 6.02 | 887.0432 | 0 | 5000 | 4.63 | 1079.9136 | 0 | 4540 | 3.96 | 1146.4646 | 0 | 4080 | 3.27 | 1247.7064 | 0 | 3700 | 2.68 | 1380.597 | 0 | 3320 | 2.09 | 1588.5167 | 0
| 10 |  | 4.6978 | max | 16980 | 5.03 | 3375.7455 | 5.73 | 16720 | 4.64 | 3603.4483 | 4.72 | 16520 | 4.19 | 3942.7208 | 4.19 | 16280 | 3.84 | 4239.5833 | 3.63 | 15520 | 3.38 | 4591.716 | 3.02 | 14720 | 2.92 | 5041.0959 | 2.41
|  | 3636.3636 | 35.2099 | nom | 14000 | 5.26 | 2661.597 | 634.6184 | 14000 | 4.87 | 2874.7433 | 770.416 | 14000 | 4.48 | 3125 | 867.8672 | 14000 | 4.07 | 3439.8034 | 1001.7531 | 14000 | 3.66 | 3825.1366 | 1204.0939 | 14000 | 3.2 | 4375 | 1508.8646
|  | 10.9262 | 67.5712 | mid | 11200 | 5.61 | 1996.4349 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.89 | 2290.3885 | 0 | 11200 | 4.48 | 2500 | 0 | 11200 | 3.94 | 2842.6396 | 0 | 11200 | 3.38 | 3313.6095 | 0
|  | 3638.4404 | 774.5062 | min | 5760 | 5.73 | 1005.2356 | 0 | 5400 | 4.72 | 1144.0678 | 0 | 4960 | 4.19 | 1183.7709 | 0 | 4520 | 3.63 | 1245.1791 | 0 | 4200 | 3.02 | 1390.7285 | 0 | 3880 | 2.41 | 1609.9585 | 0
| 11 |  | 4.8489 | max | 17040 | 5.14 | 3315.1751 | 5.44 | 16760 | 4.77 | 3513.6268 | 4.81 | 16560 | 4.32 | 3833.3333 | 4.42 | 16340 | 4.02 | 4064.6766 | 3.99 | 15560 | 3.54 | 4395.4802 | 3.36 | 14760 | 3.06 | 4823.5294 | 2.73
|  | 3305.7851 | 34.3821 | nom | 14000 | 5.38 | 2602.2305 | 607.6811 | 14000 | 5.01 | 2794.4112 | 687.2734 | 14000 | 4.64 | 3017.2414 | 747.9152 | 14000 | 4.26 | 3286.385 | 828.5176 | 14000 | 3.83 | 3655.3525 | 983.8646 | 14000 | 3.35 | 4179.1045 | 1210.9103
|  | 9.936 | 56.7665 | mid | 11200 | 5.73 | 1954.6248 | 0 | 11200 | 5.4 | 2074.0741 | 0 | 11200 | 5.07 | 2209.073 | 0 | 11200 | 4.69 | 2388.0597 | 0 | 11200 | 4.12 | 2718.4466 | 0 | 11200 | 3.54 | 3163.8418 | 0
|  | 3308.6922 | 682.3551 | min | 6180 | 5.44 | 1136.0294 | 0 | 5800 | 4.81 | 1205.8212 | 0 | 5380 | 4.42 | 1217.1946 | 0 | 4960 | 3.99 | 1243.1078 | 0 | 4700 | 3.36 | 1398.8095 | 0 | 4440 | 2.73 | 1626.3736 | 0
| 12 |  | 4.9366 | max | 17100 | 5.25 | 3257.1429 | 5.15 | 16800 | 4.9 | 3428.5714 | 4.9 | 16600 | 4.45 | 3730.3371 | 4.65 | 16400 | 4.2 | 3904.7619 | 4.35 | 15600 | 3.7 | 4216.2162 | 3.7 | 14800 | 3.2 | 4625 | 3.05
|  | 2975.2066 | 33.5349 | nom | 14000 | 5.5 | 2545.4545 | 577.71 | 14000 | 5.15 | 2718.4466 | 607.185 | 14000 | 4.8 | 2916.6667 | 639.8294 | 14000 | 4.45 | 3146.0674 | 683.9555 | 14000 | 4 | 3500 | 804.1099 | 14000 | 3.5 | 4000 | 975.4776
|  | 8.9373 | 47.5379 | mid | 11200 | 5.85 | 1914.5299 | 0 | 11200 | 5.55 | 2018.018 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.9 | 2285.7143 | 0 | 11200 | 4.3 | 2604.6512 | 0 | 11200 | 3.7 | 3027.027 | 0
|  | 2976.128 | 602.8666 | min | 6600 | 5.15 | 1281.5534 | 0 | 6200 | 4.9 | 1265.3061 | 0 | 5800 | 4.65 | 1247.3118 | 0 | 5400 | 4.35 | 1241.3793 | 0 | 5200 | 3.7 | 1405.4054 | 0 | 5000 | 3.05 | 1639.3443 | 0
| 13 |  | 5.0095 | max | 17566.6667 | 5.2833 | 3324.9211 | 5.15 | 17266.6667 | 4.9333 | 3500 | 4.9667 | 17033.3333 | 4.55 | 3743.5897 | 4.7833 | 16833.3333 | 4.3 | 3914.7287 | 4.55 | 16033.3333 | 3.8 | 4219.2982 | 3.9167 | 15200 | 3.3 | 4606.0606 | 3.2667
|  | 2644.6281 | 32.6657 | nom | 14000 | 5.5 | 2545.4545 | 513.52 | 14000 | 5.1833 | 2700.9646 | 532.4755 | 14000 | 4.8667 | 2876.7123 | 552.8839 | 14000 | 4.55 | 3076.9231 | 581.2369 | 14000 | 4.1 | 3414.6341 | 675.2242 | 14000 | 3.6167 | 3870.9677 | 809.58
|  | 7.9437 | 41.5311 | mid | 11200 | 5.9 | 1898.3051 | 0 | 11200 | 5.5833 | 2005.9701 | 0 | 11200 | 5.3167 | 2106.5831 | 0 | 11200 | 5.0167 | 2232.5581 | 0 | 11200 | 4.4167 | 2535.8491 | 0 | 11200 | 3.8167 | 2934.4978 | 0
|  | 2645.2499 | 528.0507 | min | 6700 | 5.15 | 1300.9709 | 0 | 6266.6667 | 4.9667 | 1261.745 | 0 | 5833.3333 | 4.7833 | 1219.5122 | 0 | 5400 | 4.55 | 1186.8132 | 0 | 5233.3333 | 3.9167 | 1336.1702 | 0 | 5066.6667 | 3.2667 | 1551.0204 | 0
| 14 |  | 5.071 | max | 18033.3333 | 5.3167 | 3391.8495 | 5.15 | 17733.3333 | 4.9667 | 3570.4698 | 5.0333 | 17466.6667 | 4.65 | 3756.2724 | 4.9167 | 17266.6667 | 4.4 | 3924.2424 | 4.75 | 16466.6667 | 3.9 | 4222.2222 | 4.1333 | 15600 | 3.4 | 4588.2353 | 3.4833
|  | 2314.0496 | 31.771 | nom | 14000 | 5.5 | 2545.4545 | 449.33 | 14000 | 5.2167 | 2683.7061 | 459.745 | 14000 | 4.9333 | 2837.8378 | 470.6542 | 14000 | 4.65 | 3010.7527 | 487.1683 | 14000 | 4.2 | 3333.3333 | 559.8507 | 14000 | 3.7333 | 3750 | 664.3205
|  | 6.9499 | 35.6885 | mid | 11200 | 5.95 | 1882.3529 | 0 | 11200 | 5.6167 | 1994.0653 | 0 | 11200 | 5.3833 | 2080.4954 | 0 | 11200 | 5.1333 | 2181.8182 | 0 | 11200 | 4.5333 | 2470.5882 | 0 | 11200 | 3.9333 | 2847.4576 | 0
|  | 2314.3152 | 456.3819 | min | 6800 | 5.15 | 1320.3883 | 0 | 6333.3333 | 5.0333 | 1258.2781 | 0 | 5866.6667 | 4.9167 | 1193.2203 | 0 | 5400 | 4.75 | 1136.8421 | 0 | 5266.6667 | 4.1333 | 1274.1935 | 0 | 5133.3333 | 3.4833 | 1473.6842 | 0
| 15 |  | 5.1208 | max | 18500 | 5.35 | 3457.9439 | 5.15 | 18200 | 5 | 3640 | 5.1 | 17900 | 4.75 | 3768.4211 | 5.05 | 17700 | 4.5 | 3933.3333 | 4.95 | 16900 | 4 | 4225 | 4.35 | 16000 | 3.5 | 4571.4286 | 3.7
|  | 1983.4711 | 30.8461 | nom | 14000 | 5.5 | 2545.4545 | 385.14 | 14000 | 5.25 | 2666.6667 | 388.9159 | 14000 | 5 | 2800 | 392.7665 | 14000 | 4.75 | 2947.3684 | 400.7012 | 14000 | 4.3 | 3255.814 | 455.9704 | 14000 | 3.85 | 3636.3636 | 536.0733
|  | 5.9565 | 30.0176 | mid | 11200 | 6 | 1866.6667 | 0 | 11200 | 5.65 | 1982.3009 | 0 | 11200 | 5.45 | 2055.0459 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.65 | 2408.6022 | 0 | 11200 | 4.05 | 2765.4321 | 0
|  | 1983.5169 | 387.3474 | min | 6900 | 5.15 | 1339.8058 | 0 | 6400 | 5.1 | 1254.902 | 0 | 5900 | 5.05 | 1168.3168 | 0 | 5400 | 4.95 | 1090.9091 | 0 | 5300 | 4.35 | 1218.3908 | 0 | 5200 | 3.7 | 1405.4054 | 0
| 16 |  | 6.3143 | max | 19020 | 5.73 | 3319.3717 | 6.92 | 18720 | 5.3 | 3532.0755 | 5.68 | 18420 | 4.95 | 3721.2121 | 5.37 | 18200 | 4.59 | 3965.1416 | 5.02 | 17380 | 4.08 | 4259.8039 | 4.36 | 16460 | 3.56 | 4623.5955 | 3.65
|  | 1652.8926 | 29.8848 | nom | 14000 | 5.93 | 2360.8769 | 238.8573 | 14000 | 5.57 | 2513.465 | 291.0022 | 14000 | 5.21 | 2687.1401 | 307.8012 | 14000 | 4.85 | 2886.5979 | 329.2615 | 14000 | 4.39 | 3189.0661 | 379.1038 | 14000 | 3.92 | 3571.4286 | 452.8473
|  | 5.0122 | 24.5747 | mid | 11200 | 6.42 | 1744.5483 | 0 | 11200 | 5.99 | 1869.783 | 0 | 11200 | 5.68 | 1971.831 | 0 | 11200 | 5.36 | 2089.5522 | 0 | 11200 | 4.74 | 2362.8692 | 0 | 11200 | 4.12 | 2718.4466 | 0
|  | 1669.0489 | 264.3292 | min | 6980 | 6.92 | 1008.6705 | 0 | 6460 | 5.68 | 1137.3239 | 0 | 6000 | 5.37 | 1117.3184 | 0 | 5520 | 5.02 | 1099.6016 | 0 | 5360 | 4.36 | 1229.3578 | 0 | 5180 | 3.65 | 1419.1781 | 0
| 17 |  | 7.7477 | max | 19540 | 6.11 | 3198.036 | 8.69 | 19240 | 5.6 | 3435.7143 | 6.26 | 18940 | 5.15 | 3677.6699 | 5.69 | 18700 | 4.68 | 3995.7265 | 5.09 | 17860 | 4.16 | 4293.2692 | 4.37 | 16920 | 3.62 | 4674.0331 | 3.6
|  | 1322.314 | 28.8778 | nom | 14000 | 6.36 | 2201.2579 | 152.165 | 14000 | 5.89 | 2376.91 | 211.2323 | 14000 | 5.42 | 2583.0258 | 232.3926 | 14000 | 4.95 | 2828.2828 | 259.7867 | 14000 | 4.48 | 3125 | 302.589 | 14000 | 3.99 | 3508.7719 | 367.3095
|  | 4.0732 | 19.3022 | mid | 11200 | 6.84 | 1637.4269 | 0 | 11200 | 6.33 | 1769.3523 | 0 | 11200 | 5.91 | 1895.0931 | 0 | 11200 | 5.47 | 2047.532 | 0 | 11200 | 4.83 | 2318.8406 | 0 | 11200 | 4.19 | 2673.031 | 0
|  | 1356.3898 | 175.07 | min | 7060 | 8.69 | 812.4281 | 0 | 6520 | 6.26 | 1041.5335 | 0 | 6100 | 5.69 | 1072.0562 | 0 | 5640 | 5.09 | 1108.055 | 0 | 5420 | 4.37 | 1240.2746 | 0 | 5160 | 3.6 | 1433.3333 | 0
| 18 |  | 9.4427 | max | 20060 | 6.49 | 3090.9091 | 10.46 | 19760 | 5.9 | 3349.1525 | 6.84 | 19460 | 5.35 | 3637.3832 | 6.01 | 19200 | 4.77 | 4025.1572 | 5.16 | 18340 | 4.24 | 4325.4717 | 4.38 | 17380 | 3.68 | 4722.8261 | 3.55
|  | 991.7355 | 27.8102 | nom | 14000 | 6.79 | 2061.8557 | 94.8122 | 14000 | 6.21 | 2254.4283 | 144.9906 | 14000 | 5.63 | 2486.6785 | 165.0142 | 14000 | 5.05 | 2772.2772 | 192.1968 | 14000 | 4.57 | 3063.4573 | 226.4236 | 14000 | 4.06 | 3448.2759 | 279.3621
|  | 3.0884 | 14.2029 | mid | 11200 | 7.26 | 1542.6997 | 0 | 11200 | 6.67 | 1679.1604 | 0 | 11200 | 6.14 | 1824.1042 | 0 | 11200 | 5.58 | 2007.1685 | 0 | 11200 | 4.92 | 2276.4228 | 0 | 11200 | 4.26 | 2629.108 | 0
|  | 1028.4366 | 108.9133 | min | 7140 | 10.46 | 682.6004 | 0 | 6580 | 6.84 | 961.9883 | 0 | 6200 | 6.01 | 1031.614 | 0 | 5760 | 5.16 | 1116.2791 | 0 | 5480 | 4.38 | 1251.1416 | 0 | 5140 | 3.55 | 1447.8873 | 0
| 19 |  | 11.4338 | max | 20580 | 6.87 | 2995.6332 | 12.23 | 20280 | 6.2 | 3270.9677 | 7.42 | 19980 | 5.55 | 3600 | 6.33 | 19700 | 4.86 | 4053.4979 | 5.23 | 18820 | 4.32 | 4356.4815 | 4.39 | 17840 | 3.74 | 4770.0535 | 3.5
|  | 661.157 | 26.6553 | nom | 14000 | 7.22 | 1939.0582 | 54.0603 | 14000 | 6.53 | 2143.951 | 89.1047 | 14000 | 5.84 | 2397.2603 | 104.4482 | 14000 | 5.15 | 2718.4466 | 126.4163 | 14000 | 4.66 | 3004.2918 | 150.6052 | 14000 | 4.13 | 3389.8305 | 188.902
|  | 2.0554 | 9.2807 | mid | 11200 | 7.68 | 1458.3333 | 0 | 11200 | 7.01 | 1597.7175 | 0 | 11200 | 6.37 | 1758.2418 | 0 | 11200 | 5.69 | 1968.3656 | 0 | 11200 | 5.01 | 2235.5289 | 0 | 11200 | 4.33 | 2586.6051 | 0
|  | 684.4408 | 59.8612 | min | 7220 | 12.23 | 590.3516 | 0 | 6640 | 7.42 | 894.8787 | 0 | 6300 | 6.33 | 995.2607 | 0 | 5880 | 5.23 | 1124.283 | 0 | 5540 | 4.39 | 1261.959 | 0 | 5120 | 3.5 | 1462.8571 | 0
| 20 |  | 13.7892 | max | 21100 | 7.25 | 2910.3448 | 14 | 20800 | 6.5 | 3200 | 8 | 20500 | 5.75 | 3565.2174 | 6.65 | 20200 | 4.95 | 4080.8081 | 5.3 | 19300 | 4.4 | 4386.3636 | 4.4 | 18300 | 3.8 | 4815.7895 | 3.45
|  | 330.5785 | 25.3513 | nom | 14000 | 7.65 | 1830.0654 | 23.6128 | 14000 | 6.85 | 2043.7956 | 41.3223 | 14000 | 6.05 | 2314.0496 | 49.7111 | 14000 | 5.25 | 2666.6667 | 62.3733 | 14000 | 4.75 | 2947.3684 | 75.1315 | 14000 | 4.2 | 3333.3333 | 95.8199
|  | 1.0035 | 4.5416 | mid | 11200 | 8.1 | 1382.716 | 0 | 11200 | 7.35 | 1523.8095 | 0 | 11200 | 6.6 | 1696.9697 | 0 | 11200 | 5.8 | 1931.0345 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.4 | 2545.4545 | 0
|  | 334.1803 | 24.2349 | min | 7300 | 14 | 521.4286 | 0 | 6700 | 8 | 837.5 | 0 | 6400 | 6.65 | 962.406 | 0 | 6000 | 5.3 | 1132.0755 | 0 | 5600 | 4.4 | 1272.7273 | 0 | 5100 | 3.45 | 1478.2609 | 0
Indoor Temp. |  | 22
LWT |  |  | 25 CAP: 25; 35 CAP: 35; 40 CAP: 40; 45 CAP: 45; 50 CAP: 50; 55 CAP: 55
Outdoor air temperature[℃] |  | Heating Demand | COP | CL | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP
|  |  | LWT |  |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI
| -10 |  | 2.0325 | max | 14600 | 2.4 | 6083.3333 | 2.8127 | 14400 | 2.25 | 6400 | 2.6531 | 14200 | 2.1 | 6761.9048 | 2.4945 | 14000 | 1.9 | 7368.4211 | 2.2868 | 14000 | 1.85 | 7567.5676 | 2.0388 | 14000 | 1.75 | 8000 | 1.7853
|  | 10578.5124 | 50.1249 | nom | 14000 | 2.8 | 5000 | 3760.967 | 14000 | 2.5 | 5600 | 3987.2343 | 14000 | 2.2 | 6363.6364 | 4240.7175 | 14000 | 1.9 | 7368.4211 | 4625.9062 | 14000 | 1.85 | 7567.5676 | 5188.6155 | 14000 | 1.75 | 8000 | 5925.4687
|  | 31.781 | 100 | mid | 11200 | 2.85 | 3929.8246 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.1 | 5333.3333 | 1 | 11200 | 1.85 | 6054.0541 | 1
|  | 10583.0624 | 5207.022 | min | 6200 | 2.55 | 2431.3725 | 0.8757 | 5900 | 2.3 | 2565.2174 | 0.88274 | 5600 | 2.05 | 2731.7073 | 0.88902 | 5300 | 1.75 | 3028.5714 | 0.89466 | 4600 | 1.45 | 3172.4138 | 0.90584 | 4000 | 1.1 | 3636.3636 | 0.91368
| -9 |  | 2.095 | max | 15100 | 2.5 | 6040 | 2.9715 | 14900 | 2.3333 | 6385.7143 | 2.7171 | 14700 | 2.1667 | 6784.6154 | 2.5287 | 14500 | 1.9667 | 7372.8814 | 2.3073 | 14233.3333 | 1.9167 | 7426.087 | 2.0705 | 14000 | 1.8167 | 7706.422 | 1.8297
|  | 10247.9339 | 49.4825 | nom | 14000 | 2.8833 | 4855.4913 | 3448.7335 | 14000 | 2.6 | 5384.6154 | 3771.6504 | 14000 | 2.3167 | 6043.1655 | 4052.6427 | 14000 | 2.0333 | 6885.2459 | 4441.5287 | 14000 | 1.95 | 7179.4872 | 4949.3905 | 14000 | 1.8167 | 7706.422 | 5600.9925
|  | 30.8081 | 100 | mid | 11200 | 2.9833 | 3754.1899 | 1 | 11200 | 2.8 | 4000 | 1 | 11200 | 2.6167 | 4280.2548 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.1667 | 5169.2308 | 1 | 11200 | 1.9333 | 5793.1034 | 1
|  | 10259.0898 | 4896.8309 | min | 5833.3333 | 2.9167 | 2000 | 0.8226 | 5266.6667 | 2.2833 | 2306.5693 | 0.83954 | 5066.6667 | 2.05 | 2471.5447 | 0.84477 | 4866.6667 | 1.7833 | 2728.972 | 0.84967 | 4266.6667 | 1.4667 | 2909.0909 | 0.86268 | 3700 | 1.1167 | 3313.4328 | 0.87306
| -8 |  | 2.1543 | max | 15600 | 2.6 | 6000 | 3.154 | 15400 | 2.4167 | 6372.4138 | 2.7763 | 15200 | 2.2333 | 6805.9701 | 2.5615 | 15000 | 2.0333 | 7377.0492 | 2.3299 | 14466.6667 | 1.9833 | 7294.1176 | 2.101 | 14000 | 1.8833 | 7433.6283 | 1.8714
|  | 9917.3554 | 48.8354 | nom | 14000 | 2.9667 | 4719.1011 | 3144.4209 | 14000 | 2.7 | 5185.1852 | 3572.1571 | 14000 | 2.4333 | 5753.4247 | 3871.7254 | 14000 | 2.1667 | 6461.5385 | 4256.4679 | 14000 | 2.05 | 6829.2683 | 4720.4141 | 14000 | 1.8833 | 7433.6283 | 5299.4031
|  | 29.8389 | 100 | mid | 11200 | 3.1167 | 3593.5829 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.6833 | 4173.913 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.2333 | 5014.9254 | 1 | 11200 | 2.0167 | 5553.719 | 1
|  | 9936.3379 | 4612.3499 | min | 5466.6667 | 3.2833 | 1664.9746 | 0.77628 | 4633.3333 | 2.2667 | 2044.1176 | 0.80467 | 4533.3333 | 2.05 | 2211.3821 | 0.8076 | 4433.3333 | 1.8167 | 2440.367 | 0.81045 | 3933.3333 | 1.4833 | 2651.6854 | 0.82349 | 3400 | 1.1333 | 3000 | 0.83556
| -7 |  | 2.2116 | max | 16100 | 2.7 | 5962.963 | 3.3558 | 15900 | 2.5 | 6360 | 2.832 | 15700 | 2.3 | 6826.087 | 2.5932 | 15500 | 2.1 | 7380.9524 | 2.3544 | 14700 | 2.05 | 7170.7317 | 2.1302 | 14000 | 1.95 | 7179.4872 | 1.9108
|  | 9586.7769 | 48.1832 | nom | 14000 | 3.05 | 4590.1639 | 2856.791 | 14000 | 2.8 | 5000 | 3385.214 | 14000 | 2.55 | 5490.1961 | 3696.9493 | 14000 | 2.3 | 6086.9565 | 4071.9217 | 14000 | 2.15 | 6511.6279 | 4500.439 | 14000 | 1.95 | 7179.4872 | 5017.1671
|  | 28.8559 | 100 | mid | 11200 | 3.25 | 3446.1538 | 1 | 11200 | 3 | 3733.3333 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1 | 11200 | 2.1 | 5333.3333 | 1
|  | 9608.9989 | 4344.7348 | min | 5100 | 3.65 | 1397.2603 | 0.73554 | 4000 | 2.25 | 1777.7778 | 0.77594 | 4000 | 2.05 | 1951.2195 | 0.77594 | 4000 | 1.85 | 2162.1622 | 0.77594 | 3600 | 1.5 | 2400 | 0.78773 | 3100 | 1.15 | 2695.6522 | 0.80084
| -6 |  | 2.2608 | max | 16144.4444 | 2.7611 | 5847.0825 | 3.4284 | 15944.4444 | 2.5556 | 6239.1304 | 2.869 | 15733.3333 | 2.35 | 6695.0355 | 2.6231 | 15533.3333 | 2.1444 | 7243.5233 | 2.3759 | 14744.4444 | 2.0944 | 7039.7878 | 2.1479 | 14033.3333 | 1.9944 | 7036.2117 | 1.9204
|  | 9256.1983 | 47.5259 | nom | 14000 | 3.0889 | 4532.3741 | 2699.8295 | 14000 | 2.8389 | 4931.5068 | 3226.2989 | 14000 | 2.5889 | 5407.7253 | 3528.7102 | 14000 | 2.3389 | 5985.7482 | 3895.8023 | 14000 | 2.1944 | 6379.7468 | 4309.3461 | 14000 | 2 | 7000 | 4819.995
|  | 27.8672 | 100 | mid | 11200 | 3.2944 | 3399.6627 | 1 | 11200 | 3.0444 | 3678.8321 | 1 | 11200 | 2.7944 | 4007.9523 | 1 | 11200 | 2.5444 | 4401.7467 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.15 | 5209.3023 | 1
|  | 9279.7684 | 4104.7123 | min | 5155.5556 | 3.7111 | 1389.2216 | 0.67842 | 4122.2222 | 2.4056 | 1713.6259 | 0.72537 | 4077.7778 | 2.1667 | 1882.0513 | 0.72708 | 4022.2222 | 1.9222 | 2092.4855 | 0.72919 | 3611.1111 | 1.5611 | 2313.1673 | 0.74386 | 3111.1111 | 1.1944 | 2604.6512 | 0.75969
| -5 |  | 2.313 | max | 16188.8889 | 2.8222 | 5736.2205 | 3.5035 | 15988.8889 | 2.6111 | 6123.4043 | 2.9163 | 15766.6667 | 2.4 | 6569.4444 | 2.6595 | 15566.6667 | 2.1889 | 7111.6751 | 2.3999 | 14788.8889 | 2.1389 | 6914.2857 | 2.1666 | 14066.6667 | 2.0389 | 6899.1826 | 1.9294
|  | 8925.6198 | 46.863 | nom | 14000 | 3.1278 | 4476.0213 | 2547.6626 | 14000 | 2.8778 | 4864.8649 | 3060.5846 | 14000 | 2.6278 | 5327.6956 | 3356.1001 | 14000 | 2.3778 | 5887.8505 | 3719.0922 | 14000 | 2.2389 | 6253.1017 | 4119.7211 | 14000 | 2.05 | 6829.2683 | 4626.137
|  | 26.8693 | 100 | mid | 11200 | 3.3389 | 3354.4093 | 1 | 11200 | 3.0889 | 3625.8993 | 1 | 11200 | 2.8389 | 3945.2055 | 1 | 11200 | 2.5889 | 4326.1803 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.2 | 5090.9091 | 1
|  | 8947.4778 | 3868.3697 | min | 5211.1111 | 3.7722 | 1381.4433 | 0.62023 | 4244.4444 | 2.5611 | 1657.2668 | 0.67301 | 4155.5556 | 2.2833 | 1819.9513 | 0.67714 | 4044.4444 | 1.9944 | 2027.8552 | 0.68215 | 3622.2222 | 1.6222 | 2232.8767 | 0.69986 | 3122.2222 | 1.2389 | 2520.1794 | 0.71844
| -4 |  | 2.369 | max | 16233.3333 | 2.8833 | 5630.0578 | 3.5809 | 16033.3333 | 2.6667 | 6012.5 | 2.9745 | 15800 | 2.45 | 6448.9796 | 2.7026 | 15600 | 2.2333 | 6985.0746 | 2.4264 | 14833.3333 | 2.1833 | 6793.8931 | 2.1861 | 14100 | 2.0833 | 6768 | 1.9378
|  | 8595.0413 | 46.1945 | nom | 14000 | 3.1667 | 4421.0526 | 2400.2458 | 14000 | 2.9167 | 4800 | 2889.5806 | 14000 | 2.6667 | 5250 | 3180.2784 | 14000 | 2.4167 | 5793.1034 | 3542.3057 | 14000 | 2.2833 | 6131.3869 | 3931.7473 | 14000 | 2.1 | 6666.6667 | 4435.3823
|  | 25.862 | 100 | mid | 11200 | 3.3833 | 3310.3448 | 1 | 11200 | 3.1333 | 3574.4681 | 1 | 11200 | 2.8833 | 3884.3931 | 1 | 11200 | 2.6333 | 4253.1646 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.25 | 4977.7778 | 1
|  | 8612.0601 | 3635.3463 | min | 5266.6667 | 3.8333 | 1373.913 | 0.56096 | 4366.6667 | 2.7167 | 1607.362 | 0.61879 | 4233.3333 | 2.4 | 1763.8889 | 0.62608 | 4066.6667 | 2.0667 | 1967.7419 | 0.63482 | 3633.3333 | 1.6833 | 2158.4158 | 0.65573 | 3133.3333 | 1.2833 | 2441.5584 | 0.67707
| -3 |  | 2.4294 | max | 16277.7778 | 2.9444 | 5528.3019 | 3.6608 | 16077.7778 | 2.7222 | 5906.1224 | 3.0441 | 15833.3333 | 2.5 | 6333.3333 | 2.7526 | 15633.3333 | 2.2778 | 6863.4146 | 2.4553 | 14877.7778 | 2.2278 | 6678.3042 | 2.2064 | 14133.3333 | 2.1278 | 6642.2977 | 1.9457
|  | 8264.4628 | 45.5201 | nom | 14000 | 3.2056 | 4367.4177 | 2257.5287 | 14000 | 2.9556 | 4736.8421 | 2714.8909 | 14000 | 2.7056 | 5174.538 | 3002.4287 | 14000 | 2.4556 | 5701.3575 | 3365.9425 | 14000 | 2.3278 | 6014.3198 | 3745.5989 | 14000 | 2.15 | 6511.6279 | 4247.5284
|  | 24.8447 | 100 | mid | 11200 | 3.4278 | 3267.423 | 1 | 11200 | 3.1778 | 3524.4755 | 1 | 11200 | 2.9278 | 3825.4269 | 1 | 11200 | 2.6778 | 4182.5726 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1
|  | 8273.2685 | 3405.4323 | min | 5322.2222 | 3.8944 | 1366.6191 | 0.50057 | 4488.8889 | 2.8722 | 1562.8627 | 0.56259 | 4311.1111 | 2.5167 | 1713.0243 | 0.57387 | 4088.8889 | 2.1389 | 1911.6883 | 0.58719 | 3644.4444 | 1.7444 | 2089.172 | 0.61147 | 3144.4444 | 1.3278 | 2368.2008 | 0.63559
| -2 |  | 2.4971 | max | 16322.2222 | 3.0056 | 5430.6839 | 3.7434 | 16122.2222 | 2.7778 | 5804 | 3.1258 | 15866.6667 | 2.55 | 6222.2222 | 2.8097 | 15666.6667 | 2.3222 | 6746.4115 | 2.4867 | 14922.2222 | 2.2722 | 6567.2372 | 2.2277 | 14166.6667 | 2.1722 | 6521.7391 | 1.953
|  | 7933.8843 | 44.8394 | nom | 14000 | 3.2444 | 4315.0685 | 2119.4555 | 14000 | 2.9944 | 4675.3247 | 2538.164 | 14000 | 2.7444 | 5101.2146 | 2823.7321 | 14000 | 2.4944 | 5612.4722 | 3190.4834 | 14000 | 2.3722 | 5901.6393 | 3561.4408 | 14000 | 2.2 | 6363.6364 | 4062.3805
|  | 23.8365 | 100 | mid | 11200 | 3.4722 | 3225.6 | 1 | 11200 | 3.2222 | 3475.8621 | 1 | 11200 | 2.9722 | 3768.2243 | 1 | 11200 | 2.7222 | 4114.2857 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1
|  | 7937.5679 | 3178.6999 | min | 5377.7778 | 3.9556 | 1359.5506 | 0.43903 | 4611.1111 | 3.0278 | 1522.9358 | 0.5043 | 4388.8889 | 2.6333 | 1666.6667 | 0.52047 | 4111.1111 | 2.2111 | 1859.2965 | 0.53926 | 3655.5556 | 1.8056 | 2024.6154 | 0.56708 | 3155.5556 | 1.3722 | 2299.5951 | 0.59399
| -1 |  | 2.5806 | max | 16366.6667 | 3.0667 | 5336.9565 | 3.8285 | 16166.6667 | 2.8333 | 5705.8824 | 3.2203 | 15900 | 2.6 | 6115.3846 | 2.8742 | 15700 | 2.3667 | 6633.8028 | 2.5207 | 14966.6667 | 2.3167 | 6460.4317 | 2.2499 | 14200 | 2.2167 | 6406.015 | 1.9597
|  | 7603.3058 | 44.1521 | nom | 14000 | 3.2833 | 4263.9594 | 1985.9654 | 14000 | 3.0333 | 4615.3846 | 2361.0423 | 14000 | 2.7833 | 5029.9401 | 2645.3427 | 14000 | 2.5333 | 5526.3158 | 3016.3872 | 14000 | 2.4167 | 5793.1034 | 3379.4283 | 14000 | 2.25 | 6222.2222 | 3879.7508
|  | 22.8882 | 100 | mid | 11200 | 3.5167 | 3184.8341 | 1 | 11200 | 3.2667 | 3428.5714 | 1 | 11200 | 3.0167 | 3712.7072 | 1 | 11200 | 2.7667 | 4048.1928 | 1 | 11200 | 2.6 | 4307.6923 | 1 | 11200 | 2.4 | 4666.6667 | 1
|  | 7621.7805 | 2953.4621 | min | 5433.3333 | 4.0167 | 1352.6971 | 0.3763 | 4733.3333 | 3.1833 | 1486.911 | 0.44381 | 4466.6667 | 2.75 | 1624.2424 | 0.46584 | 4133.3333 | 2.2833 | 1810.219 | 0.49103 | 3666.6667 | 1.8667 | 1964.2857 | 0.52256 | 3166.6667 | 1.4167 | 2235.2941 | 0.55228
| 0 |  | 2.6772 | max | 16411.1111 | 3.1278 | 5246.8917 | 3.9164 | 16211.1111 | 2.8889 | 5611.5385 | 3.3283 | 15933.3333 | 2.65 | 6012.5786 | 2.9464 | 15733.3333 | 2.4111 | 6525.3456 | 2.5571 | 15011.1111 | 2.3611 | 6357.6471 | 2.2729 | 14233.3333 | 2.2611 | 6294.8403 | 1.9659
|  | 7272.7273 | 43.4578 | nom | 14000 | 3.3222 | 4214.0468 | 1856.9933 | 14000 | 3.0722 | 4556.962 | 2185.1139 | 14000 | 2.8222 | 4960.6299 | 2468.3649 | 14000 | 2.5722 | 5442.7646 | 2844.0873 | 14000 | 2.4611 | 5688.4876 | 3199.707 | 14000 | 2.3 | 6086.9565 | 3699.4575
|  | 21.9337 | 100 | mid | 11200 | 3.5611 | 3145.0858 | 1 | 11200 | 3.3111 | 3382.5503 | 1 | 11200 | 3.0611 | 3658.8022 | 1 | 11200 | 2.8111 | 3984.1897 | 1 | 11200 | 2.65 | 4226.4151 | 1 | 11200 | 2.45 | 4571.4286 | 1
|  | 7303.9217 | 2728.2011 | min | 5488.8889 | 4.0778 | 1346.049 | 0.31235 | 4855.5556 | 3.3389 | 1454.2429 | 0.38099 | 4544.4444 | 2.8667 | 1585.2713 | 0.40993 | 4155.5556 | 2.3556 | 1764.1509 | 0.4425 | 3677.7778 | 1.9278 | 1907.781 | 0.47791 | 3177.7778 | 1.4611 | 2174.9049 | 0.51045
| 1 |  | 2.7893 | max | 16455.5556 | 3.1889 | 5160.2787 | 4.0071 | 16255.5556 | 2.9444 | 5520.7547 | 3.4506 | 15966.6667 | 2.7 | 5913.5802 | 3.0264 | 15766.6667 | 2.4556 | 6420.8145 | 2.5962 | 15055.5556 | 2.4056 | 6258.6605 | 2.2969 | 14266.6667 | 2.3056 | 6187.9518 | 1.9715
|  | 6942.1488 | 42.7563 | nom | 14000 | 3.3611 | 4165.2893 | 1732.4699 | 14000 | 3.1111 | 4500 | 2011.869 | 14000 | 2.8611 | 4893.2039 | 2293.8332 | 14000 | 2.6111 | 5361.7021 | 2673.989 | 14000 | 2.5056 | 5587.5831 | 3022.4126 | 14000 | 2.35 | 5957.4468 | 3521.3245
|  | 20.9688 | 100 | mid | 11200 | 3.6056 | 3106.3174 | 1 | 11200 | 3.3556 | 3337.7483 | 1 | 11200 | 3.1056 | 3606.4401 | 1 | 11200 | 2.8556 | 3922.179 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.5 | 4480 | 1
|  | 6982.6108 | 2503.3953 | min | 5544.4444 | 4.1389 | 1339.5973 | 0.24714 | 4977.7778 | 3.4944 | 1424.4833 | 0.3157 | 4622.2222 | 2.9833 | 1549.3482 | 0.35269 | 4177.7778 | 2.4278 | 1720.8238 | 0.39366 | 3688.8889 | 1.9889 | 1854.7486 | 0.43313 | 3188.8889 | 1.5056 | 2118.0812 | 0.46851
14kW-Maximum heating CAP | 2 |  | 2.9195 | max | 16500 | 3.25 | 5076.9231 | 4.1006 | 16300 | 3 | 5433.3333 | 3.5881 | 16000 | 2.75 | 5818.1818 | 3.1147 | 15800 | 2.5 | 6320 | 2.6378 | 15100 | 2.45 | 6163.2653 | 2.3217 | 14300 | 2.35 | 6085.1064 | 1.9764
|  | 6611.5702 | 42.047 | nom | 14000 | 3.4 | 4117.6471 | 1612.3228 | 14000 | 3.15 | 4444.4444 | 1842.6637 | 14000 | 2.9 | 4827.5862 | 2122.6959 | 14000 | 2.65 | 5283.0189 | 2506.4676 | 14000 | 2.55 | 5490.1961 | 2847.671 | 14000 | 2.4 | 5833.3333 | 3345.1808
|  | 19.9875 | 100 | mid | 11200 | 3.65 | 3068.4932 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 3.15 | 3555.5556 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.55 | 4392.1569 | 1
|  | 6655.8229 | 2279.8085 | min | 5600 | 4.2 | 1333.3333 | 0.18064 | 5100 | 3.65 | 1397.2603 | 0.2478 | 4700 | 3.1 | 1516.129 | 0.29409 | 4200 | 2.5 | 1680 | 0.34451 | 3700 | 2.05 | 1804.878 | 0.38821 | 3200 | 1.55 | 2064.5161 | 0.42645
| 3 |  | 3.0917 | max | 16560 | 3.54 | 4677.9661 | 4.5701 | 16360 | 3.25 | 5033.8462 | 3.7818 | 16080 | 2.96 | 5432.4324 | 3.2358 | 15860 | 2.66 | 5962.406 | 2.6937 | 15160 | 2.54 | 5968.5039 | 2.3434 | 14360 | 2.38 | 6033.6134 | 1.9661
|  | 6280.9917 | 41.3294 | nom | 14000 | 3.7 | 3783.7838 | 1374.3708 | 14000 | 3.41 | 4105.5718 | 1660.8355 | 14000 | 3.12 | 4487.1795 | 1941.0807 | 14000 | 2.82 | 4964.539 | 2331.6936 | 14000 | 2.67 | 5243.4457 | 2680.3119 | 14000 | 2.47 | 5668.0162 | 3194.5934
|  | 18.9859 | 100 | mid | 11200 | 3.97 | 2821.1587 | 1 | 11200 | 3.68 | 3043.4783 | 1 | 11200 | 3.39 | 3303.8348 | 1 | 11200 | 3.09 | 3624.5955 | 1 | 11200 | 2.88 | 3888.8889 | 1 | 11200 | 2.62 | 4274.8092 | 1
|  | 6322.3213 | 2044.9374 | min | 5380 | 4.68 | 1149.5726 | 0.15481 | 4920 | 3.81 | 1291.3386 | 0.21672 | 4500 | 3.18 | 1415.0943 | 0.26582 | 4000 | 2.51 | 1593.6255 | 0.3168 | 3500 | 2.04 | 1715.6863 | 0.36117 | 3000 | 1.53 | 1960.7843 | 0.40012
| 4 |  | 3.2752 | max | 16620 | 3.83 | 4339.4256 | 5.0461 | 16420 | 3.5 | 4691.4286 | 3.9681 | 16160 | 3.17 | 5097.7918 | 3.3485 | 15920 | 2.82 | 5645.3901 | 2.7409 | 15220 | 2.63 | 5787.0722 | 2.3588 | 14420 | 2.41 | 5983.4025 | 1.9526
|  | 5950.4132 | 40.6031 | nom | 14000 | 4 | 3500 | 1179.1989 | 14000 | 3.67 | 3814.7139 | 1499.5524 | 14000 | 3.34 | 4191.6168 | 1777.0382 | 14000 | 2.99 | 4682.2742 | 2171.0076 | 14000 | 2.79 | 5017.9211 | 2522.6598 | 14000 | 2.54 | 5511.811 | 3047.4962
|  | 17.9454 | 100 | mid | 11200 | 4.29 | 2610.7226 | 1 | 11200 | 3.96 | 2828.2828 | 1 | 11200 | 3.63 | 3085.3994 | 1 | 11200 | 3.28 | 3414.6341 | 1 | 11200 | 3.01 | 3720.9302 | 1 | 11200 | 2.69 | 4163.5688 | 1
|  | 5975.8055 | 1824.5579 | min | 5160 | 5.16 | 1000 | 0.13086 | 4740 | 3.97 | 1193.9547 | 0.18737 | 4300 | 3.26 | 1319.0184 | 0.23919 | 3800 | 2.52 | 1507.9365 | 0.2906 | 3300 | 2.03 | 1625.6158 | 0.3355 | 2800 | 1.51 | 1854.3046 | 0.37505
| 5 |  | 3.4719 | max | 16680 | 4.12 | 4048.5437 | 5.5281 | 16480 | 3.75 | 4394.6667 | 4.1476 | 16240 | 3.38 | 4804.7337 | 3.4535 | 15980 | 2.98 | 5362.4161 | 2.7798 | 15280 | 2.72 | 5617.6471 | 2.3684 | 14480 | 2.44 | 5934.4262 | 1.936
|  | 5619.8347 | 39.8674 | nom | 14000 | 4.3 | 3255.814 | 1016.5865 | 14000 | 3.93 | 3562.341 | 1354.9745 | 14000 | 3.56 | 3932.5843 | 1627.3091 | 14000 | 3.16 | 4430.3797 | 2021.653 | 14000 | 2.91 | 4810.9966 | 2372.8186 | 14000 | 2.61 | 5363.9847 | 2902.8787
|  | 16.891 | 100 | mid | 11200 | 4.61 | 2429.5011 | 1 | 11200 | 4.24 | 2641.5094 | 1 | 11200 | 3.87 | 2894.0568 | 1 | 11200 | 3.47 | 3227.6657 | 1 | 11200 | 3.14 | 3566.879 | 1 | 11200 | 2.76 | 4057.971 | 1
|  | 5624.7151 | 1620.0863 | min | 4940 | 5.64 | 875.8865 | 0.1086 | 4560 | 4.13 | 1104.1162 | 0.15961 | 4100 | 3.34 | 1227.5449 | 0.21406 | 3600 | 2.53 | 1422.9249 | 0.26577 | 3100 | 2.02 | 1534.6535 | 0.31109 | 2600 | 1.49 | 1744.9664 | 0.35114
| 6 |  | 3.6865 | max | 16740 | 4.41 | 3795.9184 | 6.0155 | 16540 | 4 | 4135 | 4.3207 | 16320 | 3.59 | 4545.961 | 3.5513 | 16040 | 3.14 | 5108.2803 | 2.8113 | 15340 | 2.81 | 5459.0747 | 2.3727 | 14540 | 2.47 | 5886.6397 | 1.9165
|  | 5289.2562 | 39.1216 | nom | 14000 | 4.6 | 3043.4783 | 879.277 | 14000 | 4.19 | 3341.2888 | 1224.1767 | 14000 | 3.78 | 3703.7037 | 1489.3804 | 14000 | 3.33 | 4204.2042 | 1881.442 | 14000 | 3.03 | 4620.462 | 2229.2081 | 14000 | 2.68 | 5223.8806 | 2759.8211
|  | 15.9724 | 100 | mid | 11200 | 4.93 | 2271.8053 | 1 | 11200 | 4.52 | 2477.8761 | 1 | 11200 | 4.11 | 2725.0608 | 1 | 11200 | 3.66 | 3060.1093 | 1 | 11200 | 3.27 | 3425.0765 | 1 | 11200 | 2.83 | 3957.5972 | 1
|  | 5318.8029 | 1442.7911 | min | 4720 | 6.12 | 771.2418 | 0.087848 | 4380 | 4.29 | 1020.979 | 0.13332 | 3900 | 3.42 | 1140.3509 | 0.19031 | 3400 | 2.54 | 1338.5827 | 0.24221 | 2900 | 2.01 | 1442.7861 | 0.28786 | 2400 | 1.47 | 1632.6531 | 0.32832
| 7 |  | 3.9191 | max | 16800 | 4.7 | 3574.4681 | 6.5076 | 16600 | 4.25 | 3905.8824 | 4.4879 | 16400 | 3.8 | 4315.7895 | 3.6427 | 16100 | 3.3 | 4878.7879 | 2.8358 | 15400 | 2.9 | 5310.3448 | 2.372 | 14600 | 2.5 | 5840 | 1.8945
|  | 4958.6777 | 38.365 | nom | 14000 | 4.9 | 2857.1429 | 761.9849 | 14000 | 4.45 | 3146.0674 | 1104.891 | 14000 | 4 | 3500 | 1361.283 | 14000 | 3.5 | 4000 | 1748.6084 | 14000 | 3.15 | 4444.4444 | 2090.4895 | 14000 | 2.75 | 5090.9091 | 2617.4711
|  | 15.0341 | 100 | mid | 11200 | 5.25 | 2133.3333 | 1 | 11200 | 4.8 | 2333.3333 | 1 | 11200 | 4.35 | 2574.7126 | 1 | 11200 | 3.85 | 2909.0909 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 2.9 | 3862.069 | 1
|  | 5006.3719 | 1277.4445 | min | 4500 | 6.6 | 681.8182 | 0.068459 | 4200 | 4.45 | 943.8202 | 0.10838 | 3700 | 3.5 | 1057.1429 | 0.16782 | 3200 | 2.55 | 1254.902 | 0.21983 | 2700 | 2 | 1350 | 0.26573 | 2200 | 1.45 | 1517.2414 | 0.30652
| 8 |  | 4.15 | max | 16860 | 4.81 | 3505.1975 | 6.31 | 16640 | 4.38 | 3799.0868 | 4.5417 | 16440 | 3.93 | 4183.2061 | 3.7874 | 16160 | 3.48 | 4643.6782 | 3.0603 | 15440 | 3.06 | 5045.7516 | 2.5614 | 14640 | 2.64 | 5545.4545 | 2.0555
|  | 4628.0992 | 37.5967 | nom | 14000 | 5.02 | 2788.8446 | 733.4547 | 14000 | 4.59 | 3050.1089 | 1019.0133 | 14000 | 4.16 | 3365.3846 | 1221.9687 | 14000 | 3.69 | 3794.0379 | 1512.2994 | 14000 | 3.32 | 4216.8675 | 1806.8946 | 14000 | 2.9 | 4827.5862 | 2251.539
|  | 14.013 | 100 | mid | 11200 | 5.37 | 2085.6611 | 0 | 11200 | 4.95 | 2262.6263 | 1 | 11200 | 4.53 | 2472.4062 | 1 | 11200 | 4.06 | 2758.6207 | 1 | 11200 | 3.58 | 3128.4916 | 1 | 11200 | 3.06 | 3660.1307 | 1
|  | 4666.3159 | 1124.4159 | min | 4920 | 6.31 | 779.7147 | 0 | 4600 | 4.54 | 1013.2159 | 0.0042575 | 4120 | 3.73 | 1104.5576 | 0.071765 | 3640 | 2.91 | 1250.8591 | 0.1307 | 3200 | 2.34 | 1367.5214 | 0.17851 | 2760 | 1.77 | 1559.322 | 0.22134
| 9 |  | 4.3867 | max | 16920 | 4.92 | 3439.0244 | 6.02 | 16680 | 4.51 | 3698.4479 | 4.63 | 16480 | 4.06 | 4059.1133 | 3.96 | 16220 | 3.66 | 4431.694 | 3.3006 | 15480 | 3.22 | 4807.4534 | 2.766 | 14680 | 2.78 | 5280.5755 | 2.78
|  | 4297.5207 | 36.8156 | nom | 14000 | 5.14 | 2723.7354 | 713.8739 | 14000 | 4.73 | 2959.8309 | 928.1902 | 14000 | 4.32 | 3240.7407 | 1085.2325 | 14000 | 3.88 | 3608.2474 | 1302.0617 | 14000 | 3.49 | 4011.4613 | 1553.671 | 14000 | 3.05 | 4590.1639 | 1545.8707
|  | 12.9785 | 88.921 | mid | 11200 | 5.49 | 2040.0729 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.71 | 2377.9193 | 0 | 11200 | 4.27 | 2622.9508 | 1 | 11200 | 3.76 | 2978.7234 | 1 | 11200 | 3.22 | 3478.2609 | 4
|  | 4321.8537 | 985.2145 | min | 5340 | 6.02 | 887.0432 | 0 | 5000 | 4.63 | 1079.9136 | 0 | 4540 | 3.96 | 1146.4646 | 0 | 4080 | 3.27 | 1247.7064 | 0.030551 | 3700 | 2.68 | 1380.597 | 0.079669 | 3320 | 2.09 | 1588.5167 | 0
| 10 |  | 4.6118 | max | 16980 | 5.03 | 3375.7455 | 5.73 | 16720 | 4.64 | 3603.4483 | 4.72 | 16520 | 4.19 | 3942.7208 | 4.19 | 16280 | 3.84 | 4239.5833 | 3.63 | 15520 | 3.38 | 4591.716 | 3.02 | 14720 | 2.92 | 5041.0959 | 2.4215
|  | 3966.9421 | 36.0204 | nom | 14000 | 5.26 | 2661.597 | 692.311 | 14000 | 4.87 | 2874.7433 | 840.4538 | 14000 | 4.48 | 3125 | 946.7642 | 14000 | 4.07 | 3439.8034 | 1092.8215 | 14000 | 3.66 | 3825.1366 | 1313.557 | 14000 | 3.2 | 4375 | 1638.2026
|  | 11.9402 | 74.7042 | mid | 11200 | 5.61 | 1996.4349 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.89 | 2290.3885 | 0 | 11200 | 4.48 | 2500 | 0 | 11200 | 3.94 | 2842.6396 | 0 | 11200 | 3.38 | 3313.6095 | 1
|  | 3976.0946 | 862.1506 | min | 5760 | 5.73 | 1005.2356 | 0 | 5400 | 4.72 | 1144.0678 | 0 | 4960 | 4.19 | 1183.7709 | 0 | 4520 | 3.63 | 1245.1791 | 0 | 4200 | 3.02 | 1390.7285 | 0 | 3880 | 2.41 | 1609.9585 | 0.011877
| 11 |  | 4.7936 | max | 17040 | 5.14 | 3315.1751 | 5.44 | 16760 | 4.77 | 3513.6268 | 4.81 | 16560 | 4.32 | 3833.3333 | 4.42 | 16340 | 4.02 | 4064.6766 | 3.99 | 15560 | 3.54 | 4395.4802 | 3.36 | 14760 | 3.06 | 4823.5294 | 2.73
|  | 3636.3636 | 35.2099 | nom | 14000 | 5.38 | 2602.2305 | 668.4492 | 14000 | 5.01 | 2794.4112 | 756.0008 | 14000 | 4.64 | 3017.2414 | 822.7067 | 14000 | 4.26 | 3286.385 | 911.3693 | 14000 | 3.83 | 3655.3525 | 1082.2511 | 14000 | 3.35 | 4179.1045 | 1332.0013
|  | 10.9232 | 62.8871 | mid | 11200 | 5.73 | 1954.6248 | 0 | 11200 | 5.4 | 2074.0741 | 0 | 11200 | 5.07 | 2209.073 | 0 | 11200 | 4.69 | 2388.0597 | 0 | 11200 | 4.12 | 2718.4466 | 0 | 11200 | 3.54 | 3163.8418 | 0
|  | 3637.4097 | 758.8005 | min | 6180 | 5.44 | 1136.0294 | 0 | 5800 | 4.81 | 1205.8212 | 0 | 5380 | 4.42 | 1217.1946 | 0 | 4960 | 3.99 | 1243.1078 | 0 | 4700 | 3.36 | 1398.8095 | 0 | 4440 | 2.73 | 1626.3736 | 0
| 12 |  | 4.9154 | max | 17100 | 5.25 | 3257.1429 | 5.15 | 16800 | 4.9 | 3428.5714 | 4.9 | 16600 | 4.45 | 3730.3371 | 4.65 | 16400 | 4.2 | 3904.7619 | 4.35 | 15600 | 3.7 | 4216.2162 | 3.7 | 14800 | 3.2 | 4625 | 3.05
|  | 3305.7851 | 34.3821 | nom | 14000 | 5.5 | 2545.4545 | 641.9 | 14000 | 5.15 | 2718.4466 | 674.65 | 14000 | 4.8 | 2916.6667 | 710.9215 | 14000 | 4.45 | 3146.0674 | 759.9506 | 14000 | 4 | 3500 | 893.4554 | 14000 | 3.5 | 4000 | 1083.864
|  | 9.9287 | 53.1074 | mid | 11200 | 5.85 | 1914.5299 | 0 | 11200 | 5.55 | 2018.018 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.9 | 2285.7143 | 0 | 11200 | 4.3 | 2604.6512 | 0 | 11200 | 3.7 | 3027.027 | 0
|  | 3306.2598 | 672.6263 | min | 6600 | 5.15 | 1281.5534 | 0 | 6200 | 4.9 | 1265.3061 | 0 | 5800 | 4.65 | 1247.3118 | 0 | 5400 | 4.35 | 1241.3793 | 0 | 5200 | 3.7 | 1405.4054 | 0 | 5000 | 3.05 | 1639.3443 | 0
| 13 |  | 4.9935 | max | 17566.6667 | 5.2833 | 3324.9211 | 5.15 | 17266.6667 | 4.9333 | 3500 | 4.9667 | 17033.3333 | 4.55 | 3743.5897 | 4.7833 | 16833.3333 | 4.3 | 3914.7287 | 4.55 | 16033.3333 | 3.8 | 4219.2982 | 3.9167 | 15200 | 3.3 | 4606.0606 | 3.2667
|  | 2975.2066 | 33.5349 | nom | 14000 | 5.5 | 2545.4545 | 577.71 | 14000 | 5.1833 | 2700.9646 | 599.0349 | 14000 | 4.8667 | 2876.7123 | 621.9944 | 14000 | 4.55 | 3076.9231 | 653.8916 | 14000 | 4.1 | 3414.6341 | 759.6272 | 14000 | 3.6167 | 3870.9677 | 910.7775
|  | 8.936 | 47.0005 | mid | 11200 | 5.9 | 1898.3051 | 0 | 11200 | 5.5833 | 2005.9701 | 0 | 11200 | 5.3167 | 2106.5831 | 0 | 11200 | 5.0167 | 2232.5581 | 0 | 11200 | 4.4167 | 2535.8491 | 0 | 11200 | 3.8167 | 2934.4978 | 0
|  | 2975.6955 | 595.9106 | min | 6700 | 5.15 | 1300.9709 | 0 | 6266.6667 | 4.9667 | 1261.745 | 0 | 5833.3333 | 4.7833 | 1219.5122 | 0 | 5400 | 4.55 | 1186.8132 | 0 | 5233.3333 | 3.9167 | 1336.1702 | 0 | 5066.6667 | 3.2667 | 1551.0204 | 0
| 14 |  | 5.0606 | max | 18033.3333 | 5.3167 | 3391.8495 | 5.15 | 17733.3333 | 4.9667 | 3570.4698 | 5.0333 | 17466.6667 | 4.65 | 3756.2724 | 4.9167 | 17266.6667 | 4.4 | 3924.2424 | 4.75 | 16466.6667 | 3.9 | 4222.2222 | 4.1333 | 15600 | 3.4 | 4588.2353 | 3.4833
|  | 2644.6281 | 32.6657 | nom | 14000 | 5.5 | 2545.4545 | 513.52 | 14000 | 5.2167 | 2683.7061 | 525.4228 | 14000 | 4.9333 | 2837.8378 | 537.8905 | 14000 | 4.65 | 3010.7527 | 556.7638 | 14000 | 4.2 | 3333.3333 | 639.8294 | 14000 | 3.7333 | 3750 | 759.2234
|  | 7.9426 | 41.0512 | mid | 11200 | 5.95 | 1882.3529 | 0 | 11200 | 5.6167 | 1994.0653 | 0 | 11200 | 5.3833 | 2080.4954 | 0 | 11200 | 5.1333 | 2181.8182 | 0 | 11200 | 4.5333 | 2470.5882 | 0 | 11200 | 3.9333 | 2847.4576 | 0
|  | 2644.8766 | 522.6443 | min | 6800 | 5.15 | 1320.3883 | 0 | 6333.3333 | 5.0333 | 1258.2781 | 0 | 5866.6667 | 4.9167 | 1193.2203 | 0 | 5400 | 4.75 | 1136.8421 | 0 | 5266.6667 | 4.1333 | 1274.1935 | 0 | 5133.3333 | 3.4833 | 1473.6842 | 0
| 15 |  | 5.1161 | max | 18500 | 5.35 | 3457.9439 | 5.15 | 18200 | 5 | 3640 | 5.1 | 17900 | 4.75 | 3768.4211 | 5.05 | 17700 | 4.5 | 3933.3333 | 4.95 | 16900 | 4 | 4225 | 4.35 | 16000 | 3.5 | 4571.4286 | 3.7
|  | 2314.0496 | 31.771 | nom | 14000 | 5.5 | 2545.4545 | 449.33 | 14000 | 5.25 | 2666.6667 | 453.7352 | 14000 | 5 | 2800 | 458.2276 | 14000 | 4.75 | 2947.3684 | 467.4848 | 14000 | 4.3 | 3255.814 | 531.9654 | 14000 | 3.85 | 3636.3636 | 625.4188
|  | 6.9492 | 35.2673 | mid | 11200 | 6 | 1866.6667 | 0 | 11200 | 5.65 | 1982.3009 | 0 | 11200 | 5.45 | 2055.0459 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.65 | 2408.6022 | 0 | 11200 | 4.05 | 2765.4321 | 0
|  | 2314.0977 | 452.3128 | min | 6900 | 5.15 | 1339.8058 | 0 | 6400 | 5.1 | 1254.902 | 0 | 5900 | 5.05 | 1168.3168 | 0 | 5400 | 4.95 | 1090.9091 | 0 | 5300 | 4.35 | 1218.3908 | 0 | 5200 | 3.7 | 1405.4054 | 0
| 16 |  | 6.1951 | max | 19020 | 5.73 | 3319.3717 | 6.92 | 18720 | 5.3 | 3532.0755 | 5.68 | 18420 | 4.95 | 3721.2121 | 5.37 | 18200 | 4.59 | 3965.1416 | 5.02 | 17380 | 4.08 | 4259.8039 | 4.36 | 16460 | 3.56 | 4623.5955 | 3.65
|  | 1983.4711 | 30.8461 | nom | 14000 | 5.93 | 2360.8769 | 286.6288 | 14000 | 5.57 | 2513.465 | 349.2027 | 14000 | 5.21 | 2687.1401 | 369.3615 | 14000 | 4.85 | 2886.5979 | 395.1138 | 14000 | 4.39 | 3189.0661 | 454.9246 | 14000 | 3.92 | 3571.4286 | 543.4167
|  | 6.013 | 29.7105 | mid | 11200 | 6.42 | 1744.5483 | 0 | 11200 | 5.99 | 1869.783 | 0 | 11200 | 5.68 | 1971.831 | 0 | 11200 | 5.36 | 2089.5522 | 0 | 11200 | 4.74 | 2362.8692 | 0 | 11200 | 4.12 | 2718.4466 | 0
|  | 2002.3135 | 323.2102 | min | 6980 | 6.92 | 1008.6705 | 0 | 6460 | 5.68 | 1137.3239 | 0 | 6000 | 5.37 | 1117.3184 | 0 | 5520 | 5.02 | 1099.6016 | 0 | 5360 | 4.36 | 1229.3578 | 0 | 5180 | 3.65 | 1419.1781 | 0
| 17 |  | 7.503 | max | 19540 | 6.11 | 3198.036 | 8.69 | 19240 | 5.6 | 3435.7143 | 6.26 | 18940 | 5.15 | 3677.6699 | 5.69 | 18700 | 4.68 | 3995.7265 | 5.09 | 17860 | 4.16 | 4293.2692 | 4.37 | 16920 | 3.62 | 4674.0331 | 3.6
|  | 1652.8926 | 29.8848 | nom | 14000 | 6.36 | 2201.2579 | 190.2063 | 14000 | 5.89 | 2376.91 | 264.0403 | 14000 | 5.42 | 2583.0258 | 290.4908 | 14000 | 4.95 | 2828.2828 | 324.7333 | 14000 | 4.48 | 3125 | 378.2363 | 14000 | 3.99 | 3508.7719 | 459.1368
|  | 5.0983 | 24.3208 | mid | 11200 | 6.84 | 1637.4269 | 0 | 11200 | 6.33 | 1769.3523 | 0 | 11200 | 5.91 | 1895.0931 | 0 | 11200 | 5.47 | 2047.532 | 0 | 11200 | 4.83 | 2318.8406 | 0 | 11200 | 4.19 | 2673.031 | 0
|  | 1697.723 | 226.273 | min | 7060 | 8.69 | 812.4281 | 0 | 6520 | 6.26 | 1041.5335 | 0 | 6100 | 5.69 | 1072.0562 | 0 | 5640 | 5.09 | 1108.055 | 0 | 5420 | 4.37 | 1240.2746 | 0 | 5160 | 3.6 | 1433.3333 | 0
| 18 |  | 9.0562 | max | 20060 | 6.49 | 3090.9091 | 10.46 | 19760 | 5.9 | 3349.1525 | 6.84 | 19460 | 5.35 | 3637.3832 | 6.01 | 19200 | 4.77 | 4025.1572 | 5.16 | 18340 | 4.24 | 4325.4717 | 4.38 | 17380 | 3.68 | 4722.8261 | 3.55
|  | 1322.314 | 28.8778 | nom | 14000 | 6.79 | 2061.8557 | 126.4163 | 14000 | 6.21 | 2254.4283 | 193.3208 | 14000 | 5.63 | 2486.6785 | 220.019 | 14000 | 5.05 | 2772.2772 | 256.2624 | 14000 | 4.57 | 3063.4573 | 301.8982 | 14000 | 4.06 | 3448.2759 | 372.4828
|  | 4.1436 | 19.1007 | mid | 11200 | 7.26 | 1542.6997 | 0 | 11200 | 6.67 | 1679.1604 | 0 | 11200 | 6.14 | 1824.1042 | 0 | 11200 | 5.58 | 2007.1685 | 0 | 11200 | 4.92 | 2276.4228 | 0 | 11200 | 4.26 | 2629.108 | 0
|  | 1379.8125 | 152.3604 | min | 7140 | 10.46 | 682.6004 | 0 | 6580 | 6.84 | 961.9883 | 0 | 6200 | 6.01 | 1031.614 | 0 | 5760 | 5.16 | 1116.2791 | 0 | 5480 | 4.38 | 1251.1416 | 0 | 5140 | 3.55 | 1447.8873 | 0
| 19 |  | 10.8783 | max | 20580 | 6.87 | 2995.6332 | 12.23 | 20280 | 6.2 | 3270.9677 | 7.42 | 19980 | 5.55 | 3600 | 6.33 | 19700 | 4.86 | 4053.4979 | 5.23 | 18820 | 4.32 | 4356.4815 | 4.39 | 17840 | 3.74 | 4770.0535 | 3.5
|  | 991.7355 | 27.8102 | nom | 14000 | 7.22 | 1939.0582 | 81.0904 | 14000 | 6.53 | 2143.951 | 133.6571 | 14000 | 5.84 | 2397.2603 | 156.6723 | 14000 | 5.15 | 2718.4466 | 189.6244 | 14000 | 4.66 | 3004.2918 | 225.9079 | 14000 | 4.13 | 3389.8305 | 283.353
|  | 3.1316 | 14.0532 | mid | 11200 | 7.68 | 1458.3333 | 0 | 11200 | 7.01 | 1597.7175 | 0 | 11200 | 6.37 | 1758.2418 | 0 | 11200 | 5.69 | 1968.3656 | 0 | 11200 | 5.01 | 2235.5289 | 0 | 11200 | 4.33 | 2586.6051 | 0
|  | 1042.8224 | 95.8626 | min | 7220 | 12.23 | 590.3516 | 0 | 6640 | 7.42 | 894.8787 | 0 | 6300 | 6.33 | 995.2607 | 0 | 5880 | 5.23 | 1124.283 | 0 | 5540 | 4.39 | 1261.959 | 0 | 5120 | 3.5 | 1462.8571 | 0
| 20 |  | 13.0068 | max | 21100 | 7.25 | 2910.3448 | 14 | 20800 | 6.5 | 3200 | 8 | 20500 | 5.75 | 3565.2174 | 6.65 | 20200 | 4.95 | 4080.8081 | 5.3 | 19300 | 4.4 | 4386.3636 | 4.4 | 18300 | 3.8 | 4815.7895 | 3.45
|  | 661.157 | 26.6553 | nom | 14000 | 7.65 | 1830.0654 | 47.2255 | 14000 | 6.85 | 2043.7956 | 82.6446 | 14000 | 6.05 | 2314.0496 | 99.4221 | 14000 | 5.25 | 2666.6667 | 124.7466 | 14000 | 4.75 | 2947.3684 | 150.263 | 14000 | 4.2 | 3333.3333 | 191.6397
|  | 2.0736 | 9.1819 | mid | 11200 | 8.1 | 1382.716 | 0 | 11200 | 7.35 | 1523.8095 | 0 | 11200 | 6.6 | 1696.9697 | 0 | 11200 | 5.8 | 1931.0345 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.4 | 2545.4545 | 0
|  | 690.5118 | 53.0885 | min | 7300 | 14 | 521.4286 | 0 | 6700 | 8 | 837.5 | 0 | 6400 | 6.65 | 962.406 | 0 | 6000 | 5.3 | 1132.0755 | 0 | 5600 | 4.4 | 1272.7273 | 0 | 5100 | 3.45 | 1478.2609 | 0
Indoor Temp. |  | 23
LWT |  |  | 25 CAP: 25; 35 CAP: 35; 40 CAP: 40; 45 CAP: 45; 50 CAP: 50; 55 CAP: 55
Outdoor air temperature[℃] |  | Heating Demand | COP | CL | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP
|  |  | LWT |  |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI
| -10 |  | 2.033 | max | 14600 | 2.4 | 6083.3333 | 2.8325 | 14400 | 2.25 | 6400 | 2.678 | 14200 | 2.1 | 6761.9048 | 2.524 | 14000 | 1.9 | 7368.4211 | 2.3204 | 14000 | 1.85 | 7567.5676 | 2.0713 | 14000 | 1.75 | 8000 | 1.8197
|  | 10909.0909 | 50.7626 | nom | 14000 | 2.8 | 5000 | 3851.3383 | 14000 | 2.5 | 5600 | 4073.5285 | 14000 | 2.2 | 6363.6364 | 4322.0993 | 14000 | 1.9 | 7368.4211 | 4701.3513 | 14000 | 1.85 | 7567.5676 | 5266.6578 | 14000 | 1.75 | 8000 | 5995.0042
|  | 32.8312 | 100 | mid | 11200 | 2.85 | 3929.8246 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.1 | 5333.3333 | 1 | 11200 | 1.85 | 6054.0541 | 1
|  | 10932.7837 | 5377.7513 | min | 6200 | 2.55 | 2431.3725 | 0.94182 | 5900 | 2.3 | 2565.2174 | 0.94511 | 5600 | 2.05 | 2731.7073 | 0.94805 | 5300 | 1.75 | 3028.5714 | 0.95069 | 4600 | 1.45 | 3172.4138 | 0.95592 | 4000 | 1.1 | 3636.3636 | 0.9596
| -9 |  | 2.098 | max | 15100 | 2.5 | 6040 | 2.9756 | 14900 | 2.3333 | 6385.7143 | 2.7459 | 14700 | 2.1667 | 6784.6154 | 2.5592 | 14500 | 1.9667 | 7372.8814 | 2.3395 | 14233.3333 | 1.9167 | 7426.087 | 2.1039 | 14000 | 1.8167 | 7706.422 | 1.8657
|  | 10578.5124 | 50.1249 | nom | 14000 | 2.8833 | 4855.4913 | 3555.07 | 14000 | 2.6 | 5384.6154 | 3852.5011 | 14000 | 2.3167 | 6043.1655 | 4133.4478 | 14000 | 2.0333 | 6885.2459 | 4521.7236 | 14000 | 1.95 | 7179.4872 | 5028.0005 | 14000 | 1.8167 | 7706.422 | 5670.1173
|  | 31.7785 | 100 | mid | 11200 | 2.9833 | 3754.1899 | 1 | 11200 | 2.8 | 4000 | 1 | 11200 | 2.6167 | 4280.2548 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.1667 | 5169.2308 | 1 | 11200 | 1.9333 | 5793.1034 | 1
|  | 10582.2386 | 5044.0405 | min | 5833.3333 | 2.9167 | 2000 | 0.88419 | 5266.6667 | 2.2833 | 2306.5693 | 0.89525 | 5066.6667 | 2.05 | 2471.5447 | 0.89867 | 4866.6667 | 1.7833 | 2728.972 | 0.90187 | 4266.6667 | 1.4667 | 2909.0909 | 0.91036 | 3700 | 1.1167 | 3313.4328 | 0.91713
| -8 |  | 2.1584 | max | 15600 | 2.6 | 6000 | 3.1443 | 15400 | 2.4167 | 6372.4138 | 2.8082 | 15200 | 2.2333 | 6805.9701 | 2.5929 | 15000 | 2.0333 | 7377.0492 | 2.3609 | 14466.6667 | 1.9833 | 7294.1176 | 2.1351 | 14000 | 1.8833 | 7433.6283 | 1.9088
|  | 10247.9339 | 49.4825 | nom | 14000 | 2.9667 | 4719.1011 | 3259.1654 | 14000 | 2.7 | 5185.1852 | 3649.3199 | 14000 | 2.4333 | 5753.4247 | 3952.3256 | 14000 | 2.1667 | 6461.5385 | 4340.7072 | 14000 | 2.05 | 6829.2683 | 4799.8125 | 14000 | 1.8833 | 7433.6283 | 5368.6507
|  | 30.8035 | 100 | mid | 11200 | 3.1167 | 3593.5829 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.6833 | 4173.913 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.2333 | 5014.9254 | 1 | 11200 | 2.0167 | 5553.719 | 1
|  | 10257.553 | 4752.2987 | min | 5466.6667 | 3.2833 | 1664.9746 | 0.83394 | 4633.3333 | 2.2667 | 2044.1176 | 0.85502 | 4533.3333 | 2.05 | 2211.3821 | 0.85719 | 4433.3333 | 1.8167 | 2440.367 | 0.8593 | 3933.3333 | 1.4833 | 2651.6854 | 0.86898 | 3400 | 1.1333 | 3000 | 0.87794
| -7 |  | 2.216 | max | 16100 | 2.7 | 5962.963 | 3.3341 | 15900 | 2.5 | 6360 | 2.8664 | 15700 | 2.3 | 6826.087 | 2.6253 | 15500 | 2.1 | 7380.9524 | 2.3842 | 14700 | 2.05 | 7170.7317 | 2.165 | 14000 | 1.95 | 7179.4872 | 1.9496
|  | 9917.3554 | 48.8354 | nom | 14000 | 3.05 | 4590.1639 | 2974.5155 | 14000 | 2.8 | 5000 | 3459.8751 | 14000 | 2.55 | 5490.1961 | 3777.6107 | 14000 | 2.3 | 6086.9565 | 4159.6056 | 14000 | 2.15 | 6511.6279 | 4580.7968 | 14000 | 1.95 | 7179.4872 | 5086.9545
|  | 29.8314 | 100 | mid | 11200 | 3.25 | 3446.1538 | 1 | 11200 | 3 | 3733.3333 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1 | 11200 | 2.1 | 5333.3333 | 1
|  | 9933.8527 | 4482.6912 | min | 5100 | 3.65 | 1397.2603 | 0.78973 | 4000 | 2.25 | 1777.7778 | 0.82185 | 4000 | 2.05 | 1951.2195 | 0.82185 | 4000 | 1.85 | 2162.1622 | 0.82185 | 3600 | 1.5 | 2400 | 0.83123 | 3100 | 1.15 | 2695.6522 | 0.84165
| -6 |  | 2.2631 | max | 16144.4444 | 2.7611 | 5847.0825 | 3.4057 | 15944.4444 | 2.5556 | 6239.1304 | 2.8988 | 15733.3333 | 2.35 | 6695.0355 | 2.6522 | 15533.3333 | 2.1444 | 7243.5233 | 2.4046 | 14744.4444 | 2.0944 | 7039.7878 | 2.1823 | 14033.3333 | 1.9944 | 7036.2117 | 1.9594
|  | 9586.7769 | 48.1832 | nom | 14000 | 3.0889 | 4532.3741 | 2814.9624 | 14000 | 2.8389 | 4931.5068 | 3307.1264 | 14000 | 2.5889 | 5407.7253 | 3614.5837 | 14000 | 2.3389 | 5985.7482 | 3986.8514 | 14000 | 2.1944 | 6379.7468 | 4392.9685 | 14000 | 2 | 7000 | 4892.6432
|  | 28.8518 | 100 | mid | 11200 | 3.2944 | 3399.6627 | 1 | 11200 | 3.0444 | 3678.8321 | 1 | 11200 | 2.7944 | 4007.9523 | 1 | 11200 | 2.5444 | 4401.7467 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.15 | 5209.3023 | 1
|  | 9607.661 | 4245.4035 | min | 5155.5556 | 3.7111 | 1389.2216 | 0.73311 | 4122.2222 | 2.4056 | 1713.6259 | 0.77207 | 4077.7778 | 2.1667 | 1882.0513 | 0.77349 | 4022.2222 | 1.9222 | 2092.4855 | 0.77525 | 3611.1111 | 1.5611 | 2313.1673 | 0.78742 | 3111.1111 | 1.1944 | 2604.6512 | 0.80056
| -5 |  | 2.3128 | max | 16188.8889 | 2.8222 | 5736.2205 | 3.4795 | 15988.8889 | 2.6111 | 6123.4043 | 2.9414 | 15766.6667 | 2.4 | 6569.4444 | 2.6856 | 15566.6667 | 2.1889 | 7111.6751 | 2.4274 | 14788.8889 | 2.1389 | 6914.2857 | 2.2005 | 14066.6667 | 2.0389 | 6899.1826 | 1.9687
|  | 9256.1983 | 47.5259 | nom | 14000 | 3.1278 | 4476.0213 | 2660.1826 | 14000 | 2.8778 | 4864.8649 | 3146.8726 | 14000 | 2.6278 | 5327.6956 | 3446.6135 | 14000 | 2.3778 | 5887.8505 | 3813.2018 | 14000 | 2.2389 | 6253.1017 | 4206.4268 | 14000 | 2.05 | 6829.2683 | 4701.6271
|  | 27.8634 | 100 | mid | 11200 | 3.3389 | 3354.4093 | 1 | 11200 | 3.0889 | 3625.8993 | 1 | 11200 | 2.8389 | 3945.2055 | 1 | 11200 | 2.5889 | 4326.1803 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.2 | 5090.9091 | 1
|  | 9278.5035 | 4011.8474 | min | 5211.1111 | 3.7722 | 1381.4433 | 0.67543 | 4244.4444 | 2.5611 | 1657.2668 | 0.72054 | 4155.5556 | 2.2833 | 1819.9513 | 0.72407 | 4044.4444 | 1.9944 | 2027.8552 | 0.72835 | 3622.2222 | 1.6222 | 2232.8767 | 0.74349 | 3122.2222 | 1.2389 | 2520.1794 | 0.75936
| -4 |  | 2.3658 | max | 16233.3333 | 2.8833 | 5630.0578 | 3.5558 | 16033.3333 | 2.6667 | 6012.5 | 2.9947 | 15800 | 2.45 | 6448.9796 | 2.7255 | 15600 | 2.2333 | 6985.0746 | 2.4527 | 14833.3333 | 2.1833 | 6793.8931 | 2.2196 | 14100 | 2.0833 | 6768 | 1.9775
|  | 8925.6198 | 46.863 | nom | 14000 | 3.1667 | 4421.0526 | 2510.1379 | 14000 | 2.9167 | 4800 | 2980.5203 | 14000 | 2.6667 | 5250 | 3274.8062 | 14000 | 2.4167 | 5793.1034 | 3639.1616 | 14000 | 2.2833 | 6131.3869 | 4021.3534 | 14000 | 2.1 | 6666.6667 | 4513.7012
|  | 26.8662 | 100 | mid | 11200 | 3.3833 | 3310.3448 | 1 | 11200 | 3.1333 | 3574.4681 | 1 | 11200 | 2.8833 | 3884.3931 | 1 | 11200 | 2.6333 | 4253.1646 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.25 | 4977.7778 | 1
|  | 8946.4464 | 3781.5693 | min | 5266.6667 | 3.8333 | 1373.913 | 0.61668 | 4366.6667 | 2.7167 | 1607.362 | 0.66716 | 4233.3333 | 2.4 | 1763.8889 | 0.67353 | 4066.6667 | 2.0667 | 1967.7419 | 0.68116 | 3633.3333 | 1.6833 | 2158.4158 | 0.69942 | 3133.3333 | 1.2833 | 2441.5584 | 0.71805
| -3 |  | 2.4228 | max | 16277.7778 | 2.9444 | 5528.3019 | 3.6346 | 16077.7778 | 2.7222 | 5906.1224 | 3.0592 | 15833.3333 | 2.5 | 6333.3333 | 2.7723 | 15633.3333 | 2.2778 | 6863.4146 | 2.4804 | 14877.7778 | 2.2278 | 6678.3042 | 2.2395 | 14133.3333 | 2.1278 | 6642.2977 | 1.9856
|  | 8595.0413 | 46.1945 | nom | 14000 | 3.2056 | 4367.4177 | 2364.7841 | 14000 | 2.9556 | 4736.8421 | 2809.595 | 14000 | 2.7056 | 5174.538 | 3100.3057 | 14000 | 2.4556 | 5701.3575 | 3465.2244 | 14000 | 2.3278 | 6014.3198 | 3837.9216 | 14000 | 2.15 | 6511.6279 | 4328.6688
|  | 25.86 | 100 | mid | 11200 | 3.4278 | 3267.423 | 1 | 11200 | 3.1778 | 3524.4755 | 1 | 11200 | 2.9278 | 3825.4269 | 1 | 11200 | 2.6778 | 4182.5726 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1
|  | 8611.3643 | 3554.2646 | min | 5322.2222 | 3.8944 | 1366.6191 | 0.55681 | 4488.8889 | 2.8722 | 1562.8627 | 0.61184 | 4311.1111 | 2.5167 | 1713.0243 | 0.62186 | 4088.8889 | 2.1389 | 1911.6883 | 0.63368 | 3644.4444 | 1.7444 | 2089.172 | 0.65523 | 3144.4444 | 1.3278 | 2368.2008 | 0.67663
| -2 |  | 2.4845 | max | 16322.2222 | 3.0056 | 5430.6839 | 3.7159 | 16122.2222 | 2.7778 | 5804 | 3.1356 | 15866.6667 | 2.55 | 6222.2222 | 2.8262 | 15666.6667 | 2.3222 | 6746.4115 | 2.5106 | 14922.2222 | 2.2722 | 6567.2372 | 2.2603 | 14166.6667 | 2.1722 | 6521.7391 | 1.9932
|  | 8264.4628 | 45.5201 | nom | 14000 | 3.2444 | 4315.0685 | 2224.0711 | 14000 | 2.9944 | 4675.3247 | 2635.6948 | 14000 | 2.7444 | 5101.2146 | 2924.269 | 14000 | 2.4944 | 5612.4722 | 3291.8683 | 14000 | 2.3722 | 5901.6393 | 3656.2963 | 14000 | 2.2 | 6363.6364 | 4146.3406
|  | 24.8437 | 100 | mid | 11200 | 3.4722 | 3225.6 | 1 | 11200 | 3.2222 | 3475.8621 | 1 | 11200 | 2.9722 | 3768.2243 | 1 | 11200 | 2.7222 | 4114.2857 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1
|  | 8272.9615 | 3329.7742 | min | 5377.7778 | 3.9556 | 1359.5506 | 0.4958 | 4611.1111 | 3.0278 | 1522.9358 | 0.55447 | 4388.8889 | 2.6333 | 1666.6667 | 0.56901 | 4111.1111 | 2.2111 | 1859.2965 | 0.5859 | 3655.5556 | 1.8056 | 2024.6154 | 0.6109 | 3155.5556 | 1.3722 | 2299.5951 | 0.63509
| -1 |  | 2.5543 | max | 16366.6667 | 3.0667 | 5336.9565 | 3.7999 | 16166.6667 | 2.8333 | 5705.8824 | 3.2246 | 15900 | 2.6 | 6115.3846 | 2.8873 | 15700 | 2.3667 | 6633.8028 | 2.5433 | 14966.6667 | 2.3167 | 6460.4317 | 2.2821 | 14200 | 2.2167 | 6406.015 | 2.0002
|  | 7933.8843 | 44.8394 | nom | 14000 | 3.2833 | 4263.9594 | 2087.9435 | 14000 | 3.0333 | 4615.3846 | 2460.4415 | 14000 | 2.7833 | 5029.9401 | 2747.8411 | 14000 | 2.5333 | 5526.3158 | 3119.5522 | 14000 | 2.4167 | 5793.1034 | 3476.6334 | 14000 | 2.25 | 6222.2222 | 3966.5341
|  | 23.8374 | 100 | mid | 11200 | 3.5167 | 3184.8341 | 1 | 11200 | 3.2667 | 3428.5714 | 1 | 11200 | 3.0167 | 3712.7072 | 1 | 11200 | 2.7667 | 4048.1928 | 1 | 11200 | 2.6 | 4307.6923 | 1 | 11200 | 2.4 | 4666.6667 | 1
|  | 7937.8611 | 3107.6093 | min | 5433.3333 | 4.0167 | 1352.6971 | 0.43362 | 4733.3333 | 3.1833 | 1486.911 | 0.49493 | 4466.6667 | 2.75 | 1624.2424 | 0.51493 | 4133.3333 | 2.2833 | 1810.219 | 0.53781 | 3666.6667 | 1.8667 | 1964.2857 | 0.56644 | 3166.6667 | 1.4167 | 2235.2941 | 0.59343
| 0 |  | 2.6425 | max | 16411.1111 | 3.1278 | 5246.8917 | 3.8865 | 16211.1111 | 2.8889 | 5611.5385 | 3.3269 | 15933.3333 | 2.65 | 6012.5786 | 2.956 | 15733.3333 | 2.4111 | 6525.3456 | 2.5785 | 15011.1111 | 2.3611 | 6357.6471 | 2.3047 | 14233.3333 | 2.2611 | 6294.8403 | 2.0066
|  | 7603.3058 | 44.1521 | nom | 14000 | 3.3222 | 4214.0468 | 1956.3411 | 14000 | 3.0722 | 4556.962 | 2285.4311 | 14000 | 2.8222 | 4960.6299 | 2572.1321 | 14000 | 2.5722 | 5442.7646 | 2948.7123 | 14000 | 2.4611 | 5688.4876 | 3299.0796 | 14000 | 2.3 | 6086.9565 | 3789.0728
|  | 22.8929 | 100 | mid | 11200 | 3.5611 | 3145.0858 | 1 | 11200 | 3.3111 | 3382.5503 | 1 | 11200 | 3.0611 | 3658.8022 | 1 | 11200 | 2.8111 | 3984.1897 | 1 | 11200 | 2.65 | 4226.4151 | 1 | 11200 | 2.45 | 4571.4286 | 1
|  | 7623.3267 | 2884.8484 | min | 5488.8889 | 4.0778 | 1346.049 | 0.37023 | 4855.5556 | 3.3389 | 1454.2429 | 0.4331 | 4544.4444 | 2.8667 | 1585.2713 | 0.4596 | 4155.5556 | 2.3556 | 1764.1509 | 0.48943 | 3677.7778 | 1.9278 | 1907.781 | 0.52186 | 3177.7778 | 1.4611 | 2174.9049 | 0.55166
| 1 |  | 2.7447 | max | 16455.5556 | 3.1889 | 5160.2787 | 3.9759 | 16255.5556 | 2.9444 | 5520.7547 | 3.4432 | 15966.6667 | 2.7 | 5913.5802 | 3.0326 | 15766.6667 | 2.4556 | 6420.8145 | 2.6163 | 15055.5556 | 2.4056 | 6258.6605 | 2.3282 | 14266.6667 | 2.3056 | 6187.9518 | 2.0125
|  | 7272.7273 | 43.4578 | nom | 14000 | 3.3611 | 4165.2893 | 1829.1994 | 14000 | 3.1111 | 4500 | 2112.1891 | 14000 | 2.8611 | 4893.2039 | 2398.196 | 14000 | 2.6111 | 5361.7021 | 2779.7598 | 14000 | 2.5056 | 5587.5831 | 3123.7726 | 14000 | 2.35 | 5957.4468 | 3613.786
|  | 21.9418 | 100 | mid | 11200 | 3.6056 | 3106.3174 | 1 | 11200 | 3.3556 | 3337.7483 | 1 | 11200 | 3.1056 | 3606.4401 | 1 | 11200 | 2.8556 | 3922.179 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.5 | 4480 | 1
|  | 7306.6068 | 2662.0718 | min | 5544.4444 | 4.1389 | 1339.5973 | 0.30559 | 4977.7778 | 3.4944 | 1424.4833 | 0.36883 | 4622.2222 | 2.9833 | 1549.3482 | 0.40295 | 4177.7778 | 2.4278 | 1720.8238 | 0.44074 | 3688.8889 | 1.9889 | 1854.7486 | 0.47714 | 3188.8889 | 1.5056 | 2118.0812 | 0.50977
14kW-Maximum heating CAP | 2 |  | 2.8634 | max | 16500 | 3.25 | 5076.9231 | 4.0682 | 16300 | 3 | 5433.3333 | 3.5745 | 16000 | 2.75 | 5818.1818 | 3.1172 | 15800 | 2.5 | 6320 | 2.6567 | 15100 | 2.45 | 6163.2653 | 2.3526 | 14300 | 2.35 | 6085.1064 | 2.0178
|  | 6942.1488 | 42.7563 | nom | 14000 | 3.4 | 4117.6471 | 1706.45 | 14000 | 3.15 | 4444.4444 | 1942.1303 | 14000 | 2.9 | 4827.5862 | 2227.0125 | 14000 | 2.65 | 5283.0189 | 2613.0778 | 14000 | 2.55 | 5490.1961 | 2950.8404 | 14000 | 2.4 | 5833.3333 | 3440.5079
|  | 20.9794 | 100 | mid | 11200 | 3.65 | 3068.4932 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 3.15 | 3555.5556 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.55 | 4392.1569 | 1
|  | 6986.1326 | 2439.8322 | min | 5600 | 4.2 | 1333.3333 | 0.23967 | 5100 | 3.65 | 1397.2603 | 0.30199 | 4700 | 3.1 | 1516.129 | 0.34495 | 4200 | 2.5 | 1680 | 0.39174 | 3700 | 2.05 | 1804.878 | 0.43229 | 3200 | 1.55 | 2064.5161 | 0.46777
| 3 |  | 3.0309 | max | 16560 | 3.54 | 4677.9661 | 4.5298 | 16360 | 3.25 | 5033.8462 | 3.775 | 16080 | 2.96 | 5432.4324 | 3.2462 | 15860 | 2.66 | 5962.406 | 2.7204 | 15160 | 2.54 | 5968.5039 | 2.3794 | 14360 | 2.38 | 6033.6134 | 2.0101
|  | 6611.5702 | 42.047 | nom | 14000 | 3.7 | 3783.7838 | 1459.5861 | 14000 | 3.41 | 4105.5718 | 1751.417 | 14000 | 3.12 | 4487.1795 | 2036.721 | 14000 | 2.82 | 4964.539 | 2430.388 | 14000 | 2.67 | 5243.4457 | 2778.6198 | 14000 | 2.47 | 5668.0162 | 3289.2164
|  | 20.0049 | 100 | mid | 11200 | 3.97 | 2821.1587 | 1 | 11200 | 3.68 | 3043.4783 | 1 | 11200 | 3.39 | 3303.8348 | 1 | 11200 | 3.09 | 3624.5955 | 1 | 11200 | 2.88 | 3888.8889 | 1 | 11200 | 2.62 | 4274.8092 | 1
|  | 6661.619 | 2197.8847 | min | 5380 | 4.68 | 1149.5726 | 0.21161 | 4920 | 3.81 | 1291.3386 | 0.26936 | 4500 | 3.18 | 1415.0943 | 0.31516 | 4000 | 2.51 | 1593.6255 | 0.36272 | 3500 | 2.04 | 1715.6863 | 0.4041 | 3000 | 1.53 | 1960.7843 | 0.44044
| 4 |  | 3.209 | max | 16620 | 3.83 | 4339.4256 | 4.9985 | 16420 | 3.5 | 4691.4286 | 3.9676 | 16160 | 3.17 | 5097.7918 | 3.3662 | 15920 | 2.82 | 5645.3901 | 2.7748 | 15220 | 2.63 | 5787.0722 | 2.3998 | 14420 | 2.41 | 5983.4025 | 1.999
|  | 6280.9917 | 41.3294 | nom | 14000 | 4 | 3500 | 1256.5671 | 14000 | 3.67 | 3814.7139 | 1583.065 | 14000 | 3.34 | 4191.6168 | 1865.8847 | 14000 | 2.99 | 4682.2742 | 2263.5799 | 14000 | 2.79 | 5017.9211 | 2617.3046 | 14000 | 2.54 | 5511.811 | 3142.0725
|  | 18.9997 | 100 | mid | 11200 | 4.29 | 2610.7226 | 1 | 11200 | 3.96 | 2828.2828 | 1 | 11200 | 3.63 | 3085.3994 | 1 | 11200 | 3.28 | 3414.6341 | 1 | 11200 | 3.01 | 3720.9302 | 1 | 11200 | 2.69 | 4163.5688 | 1
|  | 6326.9012 | 1971.6245 | min | 5160 | 5.16 | 1000 | 0.18559 | 4740 | 3.97 | 1193.9547 | 0.23854 | 4300 | 3.26 | 1319.0184 | 0.2871 | 3800 | 2.52 | 1507.9365 | 0.33527 | 3300 | 2.03 | 1625.6158 | 0.37734 | 2800 | 1.51 | 1854.3046 | 0.4144
| 5 |  | 3.3988 | max | 16680 | 4.12 | 4048.5437 | 5.4737 | 16480 | 3.75 | 4394.6667 | 4.153 | 16240 | 3.38 | 4804.7337 | 3.4781 | 15980 | 2.98 | 5362.4161 | 2.8207 | 15280 | 2.72 | 5617.6471 | 2.4141 | 14480 | 2.44 | 5934.4262 | 1.9848
|  | 5950.4132 | 40.6031 | nom | 14000 | 4.3 | 3255.814 | 1087.0817 | 14000 | 3.93 | 3562.341 | 1432.787 | 14000 | 3.56 | 3932.5843 | 1710.8084 | 14000 | 3.16 | 4430.3797 | 2109.5452 | 14000 | 2.91 | 4810.9966 | 2464.8259 | 14000 | 2.61 | 5363.9847 | 2998.0362
|  | 17.9526 | 100 | mid | 11200 | 4.61 | 2429.5011 | 1 | 11200 | 4.24 | 2641.5094 | 1 | 11200 | 3.87 | 2894.0568 | 1 | 11200 | 3.47 | 3227.6657 | 1 | 11200 | 3.14 | 3566.879 | 1 | 11200 | 2.76 | 4057.971 | 1
|  | 5978.2179 | 1758.9031 | min | 4940 | 5.64 | 875.8865 | 0.16141 | 4560 | 4.13 | 1104.1162 | 0.2094 | 4100 | 3.34 | 1227.5449 | 0.26062 | 3600 | 2.53 | 1422.9249 | 0.30926 | 3100 | 2.02 | 1534.6535 | 0.3519 | 2600 | 1.49 | 1744.9664 | 0.38958
| 6 |  | 3.6024 | max | 16740 | 4.41 | 3795.9184 | 5.9548 | 16540 | 4 | 4135 | 4.3318 | 16320 | 3.59 | 4545.961 | 3.5826 | 16040 | 3.14 | 5108.2803 | 2.8587 | 15340 | 2.81 | 5459.0747 | 2.4229 | 14540 | 2.47 | 5886.6397 | 1.9676
|  | 5619.8347 | 39.8674 | nom | 14000 | 4.6 | 3043.4783 | 943.7562 | 14000 | 4.19 | 3341.2888 | 1297.3402 | 14000 | 3.78 | 3703.7037 | 1568.6646 | 14000 | 3.33 | 4204.2042 | 1965.8395 | 14000 | 3.03 | 4620.462 | 2319.4752 | 14000 | 2.68 | 5223.8806 | 2856.1719
|  | 16.8921 | 100 | mid | 11200 | 4.93 | 2271.8053 | 1 | 11200 | 4.52 | 2477.8761 | 1 | 11200 | 4.11 | 2725.0608 | 1 | 11200 | 3.66 | 3060.1093 | 1 | 11200 | 3.27 | 3425.0765 | 1 | 11200 | 2.83 | 3957.5972 | 1
|  | 5625.0833 | 1561.4686 | min | 4720 | 6.12 | 771.2418 | 0.13886 | 4380 | 4.29 | 1020.979 | 0.18179 | 3900 | 3.42 | 1140.3509 | 0.23559 | 3400 | 2.54 | 1338.5827 | 0.28459 | 2900 | 2.01 | 1442.7861 | 0.32769 | 2400 | 1.47 | 1632.6531 | 0.36589
| 7 |  | 3.8249 | max | 16800 | 4.7 | 3574.4681 | 6.441 | 16600 | 4.25 | 3905.8824 | 4.5045 | 16400 | 3.8 | 4315.7895 | 3.6801 | 16100 | 3.3 | 4878.7879 | 2.8895 | 15400 | 2.9 | 5310.3448 | 2.4265 | 14600 | 2.5 | 5840 | 1.9477
|  | 5289.2562 | 39.1216 | nom | 14000 | 4.9 | 2857.1429 | 821.1893 | 14000 | 4.45 | 3146.0674 | 1174.2257 | 14000 | 4 | 3500 | 1437.2527 | 14000 | 3.5 | 4000 | 1830.5065 | 14000 | 3.15 | 4444.4444 | 2179.819 | 14000 | 2.75 | 5090.9091 | 2715.6233
|  | 15.9779 | 100 | mid | 11200 | 5.25 | 2133.3333 | 1 | 11200 | 4.8 | 2333.3333 | 1 | 11200 | 4.35 | 2574.7126 | 1 | 11200 | 3.85 | 2909.0909 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 2.9 | 3862.069 | 1
|  | 5320.6552 | 1391.0459 | min | 4500 | 6.6 | 681.8182 | 0.1178 | 4200 | 4.45 | 943.8202 | 0.15561 | 3700 | 3.5 | 1057.1429 | 0.2119 | 3200 | 2.55 | 1254.902 | 0.26116 | 2700 | 2 | 1350 | 0.30462 | 2200 | 1.45 | 1517.2414 | 0.34325
| 8 |  | 4.0659 | max | 16860 | 4.81 | 3505.1975 | 6.3042 | 16640 | 4.38 | 3799.0868 | 4.5623 | 16440 | 3.93 | 4183.2061 | 3.8248 | 16160 | 3.48 | 4643.6782 | 3.1106 | 15440 | 3.06 | 5045.7516 | 2.6126 | 14640 | 2.64 | 5545.4545 | 2.1061
|  | 4958.6777 | 38.365 | nom | 14000 | 5.02 | 2788.8446 | 786.566 | 14000 | 4.59 | 3050.1089 | 1086.8855 | 14000 | 4.16 | 3365.3846 | 1296.4657 | 14000 | 3.69 | 3794.0379 | 1594.1264 | 14000 | 3.32 | 4216.8675 | 1897.9894 | 14000 | 2.9 | 4827.5862 | 2354.4876
|  | 14.9931 | 100 | mid | 11200 | 5.37 | 2085.6611 | 1 | 11200 | 4.95 | 2262.6263 | 1 | 11200 | 4.53 | 2472.4062 | 1 | 11200 | 4.06 | 2758.6207 | 1 | 11200 | 3.58 | 3128.4916 | 1 | 11200 | 3.06 | 3660.1307 | 1
|  | 4992.6934 | 1227.9344 | min | 4920 | 6.31 | 779.7147 | 0.0061589 | 4600 | 4.54 | 1013.2159 | 0.054345 | 4120 | 3.73 | 1104.5576 | 0.11846 | 3640 | 2.91 | 1250.8591 | 0.17443 | 3200 | 2.34 | 1367.5214 | 0.21983 | 2760 | 1.77 | 1559.322 | 0.26051
| 9 |  | 4.2872 | max | 16920 | 4.92 | 3439.0244 | 6.02 | 16680 | 4.51 | 3698.4479 | 4.63 | 16480 | 4.06 | 4059.1133 | 3.9699 | 16220 | 3.66 | 4431.694 | 3.347 | 15480 | 3.22 | 4807.4534 | 2.8136 | 14680 | 2.78 | 5280.5755 | 2.78
|  | 4628.0992 | 37.5967 | nom | 14000 | 5.14 | 2723.7354 | 768.7872 | 14000 | 4.73 | 2959.8309 | 999.5895 | 14000 | 4.32 | 3240.7407 | 1165.7912 | 14000 | 3.88 | 3608.2474 | 1382.7686 | 14000 | 3.49 | 4011.4613 | 1644.876 | 14000 | 3.05 | 4590.1639 | 1664.7839
|  | 13.9804 | 100 | mid | 11200 | 5.49 | 2040.0729 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.71 | 2377.9193 | 1 | 11200 | 4.27 | 2622.9508 | 1 | 11200 | 3.76 | 2978.7234 | 1 | 11200 | 3.22 | 3478.2609 | 4
|  | 4655.4847 | 1085.9045 | min | 5340 | 6.02 | 887.0432 | 0 | 5000 | 4.63 | 1079.9136 | 0 | 4540 | 3.96 | 1146.4646 | 0.013228 | 4080 | 3.27 | 1247.7064 | 0.07698 | 3700 | 2.68 | 1380.597 | 0.12375 | 3320 | 2.09 | 1588.5167 | 0
| 10 |  | 4.5275 | max | 16980 | 5.03 | 3375.7455 | 5.73 | 16720 | 4.64 | 3603.4483 | 4.72 | 16520 | 4.19 | 3942.7208 | 4.19 | 16280 | 3.84 | 4239.5833 | 3.63 | 15520 | 3.38 | 4591.716 | 3.0328 | 14720 | 2.92 | 5041.0959 | 2.4653
|  | 4297.5207 | 36.8156 | nom | 14000 | 5.26 | 2661.597 | 750.0036 | 14000 | 4.87 | 2874.7433 | 910.4917 | 14000 | 4.48 | 3125 | 1025.6613 | 14000 | 4.07 | 3439.8034 | 1183.89 | 14000 | 3.66 | 3825.1366 | 1417.0063 | 14000 | 3.2 | 4375 | 1743.1847
|  | 12.9479 | 82.0102 | mid | 11200 | 5.61 | 1996.4349 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.89 | 2290.3885 | 0 | 11200 | 4.48 | 2500 | 0 | 11200 | 3.94 | 2842.6396 | 1 | 11200 | 3.38 | 3313.6095 | 1
|  | 4311.6369 | 952.3114 | min | 5760 | 5.73 | 1005.2356 | 0 | 5400 | 4.72 | 1144.0678 | 0 | 4960 | 4.19 | 1183.7709 | 0 | 4520 | 3.63 | 1245.1791 | 0 | 4200 | 3.02 | 1390.7285 | 0.013932 | 3880 | 2.41 | 1609.9585 | 0.057038
| 11 |  | 4.7304 | max | 17040 | 5.14 | 3315.1751 | 5.44 | 16760 | 4.77 | 3513.6268 | 4.81 | 16560 | 4.32 | 3833.3333 | 4.42 | 16340 | 4.02 | 4064.6766 | 3.99 | 15560 | 3.54 | 4395.4802 | 3.36 | 14760 | 3.06 | 4823.5294 | 2.73
|  | 3966.9421 | 36.0204 | nom | 14000 | 5.38 | 2602.2305 | 729.2173 | 14000 | 5.01 | 2794.4112 | 824.7281 | 14000 | 4.64 | 3017.2414 | 897.4982 | 14000 | 4.26 | 3286.385 | 994.2211 | 14000 | 3.83 | 3655.3525 | 1180.6375 | 14000 | 3.35 | 4179.1045 | 1453.0924
|  | 11.9266 | 69.4215 | mid | 11200 | 5.73 | 1954.6248 | 0 | 11200 | 5.4 | 2074.0741 | 0 | 11200 | 5.07 | 2209.073 | 0 | 11200 | 4.69 | 2388.0597 | 0 | 11200 | 4.12 | 2718.4466 | 0 | 11200 | 3.54 | 3163.8418 | 0
|  | 3971.5522 | 839.5797 | min | 6180 | 5.44 | 1136.0294 | 0 | 5800 | 4.81 | 1205.8212 | 0 | 5380 | 4.42 | 1217.1946 | 0 | 4960 | 3.99 | 1243.1078 | 0 | 4700 | 3.36 | 1398.8095 | 0 | 4440 | 2.73 | 1626.3736 | 0
| 12 |  | 4.8895 | max | 17100 | 5.25 | 3257.1429 | 5.15 | 16800 | 4.9 | 3428.5714 | 4.9 | 16600 | 4.45 | 3730.3371 | 4.65 | 16400 | 4.2 | 3904.7619 | 4.35 | 15600 | 3.7 | 4216.2162 | 3.7 | 14800 | 3.2 | 4625 | 3.05
|  | 3636.3636 | 35.2099 | nom | 14000 | 5.5 | 2545.4545 | 706.09 | 14000 | 5.15 | 2718.4466 | 742.115 | 14000 | 4.8 | 2916.6667 | 782.0137 | 14000 | 4.45 | 3146.0674 | 835.9457 | 14000 | 4 | 3500 | 982.801 | 14000 | 3.5 | 4000 | 1192.2504
|  | 10.9212 | 58.8103 | mid | 11200 | 5.85 | 1914.5299 | 0 | 11200 | 5.55 | 2018.018 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.9 | 2285.7143 | 0 | 11200 | 4.3 | 2604.6512 | 0 | 11200 | 3.7 | 3027.027 | 0
|  | 3636.7647 | 743.7896 | min | 6600 | 5.15 | 1281.5534 | 0 | 6200 | 4.9 | 1265.3061 | 0 | 5800 | 4.65 | 1247.3118 | 0 | 5400 | 4.35 | 1241.3793 | 0 | 5200 | 3.7 | 1405.4054 | 0 | 5000 | 3.05 | 1639.3443 | 0
| 13 |  | 4.978 | max | 17566.6667 | 5.2833 | 3324.9211 | 5.15 | 17266.6667 | 4.9333 | 3500 | 4.9667 | 17033.3333 | 4.55 | 3743.5897 | 4.7833 | 16833.3333 | 4.3 | 3914.7287 | 4.55 | 16033.3333 | 3.8 | 4219.2982 | 3.9167 | 15200 | 3.3 | 4606.0606 | 3.2667
|  | 3305.7851 | 34.3821 | nom | 14000 | 5.5 | 2545.4545 | 641.9 | 14000 | 5.1833 | 2700.9646 | 665.5943 | 14000 | 4.8667 | 2876.7123 | 691.1049 | 14000 | 4.55 | 3076.9231 | 726.5462 | 14000 | 4.1 | 3414.6341 | 844.0302 | 14000 | 3.6167 | 3870.9677 | 1011.975
|  | 9.928 | 52.5274 | mid | 11200 | 5.9 | 1898.3051 | 0 | 11200 | 5.5833 | 2005.9701 | 0 | 11200 | 5.3167 | 2106.5831 | 0 | 11200 | 5.0167 | 2232.5581 | 0 | 11200 | 4.4167 | 2535.8491 | 0 | 11200 | 3.8167 | 2934.4978 | 0
|  | 3306.037 | 664.1302 | min | 6700 | 5.15 | 1300.9709 | 0 | 6266.6667 | 4.9667 | 1261.745 | 0 | 5833.3333 | 4.7833 | 1219.5122 | 0 | 5400 | 4.55 | 1186.8132 | 0 | 5233.3333 | 3.9167 | 1336.1702 | 0 | 5066.6667 | 3.2667 | 1551.0204 | 0
| 14 |  | 5.0504 | max | 18033.3333 | 5.3167 | 3391.8495 | 5.15 | 17733.3333 | 4.9667 | 3570.4698 | 5.0333 | 17466.6667 | 4.65 | 3756.2724 | 4.9167 | 17266.6667 | 4.4 | 3924.2424 | 4.75 | 16466.6667 | 3.9 | 4222.2222 | 4.1333 | 15600 | 3.4 | 4588.2353 | 3.4833
|  | 2975.2066 | 33.5349 | nom | 14000 | 5.5 | 2545.4545 | 577.71 | 14000 | 5.2167 | 2683.7061 | 591.1007 | 14000 | 4.9333 | 2837.8378 | 605.1268 | 14000 | 4.65 | 3010.7527 | 626.3593 | 14000 | 4.2 | 3333.3333 | 719.8081 | 14000 | 3.7333 | 3750 | 854.1263
|  | 8.9351 | 46.4752 | mid | 11200 | 5.95 | 1882.3529 | 0 | 11200 | 5.6167 | 1994.0653 | 0 | 11200 | 5.3833 | 2080.4954 | 0 | 11200 | 5.1333 | 2181.8182 | 0 | 11200 | 4.5333 | 2470.5882 | 0 | 11200 | 3.9333 | 2847.4576 | 0
|  | 2975.402 | 589.1388 | min | 6800 | 5.15 | 1320.3883 | 0 | 6333.3333 | 5.0333 | 1258.2781 | 0 | 5866.6667 | 4.9167 | 1193.2203 | 0 | 5400 | 4.75 | 1136.8421 | 0 | 5266.6667 | 4.1333 | 1274.1935 | 0 | 5133.3333 | 3.4833 | 1473.6842 | 0
| 15 |  | 5.1117 | max | 18500 | 5.35 | 3457.9439 | 5.15 | 18200 | 5 | 3640 | 5.1 | 17900 | 4.75 | 3768.4211 | 5.05 | 17700 | 4.5 | 3933.3333 | 4.95 | 16900 | 4 | 4225 | 4.35 | 16000 | 3.5 | 4571.4286 | 3.7
|  | 2644.6281 | 32.6657 | nom | 14000 | 5.5 | 2545.4545 | 513.52 | 14000 | 5.25 | 2666.6667 | 518.5545 | 14000 | 5 | 2800 | 523.6887 | 14000 | 4.75 | 2947.3684 | 534.2683 | 14000 | 4.3 | 3255.814 | 607.9605 | 14000 | 3.85 | 3636.3636 | 714.7644
|  | 7.942 | 40.5822 | mid | 11200 | 6 | 1866.6667 | 0 | 11200 | 5.65 | 1982.3009 | 0 | 11200 | 5.45 | 2055.0459 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.65 | 2408.6022 | 0 | 11200 | 4.05 | 2765.4321 | 0
|  | 2644.6731 | 517.3793 | min | 6900 | 5.15 | 1339.8058 | 0 | 6400 | 5.1 | 1254.902 | 0 | 5900 | 5.05 | 1168.3168 | 0 | 5400 | 4.95 | 1090.9091 | 0 | 5300 | 4.35 | 1218.3908 | 0 | 5200 | 3.7 | 1405.4054 | 0
| 16 |  | 6.0804 | max | 19020 | 5.73 | 3319.3717 | 6.92 | 18720 | 5.3 | 3532.0755 | 5.68 | 18420 | 4.95 | 3721.2121 | 5.37 | 18200 | 4.59 | 3965.1416 | 5.02 | 17380 | 4.08 | 4259.8039 | 4.36 | 16460 | 3.56 | 4623.5955 | 3.65
|  | 2314.0496 | 31.771 | nom | 14000 | 5.93 | 2360.8769 | 334.4002 | 14000 | 5.57 | 2513.465 | 407.4031 | 14000 | 5.21 | 2687.1401 | 430.9217 | 14000 | 4.85 | 2886.5979 | 460.9661 | 14000 | 4.39 | 3189.0661 | 530.7453 | 14000 | 3.92 | 3571.4286 | 633.9862
|  | 7.0085 | 34.9137 | mid | 11200 | 6.42 | 1744.5483 | 0 | 11200 | 5.99 | 1869.783 | 0 | 11200 | 5.68 | 1971.831 | 0 | 11200 | 5.36 | 2089.5522 | 0 | 11200 | 4.74 | 2362.8692 | 0 | 11200 | 4.12 | 2718.4466 | 0
|  | 2333.8414 | 383.8301 | min | 6980 | 6.92 | 1008.6705 | 0 | 6460 | 5.68 | 1137.3239 | 0 | 6000 | 5.37 | 1117.3184 | 0 | 5520 | 5.02 | 1099.6016 | 0 | 5360 | 4.36 | 1229.3578 | 0 | 5180 | 3.65 | 1419.1781 | 0
| 17 |  | 7.2694 | max | 19540 | 6.11 | 3198.036 | 8.69 | 19240 | 5.6 | 3435.7143 | 6.26 | 18940 | 5.15 | 3677.6699 | 5.69 | 18700 | 4.68 | 3995.7265 | 5.09 | 17860 | 4.16 | 4293.2692 | 4.37 | 16920 | 3.62 | 4674.0331 | 3.6
|  | 1983.4711 | 30.8461 | nom | 14000 | 6.36 | 2201.2579 | 228.2475 | 14000 | 5.89 | 2376.91 | 316.8484 | 14000 | 5.42 | 2583.0258 | 348.5889 | 14000 | 4.95 | 2828.2828 | 389.68 | 14000 | 4.48 | 3125 | 453.8835 | 14000 | 3.99 | 3508.7719 | 550.9642
|  | 6.1134 | 29.4096 | mid | 11200 | 6.84 | 1637.4269 | 0 | 11200 | 6.33 | 1769.3523 | 0 | 11200 | 5.91 | 1895.0931 | 0 | 11200 | 5.47 | 2047.532 | 0 | 11200 | 4.83 | 2318.8406 | 0 | 11200 | 4.19 | 2673.031 | 0
|  | 2035.7547 | 280.0447 | min | 7060 | 8.69 | 812.4281 | 0 | 6520 | 6.26 | 1041.5335 | 0 | 6100 | 5.69 | 1072.0562 | 0 | 5640 | 5.09 | 1108.055 | 0 | 5420 | 4.37 | 1240.2746 | 0 | 5160 | 3.6 | 1433.3333 | 0
| 18 |  | 8.6917 | max | 20060 | 6.49 | 3090.9091 | 10.46 | 19760 | 5.9 | 3349.1525 | 6.84 | 19460 | 5.35 | 3637.3832 | 6.01 | 19200 | 4.77 | 4025.1572 | 5.16 | 18340 | 4.24 | 4325.4717 | 4.38 | 17380 | 3.68 | 4722.8261 | 3.55
|  | 1652.8926 | 29.8848 | nom | 14000 | 6.79 | 2061.8557 | 158.0203 | 14000 | 6.21 | 2254.4283 | 241.651 | 14000 | 5.63 | 2486.6785 | 275.0237 | 14000 | 5.05 | 2772.2772 | 320.328 | 14000 | 4.57 | 3063.4573 | 377.3727 | 14000 | 4.06 | 3448.2759 | 465.6035
|  | 5.1908 | 24.072 | mid | 11200 | 7.26 | 1542.6997 | 0 | 11200 | 6.67 | 1679.1604 | 0 | 11200 | 6.14 | 1824.1042 | 0 | 11200 | 5.58 | 2007.1685 | 0 | 11200 | 4.92 | 2276.4228 | 0 | 11200 | 4.26 | 2629.108 | 0
|  | 1728.5381 | 198.8725 | min | 7140 | 10.46 | 682.6004 | 0 | 6580 | 6.84 | 961.9883 | 0 | 6200 | 6.01 | 1031.614 | 0 | 5760 | 5.16 | 1116.2791 | 0 | 5480 | 4.38 | 1251.1416 | 0 | 5140 | 3.55 | 1447.8873 | 0
| 19 |  | 10.3648 | max | 20580 | 6.87 | 2995.6332 | 12.23 | 20280 | 6.2 | 3270.9677 | 7.42 | 19980 | 5.55 | 3600 | 6.33 | 19700 | 4.86 | 4053.4979 | 5.23 | 18820 | 4.32 | 4356.4815 | 4.39 | 17840 | 3.74 | 4770.0535 | 3.5
|  | 1322.314 | 28.8778 | nom | 14000 | 7.22 | 1939.0582 | 108.1205 | 14000 | 6.53 | 2143.951 | 178.2094 | 14000 | 5.84 | 2397.2603 | 208.8964 | 14000 | 5.15 | 2718.4466 | 252.8325 | 14000 | 4.66 | 3004.2918 | 301.2105 | 14000 | 4.13 | 3389.8305 | 377.804
|  | 4.2113 | 18.9035 | mid | 11200 | 7.68 | 1458.3333 | 0 | 11200 | 7.01 | 1597.7175 | 0 | 11200 | 6.37 | 1758.2418 | 0 | 11200 | 5.69 | 1968.3656 | 0 | 11200 | 5.01 | 2235.5289 | 0 | 11200 | 4.33 | 2586.6051 | 0
|  | 1402.3503 | 135.2995 | min | 7220 | 12.23 | 590.3516 | 0 | 6640 | 7.42 | 894.8787 | 0 | 6300 | 6.33 | 995.2607 | 0 | 5880 | 5.23 | 1124.283 | 0 | 5540 | 4.39 | 1261.959 | 0 | 5120 | 3.5 | 1462.8571 | 0
| 20 |  | 12.3139 | max | 21100 | 7.25 | 2910.3448 | 14 | 20800 | 6.5 | 3200 | 8 | 20500 | 5.75 | 3565.2174 | 6.65 | 20200 | 4.95 | 4080.8081 | 5.3 | 19300 | 4.4 | 4386.3636 | 4.4 | 18300 | 3.8 | 4815.7895 | 3.45
|  | 991.7355 | 27.8102 | nom | 14000 | 7.65 | 1830.0654 | 70.8383 | 14000 | 6.85 | 2043.7956 | 123.9669 | 14000 | 6.05 | 2314.0496 | 149.1332 | 14000 | 5.25 | 2666.6667 | 187.1199 | 14000 | 4.75 | 2947.3684 | 225.3944 | 14000 | 4.2 | 3333.3333 | 287.4596
|  | 3.1716 | 13.9066 | mid | 11200 | 8.1 | 1382.716 | 0 | 11200 | 7.35 | 1523.8095 | 0 | 11200 | 6.6 | 1696.9697 | 0 | 11200 | 5.8 | 1931.0345 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.4 | 2545.4545 | 0
|  | 1056.1426 | 85.7684 | min | 7300 | 14 | 521.4286 | 0 | 6700 | 8 | 837.5 | 0 | 6400 | 6.65 | 962.406 | 0 | 6000 | 5.3 | 1132.0755 | 0 | 5600 | 4.4 | 1272.7273 | 0 | 5100 | 3.45 | 1478.2609 | 0