## Notes
Modelling Tool for Home Heating System with 14kW Mitsubishi Ecodan ASHP Models PUZ-HWM140VHA(-BS) and PUZ-HWM140YHA(-BS).
The initial data used in the accompanying tables was obtained from document Mitsubishi Ecodan Data Book Vol.5.3 R32, the Performance Data
having been obtained from testing carried out to the requirements of EN14511-2013.
How to use the Modelling Tool.
1. Open the Initial Data sheet and set the operating parameters for the particular system under investigation. (The cells that require setting are highlighted in green).
a) In cell C1 set the the Heat Demand as derived from Heat Loss calculations carried out at the specified Ambient Air Temperature (cell E1).
b) In cell H1 set a desired Indoor Temperature.
c) In cell P1 set the value for the Total Heating Elements Output. (If the required information is not available, measure the size and type of all radiators etc. and
obtain the data from a suitable source).
Once the initial operating parameters have been set the table below will show the anticipated operating characteristics for the system.
Of particular interest may be the following:-
Column B shows various Ambient Air Temperatures.
Column C shows the corresponding calculated Heating Demand.
Column D shows the following:-
Calculated Coefficient of Performance (COP).
Calculated Leaving (Flow) Water Temperature (LWT).
Calculated Duty Cycle (Duty (%)). At higher ambient air temperatures the ASHP will not operate continuoiusly, but will cycle.
Calculated Power Input (PI). The electrical energy drawn from the power supply.
Using the Initial Data sheet it should be possible to compare the performance of a working heating system against the manufacturers specified operating criteria.
Any large discrepancies should become obvious and may lead to further investigation becoming necessary.
It will also be possible to carry out 'what if' scenarious, to investigate the effect of possible improvements that could be made to improve overall efficiency.
To see what effect lowering the Heating Demand by improved insulation would have on system operation.
To see what effect varying the Indoor Temperature would have on system operation.
To see what effect installing larger Heat Emitters would have on system operation.
Using the Playroom sheet will allow more detailed investigation of system operation over specific 24 hours periods.
The Play Area table allows hourly variations to be made to the Outdoor Temperature and Indoor Temperature experienced by the system.
This in turn allows the calculation of the following parameters:-
COP
LWT
PI
Heat Energy
It should therefore be possible to see the effects of making changes to the desired indoor temperature throughout the day.
The Lookup Table contains the data necessary for the calculations to be made and should not be changed.
The Data for Graph table contains the data necessary for the production of the graph and should not be changed.
The Pretty Graph shows the calculated Input Power, Output Power and COP, for Indoor Temperatures of 19C, 21C and 23C.
The Detailed Data sheet contains 6 tables which calculate the various parameters at Indoor Temperatures from 18C to 23C.
The data within the tables has been extrapolated from the manufaturers data, to provide ambient air increments of 1C.
Cells containing Bold text or highlighted in Yellow contain formulas, and should not be changed.
Two further parameters have been added to the Detailed Data sheet, Water Temp Hyst. (C.) in cell C2 and Buffer Tank Effect (%) in cell N2.
The Water Temp Hyst. (C.) allows investigation of the possible effect of changing the point at which the ASHP would start and stop operating as the water flowing heat up and cools down.
The Buffer Tank Effect (%) allows investigation of the possible effect of changing of flow rates as pumps stop and start and valves open and close
Both of these paramaters have been set at zero for the moment.
The modelling tool deals solely with heating demand and makes no allowance for hot water production and usage.
It is also impossible to take any account of changes in operation due to solar gain, human activity, wind chill and rain effect.

## Initial Data
Heating Demand (W) |  | 10230 | at Amb. | -3.2 | Indoor Temp. |  | 21 |  | Total Heating Elements Output (W) | [5 empty] | 24000 | at Delta T of 50C | [8 empty] | 7440 |  |  |  | 24000
LWT |  |  |  |  | 25 |  |  |  | 35 |  |  |  | 40 |  |  |  | 45 |  |  |  | 50 |  |  |  | 55
Outdoor air temperature[℃] |  | Heating Demand | COP | CL | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP
|  |  | LWT |  |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI
Duty (%)
PI
12kW-Maximum heating CAP | -15 |  | 0.4446 | max | - | - | - | - | 14000 | 1.85 | 7567.5676 | 1.6673 | 13500 | 1.7 | 7941.1765 | 1.4251 | 13100 | 1.55 | 8451.6129 | 1.197 | 12600 | 1.45 | 8689.6552 | 0.95909 | 12200 | 1.3 | 9384.6154 | 0.54545
|  | 15218.1818 | 56.2192 | nom | - | - | - | - | 11000 | 2.3 | 4782.6087 | 9127.59 | 11000 | 2.1 | 5238.0952 | 10678.7446 | 11000 | 1.9 | 5789.4737 | 12713.9241 | 11000 | 1.75 | 6285.7143 | 15867.2986 | 11000 | 1.6 | 6875 | 27900
|  |  | 100 | mid | - | - | - | - | 8800 | 2.5 | 3520 | 3 | 8800 | 2.3 | 3826.087 | 3 | 8800 | 2.1 | 4190.4762 | 3 | 8800 | 1.9 | 4631.5789 | 3 | 8800 | 1.7 | 5176.4706 | 3
|  |  | 34229.1149 | min | - | - | - | - | 7800 | 2.35 | 3319.1489 | 1.4061 | 7200 | 2 | 3600 | 1.6873 | 6500 | 1.6 | 4062.5 | 2.0087 | 5700 | 1.3 | 4384.6154 | 2.6364 | 4800 | 1 | 4800 | 3.5152
| -10 |  | 1.8592 | max | 14600 | 2.4 | 6083.3333 | 2.816 | 14400 | 2.25 | 6400 | 2.564 | 14200 | 2.1 | 6761.9048 | 2.3119 | 14000 | 1.9 | 7368.4211 | 2.0439 | 14000 | 1.85 | 7567.5676 | 1.93 | 14000 | 1.75 | 8000 | 1.782
|  | 13104.5455 | 52.3924 | nom | 14000 | 2.8 | 5000 | 4653.6189 | 14000 | 2.5 | 5600 | 5111.0548 | 14000 | 2.2 | 6363.6364 | 5668.2232 | 14000 | 1.9 | 7368.4211 | 6411.5007 | 14000 | 1.85 | 7567.5676 | 6790.0913 | 14000 | 1.75 | 8000 | 7353.9218
|  |  | 100 | mid | 11200 | 2.85 | 3929.8246 | 2 | 11200 | 2.7 | 4148.1481 | 2 | 11200 | 2.55 | 4392.1569 | 2 | 11200 | 2.35 | 4765.9574 | 2 | 11200 | 2.1 | 5333.3333 | 2 | 11200 | 1.85 | 6054.0541 | 2
|  |  | 7048.6739 | min | 6200 | 2.55 | 2431.3725 | 0.68019 | 5900 | 2.3 | 2565.2174 | 0.68019 | 5600 | 2.05 | 2731.7073 | 0.68019 | 5300 | 1.75 | 3028.5714 | 0.68019 | 4600 | 1.45 | 3172.4138 | 0.68019 | 4000 | 1.1 | 3636.3636 | 0.68019
| -7 |  | 2.2648 | max | 16100 | 2.7 | 5962.963 | 3.2045 | 15900 | 2.5 | 6360 | 2.9545 | 15700 | 2.3 | 6826.087 | 2.7045 | 15500 | 2.1 | 7380.9524 | 2.4545 | 14700 | 2.05 | 7170.7317 | 2.2659 | 14000 | 1.95 | 7179.4872 | 2.0659
|  | 11836.3636 | 50.0283 | nom | 14000 | 3.05 | 4590.1639 | 3693.617 | 14000 | 2.8 | 5000 | 4006.1538 | 14000 | 2.55 | 5490.1961 | 4376.4706 | 14000 | 2.3 | 6086.9565 | 4822.2222 | 14000 | 2.15 | 6511.6279 | 5223.671 | 14000 | 1.95 | 7179.4872 | 5729.3729
|  |  | 100 | mid | 11200 | 3.25 | 3446.1538 | 2 | 11200 | 3 | 3733.3333 | 2 | 11200 | 2.75 | 4072.7273 | 2 | 11200 | 2.5 | 4480 | 2 | 11200 | 2.3 | 4869.5652 | 2 | 11200 | 2.1 | 5333.3333 | 2
|  |  | 5226.2819 | min | 5100 | 3.65 | 1397.2603 | 0.22727 | 4000 | 2.25 | 1777.7778 | 0.22727 | 4000 | 2.05 | 1951.2195 | 0.22727 | 4000 | 1.85 | 2162.1622 | 0.22727 | 3600 | 1.5 | 2400 | 0.22727 | 3100 | 1.15 | 2695.6522 | 0.22727 |  | 114982
| 2 |  | 2.9189 | max | 16500 | 3.25 | 5076.9231 | 3.9612 | 16300 | 3 | 5433.3333 | 3.5298 | 16000 | 2.75 | 5818.1818 | 3.1256 | 15800 | 2.5 | 6320 | 2.719 | 15100 | 2.45 | 6163.2653 | 2.4543 | 14300 | 2.35 | 6085.1064 | 2.154
|  | 8031.8182 | 42.5417 | nom | 14000 | 3.4 | 4117.6471 | 2027.6426 | 14000 | 3.15 | 4444.4444 | 2275.4035 | 14000 | 2.9 | 4827.5862 | 2569.6643 | 14000 | 2.65 | 5283.0189 | 2954.0027 | 14000 | 2.55 | 5490.1961 | 3272.5454 | 14000 | 2.4 | 5833.3333 | 3728.8314 | 7583 | 114981.8182
|  |  | 100 | mid | 11200 | 3.65 | 3068.4932 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 3.15 | 3555.5556 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.55 | 4392.1569 | 1
|  |  | 2751.6549 | min | 5600 | 4.2 | 1333.3333 | 0.43425 | 5100 | 3.65 | 1397.2603 | 0.48063 | 4700 | 3.1 | 1516.129 | 0.51259 | 4200 | 2.5 | 1680 | 0.5474 | 3700 | 2.05 | 1804.878 | 0.57758 | 3200 | 1.55 | 2064.5161 | 0.60398
| 7 |  | 4.0602 | max | 16800 | 4.7 | 3574.4681 | 6.3142 | 16600 | 4.25 | 3905.8824 | 4.5359 | 16400 | 3.8 | 4315.7895 | 3.7514 | 16100 | 3.3 | 4878.7879 | 2.9917 | 15400 | 2.9 | 5310.3448 | 2.5301 | 14600 | 2.5 | 5840 | 2.049
|  | 5918.1818 | 38.0318 | nom | 14000 | 4.9 | 2857.1429 | 937.2744 | 14000 | 4.45 | 3146.0674 | 1304.74 | 14000 | 4 | 3500 | 1577.5954 | 14000 | 3.5 | 4000 | 1978.1973 | 14000 | 3.15 | 4444.4444 | 2339.1529 | 14000 | 2.75 | 5090.9091 | 2888.2699
|  |  | 100 | mid | 11200 | 5.25 | 2133.3333 | 1 | 11200 | 4.8 | 2333.3333 | 1 | 11200 | 4.35 | 2574.7126 | 1 | 11200 | 3.85 | 2909.0909 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 2.9 | 3862.069 | 1
|  |  | 1457.6036 | min | 4500 | 6.6 | 681.8182 | 0.21167 | 4200 | 4.45 | 943.8202 | 0.24545 | 3700 | 3.5 | 1057.1429 | 0.29576 | 3200 | 2.55 | 1254.902 | 0.33977 | 2700 | 2 | 1350 | 0.37861 | 2200 | 1.45 | 1517.2414 | 0.41313
| 12 |  | 4.9469 | max | 17100 | 5.25 | 3257.1429 | 5.15 | 16800 | 4.9 | 3428.5714 | 4.9 | 16600 | 4.45 | 3730.3371 | 4.65 | 16400 | 4.2 | 3904.7619 | 4.35 | 15600 | 3.7 | 4216.2162 | 3.7 | 14800 | 3.2 | 4625 | 3.05
|  | 3804.5455 | 33.1243 | nom | 14000 | 5.5 | 2545.4545 | 738.7467 | 14000 | 5.15 | 2718.4466 | 776.4378 | 14000 | 4.8 | 2916.6667 | 818.1818 | 14000 | 4.45 | 3146.0674 | 874.6082 | 14000 | 4 | 3500 | 1028.2555 | 14000 | 3.5 | 4000 | 1247.392
|  |  | 60.6299 | mid | 11200 | 5.85 | 1914.5299 | 0 | 11200 | 5.55 | 2018.018 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.9 | 2285.7143 | 0 | 11200 | 4.3 | 2604.6512 | 0 | 11200 | 3.7 | 3027.027 | 0
|  |  | 769.0778 | min | 6600 | 5.15 | 1281.5534 | 0 | 6200 | 4.9 | 1265.3061 | 0 | 5800 | 4.65 | 1247.3118 | 0 | 5400 | 4.35 | 1241.3793 | 0 | 5200 | 3.7 | 1405.4054 | 0 | 5000 | 3.05 | 1639.3443 | 0
| 15 |  | 5.1256 | max | 18500 | 5.35 | 3457.9439 | 5.15 | 18200 | 5 | 3640 | 5.1 | 17900 | 4.75 | 3768.4211 | 5.05 | 17700 | 4.5 | 3933.3333 | 4.95 | 16900 | 4 | 4225 | 4.35 | 16000 | 3.5 | 4571.4286 | 3.7
|  | 2536.3636 | 29.8757 | nom | 14000 | 5.5 | 2545.4545 | 492.4978 | 14000 | 5.25 | 2666.6667 | 497.3262 | 14000 | 5 | 2800 | 502.2502 | 14000 | 4.75 | 2947.3684 | 512.3967 | 14000 | 4.3 | 3255.814 | 583.0721 | 14000 | 3.85 | 3636.3636 | 685.5037
|  |  | 38.1052 | mid | 11200 | 6 | 1866.6667 | 0 | 11200 | 5.65 | 1982.3009 | 0 | 11200 | 5.45 | 2055.0459 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.65 | 2408.6022 | 0 | 11200 | 4.05 | 2765.4321 | 0
|  |  | 494.8402 | min | 6900 | 5.15 | 1339.8058 | 0 | 6400 | 5.1 | 1254.902 | 0 | 5900 | 5.05 | 1168.3168 | 0 | 5400 | 4.95 | 1090.9091 | 0 | 5300 | 4.35 | 1218.3908 | 0 | 5200 | 3.7 | 1405.4054 | 0
| 20 |  | 14 | max | 21100 | 7.25 | 2910.3448 | 14 | 20800 | 6.5 | 3200 | 8 | 20500 | 5.75 | 3565.2174 | 6.65 | 20200 | 4.95 | 4080.8081 | 5.3 | 19300 | 4.4 | 4386.3636 | 4.4 | 18300 | 3.8 | 4815.7895 | 3.45
|  | 422.7273 | 23.2368 | nom | 14000 | 7.65 | 1830.0654 | 30.1948 | 14000 | 6.85 | 2043.7956 | 52.8409 | 14000 | 6.05 | 2314.0496 | 63.568 | 14000 | 5.25 | 2666.6667 | 79.7599 | 14000 | 4.75 | 2947.3684 | 96.0744 | 14000 | 4.2 | 3333.3333 | 122.5296
|  |  | 5.7908 | mid | 11200 | 8.1 | 1382.716 | 0 | 11200 | 7.35 | 1523.8095 | 0 | 11200 | 6.6 | 1696.9697 | 0 | 11200 | 5.8 | 1931.0345 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.4 | 2545.4545 | 0
|  |  | 30.1948 | min | 7300 | 14 | 521.4286 | 0 | 6700 | 8 | 837.5 | 0 | 6400 | 6.65 | 962.406 | 0 | 6000 | 5.3 | 1132.0755 | 0 | 5600 | 4.4 | 1272.7273 | 0 | 5100 | 3.45 | 1478.2609 | 0
Abbreviations:
LWT: Leaving water temperature (°C )
CL: Capacity level
CAP: Total heating capacity (W)
PI: Power input (W)

## Playroom
Initial Conditions
Heating Demand (W) = |  | 10230
Heating Elements (W) = |  | 24000
Play Area.
Hour |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Indoor Temp. (18 to 23) |  | 20 | 20 | 19 | 19 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
Outside Temp (-15 to 20) |  | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 4 | 5 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 5 | 4 | 3 | Ave COP
COP |  | 3.0656 | 3.0656 | 3.2282 | 3.2282 | 3.4072 | 3.4072 | 3.1188 | 3.33 | 3.5546 | 3.7974 | 4.0602 | 4.0602 | 4.0602 | 4.0602 | 4.0602 | 4.0602 | 4.0602 | 4.0602 | 4.0602 | 4.0602 | 3.7974 | 3.5546 | 3.33 | 3.1188 | 3.5686 | 3.5167 | 4.0406
LWT |  | 40.6641 | 40.6641 | 38.7753 | 38.7753 | 36.8742 | 36.8742 | 41.6641 | 40.7753 | 39.8742 | 38.9601 | 38.0318 | 38.0318 | 38.0318 | 38.0318 | 38.0318 | 38.0318 | 38.0318 | 38.0318 | 38.0318 | 38.0318 | 38.9601 | 39.8742 | 40.7753 | 41.6641 | Totals
PI (W/h) |  | 2482.1016 | 2482.1016 | 2226.1089 | 2226.1089 | 1985.1238 | 1985.1238 | 2439.7617 | 2158.0904 | 1902.7716 | 1669.7902 | 1457.6036 | 1457.6036 | 1457.6036 | 1457.6036 | 1457.6036 | 1457.6036 | 1457.6036 | 1457.6036 | 1457.6036 | 1457.6036 | 1669.7902 | 1902.7716 | 2158.0904 | 2439.7617 | 44303.5325 | 43805 | 28457 | 498.5325
Heat Energy (W/h) |  | 7609.0909 | 7609.0909 | 7186.3636 | 7186.3636 | 6763.6364 | 6763.6364 | 7609.0909 | 7186.3636 | 6763.6364 | 6340.9091 | 5918.1818 | 5918.1818 | 5918.1818 | 5918.1818 | 5918.1818 | 5918.1818 | 5918.1818 | 5918.1818 | 5918.1818 | 5918.1818 | 6340.9091 | 6763.6364 | 7186.3636 | 7609.0909 | 158100 | 154049 | 114982 | 39067
|  | Play Area. 6: 13386.6686 | 114981.8182
[7 empty] | 43118.1818 | 7583 | 7583 | 7583 | 7583 | 7583 | 7583 | 7583 | 7583 | 7583 | 7583 | 7583 | 7583 | 7583 | 7583 | 7583 | 7583 | 7583 | 7583 | 136494 | 7583
Lookup Table.
|  | Play Area. 1: Indoor; Play Area. 2: 18; Play Area. 5: 19; Play Area. 8: 20; Play Area. 11: 21; Play Area. 14: 22; Play Area. 17: 23 | 35048 | 3689 | 6046
|  | Amb. | COP | LWT | PI | COP | LWT | PI | COP | LWT | PI | COP | LWT | PI | COP | LWT | PI | COP | LWT | PI
|  | -15 | 1.1341 | 50.939 | 12300.7449 | 0.92248 | 52.7042 | 15580.4922 | 0.69263 | 54.4642 | 21361.1688 | 0.4446 | 56.2192 | 34229.1149 | 0.17844 | 57.9693 | 87653.7953 | -0.10578 | 59.7148 | -151860.1008 | [5 empty] | 140187
|  | -14 | 1.7936 | 50.1685 | 7542.03 | 1.7183 | 51.939 | 8118.6865 | 1.733 | 53.7042 | 8293.534 | 1.7461 | 55.4642 | 8473.6098 | 1.7451 | 57.2192 | 8720.2809 | 1.7303 | 58.9693 | 9039.3529 |  | Hours | Temp | PI/Hr | PI | PO/Hr | PO | COP | PI
|  | -13 | 1.8684 | 49.3924 | 7013.7594 | 1.7881 | 51.1685 | 7564.9712 | 1.716 | 52.939 | 8129.2119 | 1.7309 | 54.7042 | 8303.7948 | 1.7434 | 56.4642 | 8486.4772 | 1.742 | 58.2192 | 8736.1169 |  | 24 | 21 | 1756 | 42144 | 5841 | 140184 | 3.3263
|  | -12 | 1.9522 | 48.6105 | 6496.1967 | 1.865 | 50.3924 | 7026.6378 | 1.7854 | 52.1685 | 7576.7921 | 1.7177 | 53.939 | 8121.4862 | 1.7327 | 55.7042 | 8294.8878 | 1.7448 | 57.4642 | 8479.8984 |  | 2 | 20 | 0 | 0 | 5534 | 11068 |  | 11682
|  | -11 | 2.0495 | 47.8225 | 5981.4498 | 1.95 | 49.6105 | 6503.606 | 1.8613 | 51.3924 | 7040.3638 | 1.7852 | 53.1685 | 7577.3882 | 1.7232 | 54.939 | 8095.6131 | 1.7386 | 56.7042 | 8266.9361 |  | 2 | 19 | 0 | 0 | 5226 | 10452 |  | 11682
|  | -10 | 2.1648 | 47.0283 | 5467.7704 | 2.0465 | 48.8225 | 5990.282 | 1.9469 | 50.6105 | 6513.9757 | 1.8592 | 52.3924 | 7048.6739 | 1.7877 | 54.1685 | 7566.7539 | 1.7325 | 55.939 | 8051.938 |  | 2 | 18 | 0 | 0 | 4919 | 9838 |  | 11682
|  | -9 | 2.3176 | 46.2275 | 4924.8697 | 2.196 | 48.0283 | 5389.9811 | 2.091 | 49.8225 | 5862.842 | 1.9939 | 51.6105 | 6360.3329 | 1.9071 | 53.3924 | 6871.3462 | 1.8313 | 55.1685 | 7386.6992 |  | 18 | 21 | 6257 | 112626 |  | 31358 |  | 35046 | 3688
|  | -8 | 2.4121 | 45.4198 | 4556.6291 | 2.3353 | 47.2275 | 4887.5293 | 2.2294 | 49.0283 | 5309.3175 | 2.1315 | 50.8225 | 5751.5105 | 2.037 | 52.6105 | 6225.7217 | 1.9482 | 54.3924 | 6726.5896 | [6 empty] | 108826
|  | -7 | 2.4624 | 44.6049 | 4291.8752 | 2.4234 | 46.4198 | 4535.2467 | 2.3581 | 48.2275 | 4840.1762 | 2.2648 | 50.0283 | 5226.2819 | 2.1704 | 51.8225 | 5648.41 | 2.0762 | 53.6105 | 6108.1946 |  | 18 | 21 | 1843 | 33174 | 6045 | 108810 | 3.28
|  | -6 | 2.5135 | 43.7824 | 4036.3329 | 2.4648 | 45.6049 | 4287.59 | 2.4305 | 47.4198 | 4522.1355 | 2.3676 | 49.2275 | 4820.7942 | 2.2738 | 51.0283 | 5205.6021 | 2.1794 | 52.8225 | 5624.865
|  | -5 | 2.5711 | 42.952 | 3781.5281 | 2.5124 | 44.7824 | 4038.2264 | 2.4718 | 46.6049 | 4275.4939 | 2.4395 | 48.4198 | 4505.3411 | 2.3786 | 50.2275 | 4798.374 | 2.2833 | 52.0283 | 5183.9384
|  | -4 | 2.6378 | 42.1133 | 3525.702 | 2.5715 | 43.952 | 3780.9657 | 2.5173 | 45.7824 | 4030.3557 | 2.4804 | 47.6049 | 4260.631 | 2.4506 | 49.4198 | 4484.9507 | 2.3885 | 51.2275 | 4778.5863
|  | -3 | 2.7164 | 41.2656 | 3268.0121 | 2.6397 | 43.1133 | 3523.1594 | 2.5685 | 44.952 | 3785.4389 | 2.5254 | 46.7824 | 4017.393 | 2.4907 | 48.6049 | 4243.0715 | 2.4619 | 50.4198 | 4464.3357
|  | -2 | 2.8102 | 40.4086 | 3008.5468 | 2.7199 | 42.2656 | 3263.8776 | 2.6371 | 44.1133 | 3526.6038 | 2.5754 | 45.952 | 3775.1669 | 2.5348 | 47.7824 | 4002.5391 | 2.5026 | 49.6049 | 4222.8952
|  | -1 | 2.9219 | 39.5417 | 2748.8636 | 2.8152 | 41.4086 | 3003.1412 | 2.7177 | 43.2656 | 3266.4449 | 2.6317 | 45.1133 | 3533.8474 | 2.5839 | 46.952 | 3762.8651 | 2.5454 | 48.7824 | 3985.8556
|  | 0 | 3.0552 | 38.6641 | 2490.5183 | 2.9293 | 40.5417 | 2741.8914 | 2.8136 | 42.4086 | 3004.906 | 2.7097 | 44.2656 | 3276.0892 | 2.6391 | 46.1133 | 3523.9161 | 2.5931 | 47.952 | 3749.4332
|  | 1 | 3.2153 | 37.7753 | 2235.0796 | 3.0655 | 39.6641 | 2482.1764 | 2.9282 | 41.5417 | 2742.8772 | 2.8049 | 43.4086 | 3014.2369 | 2.7016 | 45.2656 | 3285.8943 | 2.647 | 47.1133 | 3513.4672
|  | 2 | 3.4072 | 36.8742 | 1985.1238 | 3.2282 | 38.7753 | 2226.1089 | 3.0656 | 40.6641 | 2482.1016 | 2.9189 | 42.5417 | 2751.6549 | 2.7887 | 44.4086 | 3031.6696 | 2.708 | 46.2656 | 3278.1345
|  | 3 | 3.6763 | 35.9601 | 1724.7878 | 3.4724 | 37.8742 | 1947.8239 | 3.2866 | 39.7753 | 2186.5494 | 3.1188 | 41.6641 | 2439.7617 | 2.9678 | 43.5417 | 2706.3587 | 2.8453 | 45.4086 | 2971.4356
|  | 4 | 3.9642 | 35.0318 | 1492.897 | 3.7331 | 36.9601 | 1698.5812 | 3.5215 | 38.8742 | 1920.6596 | 3.33 | 40.7753 | 2158.0904 | 3.157 | 42.6641 | 2410.1913 | 3.001 | 44.5417 | 2676.4217
|  | 5 | 4.2735 | 34.088 | 1285.9503 | 4.0128 | 36.0318 | 1474.8102 | 3.7734 | 37.9601 | 1680.4349 | 3.5546 | 39.8742 | 1902.7716 | 3.3585 | 41.7753 | 2139.7602 | 3.1798 | 43.6641 | 2392.9652
|  | 6 | 4.6396 | 33.1273 | 1093.3654 | 4.3143 | 35.088 | 1273.7781 | 4.0448 | 37.0318 | 1463.1648 | 3.7974 | 38.9601 | 1669.7902 | 3.5739 | 40.8742 | 1892.4928 | 3.3715 | 42.7753 | 2131.4782
|  | 7 | 5.0706 | 32.148 | 917.0426 | 4.6674 | 34.1273 | 1086.8468 | 4.3382 | 36.088 | 1266.7495 | 4.0602 | 38.0318 | 1457.6036 | 3.8054 | 39.9601 | 1666.3142 | 3.578 | 41.8742 | 1890.3256
|  | 8 | 5.2218 | 31.1478 | 809.5377 | 4.8703 | 33.148 | 954.7591 | 4.5507 | 35.1273 | 1114.7059 | 4.299 | 37.088 | 1278.2978 | 4.0665 | 39.0318 | 1455.3333 | 3.8542 | 40.9601 | 1645.1952
|  | 9 | 5.3077 | 30.1243 | 716.7939 | 5.0265 | 32.1478 | 841.0052 | 4.7484 | 34.148 | 979.2708 | 4.4967 | 36.1273 | 1128.0917 | 4.297 | 38.088 | 1278.8992 | 4.1115 | 40.0318 | 1439.4323
|  | 10 | 5.3185 | 29.0741 | 635.8573 | 5.1114 | 31.1243 | 744.3185 | 4.9071 | 33.1478 | 861.4658 | 4.7043 | 35.148 | 988.4544 | 4.4999 | 37.1273 | 1127.3022 | 4.3374 | 39.088 | 1267.001
|  | 11 | 5.2514 | 27.9931 | 563.4821 | 5.1203 | 30.0741 | 660.4684 | 4.9912 | 32.1243 | 762.2551 | 4.8637 | 34.1478 | 869.1498 | 4.7205 | 36.148 | 985.074 | 4.5661 | 38.1273 | 1110.9619
|  | 12 | 5.1031 | 26.8757 | 497.0233 | 5.0502 | 28.9931 | 585.9385 | 4.9981 | 31.0741 | 676.6143 | 4.9469 | 33.1243 | 769.0778 | 4.8926 | 35.1478 | 864.012 | 4.7926 | 37.148 | 970.2456
|  | 13 | 5.1369 | 25.7142 | 411.461 | 5.0973 | 27.8757 | 497.5916 | 5.0585 | 29.9931 | 584.9785 | 5.0203 | 32.0741 | 673.6276 | 4.9827 | 34.1243 | 763.5477 | 4.9246 | 36.1478 | 858.4027
|  | 14 | 5.15 | 24.4975 | 328.3319 | 5.13 | 26.7142 | 412.0148 | 5.1048 | 28.8757 | 496.8601 | 5.0801 | 30.9931 | 582.4889 | 5.0558 | 33.0741 | 668.8984 | 5.0304 | 35.1243 | 756.3057
|  | 15 | 5.15 | 23.2076 | 246.2489 | 5.1475 | 25.4975 | 328.4905 | 5.1364 | 27.7142 | 411.4992 | 5.1256 | 29.8757 | 494.8402 | 5.115 | 31.9931 | 578.5085 | 5.1046 | 34.0741 | 662.5002
|  | 16 | 6.92 | 21.8123 | 122.1755 | 6.92 | 24.2076 | 183.2633 | 6.7343 | 26.4975 | 251.0887 | 6.4594 | 28.7142 | 327.2169 | 6.1914 | 30.8757 | 409.658 | 5.9289 | 32.9931 | 499.0994
|  | 17 | 8.69 | 20.2368 | 48.6453 | 8.69 | 22.8123 | 97.2905 | 8.6395 | 25.2076 | 146.788 | 8.0831 | 27.4975 | 209.1905 | 7.5444 | 29.7142 | 280.158 | 7.0192 | 31.8757 | 361.3459
|  | 18 | 10.46 | 18 | 0 | 10.46 | 21.2368 | 40.4137 | 10.46 | 23.8123 | 80.8274 | 10.0228 | 26.2076 | 126.5292 | 9.1939 | 28.4975 | 183.9163 | 8.3915 | 30.7142 | 251.8797
|  | 19 |  |  |  | 12.23 | 19 | 0 | 12.23 | 22.2368 | 34.5648 | 12.23 | 24.8123 | 69.1296 | 11.1681 | 27.2076 | 113.5536 | 10.0667 | 29.4975 | 167.9705
|  | 20 | [6 empty] | 14 | 20 | 0 | 14 | 23.2368 | 30.1948 | 13.5126 | 25.8123 | 62.5677 | 12.0754 | 28.2076 | 105.0217
Data for Graph.
|  | Indoor | 19 |  |  | 21 |  |  | 23
|  | Amb. | PI (kW) | PO (kW) | COP (%) | PI (kW) | PO (kW) | COP (%) | PI (kW) | PO (kW) | COP (%)
|  | -15 | 15.5805 | 13.95 | 0.92248 | 34.2291 | 15.2182 | 0.4446 | -151.8601 | 16.0636 | -0.10578
|  | -14 | 8.1187 | 13.5273 | 1.7183 | 8.4736 | 14.7955 | 1.7461 | 9.0394 | 15.6409 | 1.7303
|  | -13 | 7.565 | 13.1045 | 1.7881 | 8.3038 | 14.3727 | 1.7309 | 8.7361 | 15.2182 | 1.742
|  | -12 | 7.0266 | 12.6818 | 1.865 | 8.1215 | 13.95 | 1.7177 | 8.4799 | 14.7955 | 1.7448
|  | -11 | 6.5036 | 12.2591 | 1.95 | 7.5774 | 13.5273 | 1.7852 | 8.2669 | 14.3727 | 1.7386
|  | -10 | 5.9903 | 11.8364 | 2.0465 | 7.0487 | 13.1045 | 1.8592 | 8.0519 | 13.95 | 1.7325
|  | -9 | 5.39 | 11.4136 | 2.196 | 6.3603 | 12.6818 | 1.9939 | 7.3867 | 13.5273 | 1.8313
|  | -8 | 4.8875 | 10.9909 | 2.3353 | 5.7515 | 12.2591 | 2.1315 | 6.7266 | 13.1045 | 1.9482
|  | -7 | 4.5352 | 10.5682 | 2.4234 | 5.2263 | 11.8364 | 2.2648 | 6.1082 | 12.6818 | 2.0762
|  | -6 | 4.2876 | 10.1455 | 2.4648 | 4.8208 | 11.4136 | 2.3676 | 5.6249 | 12.2591 | 2.1794
|  | -5 | 4.0382 | 9.7227 | 2.5124 | 4.5053 | 10.9909 | 2.4395 | 5.1839 | 11.8364 | 2.2833
|  | -4 | 3.781 | 9.3 | 2.5715 | 4.2606 | 10.5682 | 2.4804 | 4.7786 | 11.4136 | 2.3885
|  | -3 | 3.5232 | 8.8773 | 2.6397 | 4.0174 | 10.1455 | 2.5254 | 4.4643 | 10.9909 | 2.4619
|  | -2 | 3.2639 | 8.4545 | 2.7199 | 3.7752 | 9.7227 | 2.5754 | 4.2229 | 10.5682 | 2.5026
|  | -1 | 3.0031 | 8.0318 | 2.8152 | 3.5338 | 9.3 | 2.6317 | 3.9859 | 10.1455 | 2.5454
|  | 0 | 2.7419 | 7.6091 | 2.9293 | 3.2761 | 8.8773 | 2.7097 | 3.7494 | 9.7227 | 2.5931
|  | 1 | 2.4822 | 7.1864 | 3.0655 | 3.0142 | 8.4545 | 2.8049 | 3.5135 | 9.3 | 2.647
|  | 2 | 2.2261 | 6.7636 | 3.2282 | 2.7517 | 8.0318 | 2.9189 | 3.2781 | 8.8773 | 2.708
|  | 3 | 1.9478 | 6.3409 | 3.4724 | 2.4398 | 7.6091 | 3.1188 | 2.9714 | 8.4545 | 2.8453
|  | 4 | 1.6986 | 5.9182 | 3.7331 | 2.1581 | 7.1864 | 3.33 | 2.6764 | 8.0318 | 3.001
|  | 5 | 1.4748 | 5.4955 | 4.0128 | 1.9028 | 6.7636 | 3.5546 | 2.393 | 7.6091 | 3.1798
|  | 6 | 1.2738 | 5.0727 | 4.3143 | 1.6698 | 6.3409 | 3.7974 | 2.1315 | 7.1864 | 3.3715
|  | 7 | 1.0868 | 4.65 | 4.6674 | 1.4576 | 5.9182 | 4.0602 | 1.8903 | 6.7636 | 3.578
|  | 8 | 0.95476 | 4.2273 | 4.8703 | 1.2783 | 5.4955 | 4.299 | 1.6452 | 6.3409 | 3.8542
|  | 9 | 0.84101 | 3.8045 | 5.0265 | 1.1281 | 5.0727 | 4.4967 | 1.4394 | 5.9182 | 4.1115
|  | 10 | 0.74432 | 3.3818 | 5.1114 | 0.98845 | 4.65 | 4.7043 | 1.267 | 5.4955 | 4.3374
|  | 11 | 0.66047 | 2.9591 | 5.1203 | 0.86915 | 4.2273 | 4.8637 | 1.111 | 5.0727 | 4.5661
|  | 12 | 0.58594 | 2.5364 | 5.0502 | 0.76908 | 3.8045 | 4.9469 | 0.97025 | 4.65 | 4.7926
|  | 13 | 0.49759 | 2.1136 | 5.0973 | 0.67363 | 3.3818 | 5.0203 | 0.8584 | 4.2273 | 4.9246
|  | 14 | 0.41201 | 1.6909 | 5.13 | 0.58249 | 2.9591 | 5.0801 | 0.75631 | 3.8045 | 5.0304
|  | 15 | 0.32849 | 1.2682 | 5.1475 | 0.49484 | 2.5364 | 5.1256 | 0.6625 | 3.3818 | 5.1046
|  | 16 | 0.18326 | 0.84545 | 6.92 | 0.32722 | 2.1136 | 6.4594 | 0.4991 | 2.9591 | 5.9289
|  | 17 | 0.097291 | 0.42273 | 8.69 | 0.20919 | 1.6909 | 8.0831 | 0.36135 | 2.5364 | 7.0192
|  | 18 | 0.040414 | 0 | 10.46 | 0.12653 | 1.2682 | 10.0228 | 0.25188 | 2.1136 | 8.3915
|  | 19 | 0 | 0 | 12.23 | 0.06913 | 0.84545 | 12.23 | 0.16797 | 1.6909 | 10.0667
|  | 20 | 0 | 0 | 0 | 0.030195 | 0.42273 | 14 | 0.10502 | 1.2682 | 12.0754
Pretty Graph.

## Detailed Data
Heating Demand (W) |  | 10230 | at Amb. | -3.2 |  |  |  |  | Total Heating Elements Output (W) | [5 empty] | 24000 | at Delta T of 50C
Water Temp Hyst. (C.) |  | 0 | [6 empty] | Buffer Tank Effect (%) |  |  |  | 0
Indoor Temp. |  | 18
LWT |  |  |  |  | 25 |  |  |  | 35 |  |  |  | 40 |  |  |  | 45 |  |  |  | 50 |  |  |  | 55
Outdoor air temperature[℃] |  | Heating Demand | COP | CL | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP
|  |  | LWT |  |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI
| -15 |  | 1.1341 | max | - | - | - | - | 14000 | 1.85 | 7567.5676 | 1.8575 | 13500 | 1.7 | 7941.1765 | 1.628 | 13100 | 1.55 | 8451.6129 | 1.4083 | 12600 | 1.45 | 8689.6552 | 1.1969 | 12200 | 1.3 | 9384.6154 | 0.8625
|  | 13950 | 50.939 | nom | - | - | - | - | 11000 | 2.3 | 4782.6087 | 7510.0942 | 11000 | 2.1 | 5238.0952 | 8568.7961 | 11000 | 1.9 | 5789.4737 | 9905.3254 | 11000 | 1.75 | 6285.7143 | 11655.3525 | 11000 | 1.6 | 6875 | 16173.913
|  |  | 100 | mid | - | - | - | - | 8800 | 2.5 | 3520 | 3 | 8800 | 2.3 | 3826.087 | 3 | 8800 | 2.1 | 4190.4762 | 3 | 8800 | 1.9 | 4631.5789 | 3 | 8800 | 1.7 | 5176.4706 | 3
|  |  | 12300.7449 | min | - | - | - | - | 7800 | 2.35 | 3319.1489 | 0.98333 | 7200 | 2 | 3600 | 1.18 | 6500 | 1.6 | 4062.5 | 1.4048 | 5700 | 1.3 | 4384.6154 | 1.8438 | 4800 | 1 | 4800 | 2.4583
| -14 |  | 1.7936 | max | 14280 | 2.08 | 6865.3846 | 2.6484 | 14080 | 1.93 | 7295.3368 | 2.3738 | 13640 | 1.78 | 7662.9213 | 2.1588 | 13280 | 1.62 | 8197.5309 | 1.9422 | 12880 | 1.53 | 8418.3007 | 1.7987 | 12560 | 1.39 | 9035.9712 | 1.6469
|  | 13527.2727 | 50.1685 | nom | 14000 | 2.64 | 5303.0303 | 5107.635 | 14000 | 2.34 | 5982.906 | 5698.6541 | 14000 | 2.12 | 6603.7736 | 6266.017 | 14000 | 1.9 | 7368.4211 | 6964.8947 | 14000 | 1.77 | 7909.6045 | 7520.5776 | 14000 | 1.63 | 8588.9571 | 8213.8633
|  |  | 100 | mid | 11200 | 2.69 | 4163.5688 | 2 | 11200 | 2.54 | 4409.4488 | 2 | 11200 | 2.35 | 4765.9574 | 2 | 11200 | 2.15 | 5209.3023 | 2 | 11200 | 1.94 | 5773.1959 | 2 | 11200 | 1.73 | 6473.9884 | 2
|  |  | 7542.03 | min | 7720 | 2.59 | 2980.695 | 0.83117 | 7420 | 2.34 | 3170.9402 | 0.83117 | 6880 | 2.01 | 3422.8856 | 0.83117 | 6260 | 1.63 | 3840.4908 | 0.83117 | 5480 | 1.33 | 4120.3008 | 0.83117 | 4640 | 1.02 | 4549.0196 | 0.83117
| -13 |  | 1.8684 | max | 14360 | 2.16 | 6648.1481 | 2.696 | 14160 | 2.01 | 7044.7761 | 2.444 | 13780 | 1.86 | 7408.6022 | 2.2231 | 13460 | 1.69 | 7964.497 | 1.9959 | 13160 | 1.61 | 8173.913 | 1.8508 | 12920 | 1.48 | 8729.7297 | 1.692
|  | 13104.5455 | 49.3924 | nom | 14000 | 2.68 | 5223.8806 | 4860.754 | 14000 | 2.38 | 5882.3529 | 5362.0108 | 14000 | 2.14 | 6542.0561 | 5894.5862 | 14000 | 1.9 | 7368.4211 | 6565.5958 | 14000 | 1.79 | 7821.2291 | 7080.6179 | 14000 | 1.66 | 8433.7349 | 7745.0924
|  |  | 100 | mid | 11200 | 2.73 | 4102.5641 | 2 | 11200 | 2.58 | 4341.0853 | 2 | 11200 | 2.4 | 4666.6667 | 2 | 11200 | 2.2 | 5090.9091 | 2 | 11200 | 1.98 | 5656.5657 | 2 | 11200 | 1.76 | 6363.6364 | 2
|  |  | 7013.7594 | min | 7340 | 2.58 | 2844.9612 | 0.68019 | 7040 | 2.33 | 3021.4592 | 0.68019 | 6560 | 2.02 | 3247.5248 | 0.68019 | 6020 | 1.66 | 3626.506 | 0.68019 | 5260 | 1.36 | 3867.6471 | 0.68019 | 4480 | 1.04 | 4307.6923 | 0.68019
| -12 |  | 1.9522 | max | 14440 | 2.24 | 6446.4286 | 2.7435 | 14240 | 2.09 | 6813.3971 | 2.5142 | 13920 | 1.94 | 7175.2577 | 2.2965 | 13640 | 1.76 | 7750 | 2.0648 | 13440 | 1.69 | 7952.6627 | 1.9089 | 13280 | 1.57 | 8458.5987 | 1.7371
|  | 12681.8182 | 48.6105 | nom | 14000 | 2.72 | 5147.0588 | 4622.4305 | 14000 | 2.42 | 5785.124 | 5044.1655 | 14000 | 2.16 | 6481.4815 | 5522.1749 | 14000 | 1.9 | 7368.4211 | 6141.9923 | 14000 | 1.81 | 7734.8066 | 6643.6481 | 14000 | 1.69 | 8284.0237 | 7300.6617
|  |  | 100 | mid | 11200 | 2.77 | 4043.3213 | 2 | 11200 | 2.62 | 4274.8092 | 2 | 11200 | 2.45 | 4571.4286 | 2 | 11200 | 2.25 | 4977.7778 | 2 | 11200 | 2.02 | 5544.5545 | 2 | 11200 | 1.79 | 6256.9832 | 2
|  |  | 6496.1967 | min | 6960 | 2.57 | 2708.1712 | 0.52922 | 6660 | 2.32 | 2870.6897 | 0.52922 | 6240 | 2.03 | 3073.8916 | 0.52922 | 5780 | 1.69 | 3420.1183 | 0.52922 | 5040 | 1.39 | 3625.8993 | 0.52922 | 4320 | 1.06 | 4075.4717 | 0.52922
| -11 |  | 2.0495 | max | 14520 | 2.32 | 6258.6207 | 2.7911 | 14320 | 2.17 | 6599.0783 | 2.5844 | 14060 | 2.02 | 6960.396 | 2.379 | 13820 | 1.83 | 7551.9126 | 2.1487 | 13720 | 1.77 | 7751.4124 | 1.973 | 13640 | 1.66 | 8216.8675 | 1.7822
|  | 12259.0909 | 47.8225 | nom | 14000 | 2.76 | 5072.4638 | 4392.2271 | 14000 | 2.46 | 5691.0569 | 4743.5865 | 14000 | 2.18 | 6422.0183 | 5153.1281 | 14000 | 1.9 | 7368.4211 | 5705.349 | 14000 | 1.83 | 7650.2732 | 6213.4165 | 14000 | 1.72 | 8139.5349 | 6878.7233
|  |  | 100 | mid | 11200 | 2.81 | 3985.7651 | 2 | 11200 | 2.66 | 4210.5263 | 2 | 11200 | 2.5 | 4480 | 2 | 11200 | 2.3 | 4869.5652 | 2 | 11200 | 2.06 | 5436.8932 | 2 | 11200 | 1.82 | 6153.8462 | 2
|  |  | 5981.4498 | min | 6580 | 2.56 | 2570.3125 | 0.37825 | 6280 | 2.31 | 2718.6147 | 0.37825 | 5920 | 2.04 | 2901.9608 | 0.37825 | 5540 | 1.72 | 3220.9302 | 0.37825 | 4820 | 1.42 | 3394.3662 | 0.37825 | 4160 | 1.08 | 3851.8519 | 0.37825
| -10 |  | 2.1648 | max | 14600 | 2.4 | 6083.3333 | 2.8386 | 14400 | 2.25 | 6400 | 2.6545 | 14200 | 2.1 | 6761.9048 | 2.4705 | 14000 | 1.9 | 7368.4211 | 2.2477 | 14000 | 1.85 | 7567.5676 | 2.0432 | 14000 | 1.75 | 8000 | 1.8273
|  | 11836.3636 | 47.0283 | nom | 14000 | 2.8 | 5000 | 4169.7358 | 14000 | 2.5 | 5600 | 4458.9041 | 14000 | 2.2 | 6363.6364 | 4791.1684 | 14000 | 1.9 | 7368.4211 | 5265.9252 | 14000 | 1.85 | 7567.5676 | 5793.1034 | 14000 | 1.75 | 8000 | 6477.6119
|  |  | 100 | mid | 11200 | 2.85 | 3929.8246 | 2 | 11200 | 2.7 | 4148.1481 | 2 | 11200 | 2.55 | 4392.1569 | 2 | 11200 | 2.35 | 4765.9574 | 2 | 11200 | 2.1 | 5333.3333 | 2 | 11200 | 1.85 | 6054.0541 | 2
|  |  | 5467.7704 | min | 6200 | 2.55 | 2431.3725 | 0.22727 | 5900 | 2.3 | 2565.2174 | 0.22727 | 5600 | 2.05 | 2731.7073 | 0.22727 | 5300 | 1.75 | 3028.5714 | 0.22727 | 4600 | 1.45 | 3172.4138 | 0.22727 | 4000 | 1.1 | 3636.3636 | 0.22727
| -9 |  | 2.3176 | max | 15100 | 2.5 | 6040 | 2.9757 | 14900 | 2.3333 | 6385.7143 | 2.7847 | 14700 | 2.1667 | 6784.6154 | 2.5938 | 14500 | 1.9667 | 7372.8814 | 2.372 | 14233.3333 | 1.9167 | 7426.087 | 2.1501 | 14000 | 1.8167 | 7706.422 | 1.9244
|  | 11413.6364 | 46.2275 | nom | 14000 | 2.8833 | 4855.4913 | 3835.6095 | 14000 | 2.6 | 5384.6154 | 4098.6359 | 14000 | 2.3167 | 6043.1655 | 4400.3922 | 14000 | 2.0333 | 6885.2459 | 4811.7714 | 14000 | 1.95 | 7179.4872 | 5308.3341 | 14000 | 1.8167 | 7706.422 | 5930.9123
|  |  | 100 | mid | 11200 | 2.9833 | 3754.1899 | 2 | 11200 | 2.8 | 4000 | 2 | 11200 | 2.6167 | 4280.2548 | 2 | 11200 | 2.4 | 4666.6667 | 2 | 11200 | 2.1667 | 5169.2308 | 2 | 11200 | 1.9333 | 5793.1034 | 2
|  |  | 4924.8697 | min | 5833.3333 | 2.9167 | 2000 | 0.076299 | 5266.6667 | 2.2833 | 2306.5693 | 0.076299 | 5066.6667 | 2.05 | 2471.5447 | 0.076299 | 4866.6667 | 1.7833 | 2728.972 | 0.076299 | 4266.6667 | 1.4667 | 2909.0909 | 0.076299 | 3700 | 1.1167 | 3313.4328 | 0.076299
| -8 |  | 2.4121 | max | 15600 | 2.6 | 6000 | 3.1227 | 15400 | 2.4167 | 6372.4138 | 2.8798 | 15200 | 2.2333 | 6805.9701 | 2.6635 | 15000 | 2.0333 | 7377.0492 | 2.4304 | 14466.6667 | 1.9833 | 7294.1176 | 2.2118 | 14000 | 1.8833 | 7433.6283 | 1.993
|  | 10990.9091 | 45.4198 | nom | 14000 | 2.9667 | 4719.1011 | 3519.6308 | 14000 | 2.7 | 5185.1852 | 3816.508 | 14000 | 2.4333 | 5753.4247 | 4126.5381 | 14000 | 2.1667 | 6461.5385 | 4522.2078 | 14000 | 2.05 | 6829.2683 | 4969.3206 | 14000 | 1.8833 | 7433.6283 | 5514.7906
|  |  | 100 | mid | 11200 | 3.1167 | 3593.5829 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.6833 | 4173.913 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.2333 | 5014.9254 | 1 | 11200 | 2.0167 | 5553.719 | 1
|  |  | 4556.6291 | min | 5466.6667 | 3.2833 | 1664.9746 | 0.96353 | 4633.3333 | 2.2667 | 2044.1176 | 0.96816 | 4533.3333 | 2.05 | 2211.3821 | 0.96864 | 4433.3333 | 1.8167 | 2440.367 | 0.9691 | 3933.3333 | 1.4833 | 2651.6854 | 0.97123 | 3400 | 1.1333 | 3000 | 0.97319
| -7 |  | 2.4624 | max | 16100 | 2.7 | 5962.963 | 3.2914 | 15900 | 2.5 | 6360 | 2.9342 | 15700 | 2.3 | 6826.087 | 2.6886 | 15500 | 2.1 | 7380.9524 | 2.443 | 14700 | 2.05 | 7170.7317 | 2.2335 | 14000 | 1.95 | 7179.4872 | 2.0259
|  | 10568.1818 | 44.6049 | nom | 14000 | 3.05 | 4590.1639 | 3210.8171 | 14000 | 2.8 | 5000 | 3601.7428 | 14000 | 2.55 | 5490.1961 | 3930.777 | 14000 | 2.3 | 6086.9565 | 4325.9726 | 14000 | 2.15 | 6511.6279 | 4731.6838 | 14000 | 1.95 | 7179.4872 | 5216.5422
|  |  | 100 | mid | 11200 | 3.25 | 3446.1538 | 1 | 11200 | 3 | 3733.3333 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1 | 11200 | 2.1 | 5333.3333 | 1
|  |  | 4291.8752 | min | 5100 | 3.65 | 1397.2603 | 0.89642 | 4000 | 2.25 | 1777.7778 | 0.91225 | 4000 | 2.05 | 1951.2195 | 0.91225 | 4000 | 1.85 | 2162.1622 | 0.91225 | 3600 | 1.5 | 2400 | 0.91687 | 3100 | 1.15 | 2695.6522 | 0.922
| -6 |  | 2.5135 | max | 16144.4444 | 2.7611 | 5847.0825 | 3.3671 | 15944.4444 | 2.5556 | 6239.1304 | 2.9493 | 15733.3333 | 2.35 | 6695.0355 | 2.7015 | 15533.3333 | 2.1444 | 7243.5233 | 2.453 | 14744.4444 | 2.0944 | 7039.7878 | 2.2404 | 14033.3333 | 1.9944 | 7036.2117 | 2.0254
|  | 10145.4545 | 43.7824 | nom | 14000 | 3.0889 | 4532.3741 | 3013.0793 | 14000 | 2.8389 | 4931.5068 | 3440.0071 | 14000 | 2.5889 | 5407.7253 | 3755.499 | 14000 | 2.3389 | 5985.7482 | 4135.889 | 14000 | 2.1944 | 6379.7468 | 4528.4593 | 14000 | 2 | 7000 | 5009.0508
|  |  | 100 | mid | 11200 | 3.2944 | 3399.6627 | 1 | 11200 | 3.0444 | 3678.8321 | 1 | 11200 | 2.7944 | 4007.9523 | 1 | 11200 | 2.5444 | 4401.7467 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.15 | 5209.3023 | 1
|  |  | 4036.3329 | min | 5155.5556 | 3.7111 | 1389.2216 | 0.82553 | 4122.2222 | 2.4056 | 1713.6259 | 0.85101 | 4077.7778 | 2.1667 | 1882.0513 | 0.85194 | 4022.2222 | 1.9222 | 2092.4855 | 0.85308 | 3611.1111 | 1.5611 | 2313.1673 | 0.86104 | 3111.1111 | 1.1944 | 2604.6512 | 0.86963
| -5 |  | 2.5711 | max | 16188.8889 | 2.8222 | 5736.2205 | 3.4458 | 15988.8889 | 2.6111 | 6123.4043 | 2.9768 | 15766.6667 | 2.4 | 6569.4444 | 2.7224 | 15566.6667 | 2.1889 | 7111.6751 | 2.4662 | 14788.8889 | 2.1389 | 6914.2857 | 2.2484 | 14066.6667 | 2.0389 | 6899.1826 | 2.0242
|  | 9722.7273 | 42.952 | nom | 14000 | 3.1278 | 4476.0213 | 2821.6342 | 14000 | 2.8778 | 4864.8649 | 3266.1724 | 14000 | 2.6278 | 5327.6956 | 3571.4009 | 14000 | 2.3778 | 5887.8505 | 3942.4478 | 14000 | 2.2389 | 6253.1017 | 4324.3376 | 14000 | 2.05 | 6829.2683 | 4803.1709
|  |  | 100 | mid | 11200 | 3.3389 | 3354.4093 | 1 | 11200 | 3.0889 | 3625.8993 | 1 | 11200 | 2.8389 | 3945.2055 | 1 | 11200 | 2.5889 | 4326.1803 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.2 | 5090.9091 | 1
|  |  | 3781.5281 | min | 5211.1111 | 3.7722 | 1381.4433 | 0.75333 | 4244.4444 | 2.5611 | 1657.2668 | 0.78761 | 4155.5556 | 2.2833 | 1819.9513 | 0.79029 | 4044.4444 | 1.9944 | 2027.8552 | 0.79355 | 3622.2222 | 1.6222 | 2232.8767 | 0.80505 | 3122.2222 | 1.2389 | 2520.1794 | 0.81712
| -4 |  | 2.6378 | max | 16233.3333 | 2.8833 | 5630.0578 | 3.5274 | 16033.3333 | 2.6667 | 6012.5 | 3.0175 | 15800 | 2.45 | 6448.9796 | 2.7515 | 15600 | 2.2333 | 6985.0746 | 2.4824 | 14833.3333 | 2.1833 | 6793.8931 | 2.2575 | 14100 | 2.0833 | 6768 | 2.0223
|  | 9300 | 42.1133 | nom | 14000 | 3.1667 | 4421.0526 | 2636.4771 | 14000 | 2.9167 | 4800 | 3082.0423 | 14000 | 2.6667 | 5250 | 3379.9559 | 14000 | 2.4167 | 5793.1034 | 3746.3764 | 14000 | 2.2833 | 6131.3869 | 4119.6214 | 14000 | 2.1 | 6666.6667 | 4598.6923
|  |  | 100 | mid | 11200 | 3.3833 | 3310.3448 | 1 | 11200 | 3.1333 | 3574.4681 | 1 | 11200 | 2.8833 | 3884.3931 | 1 | 11200 | 2.6333 | 4253.1646 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.25 | 4977.7778 | 1
|  |  | 3525.702 | min | 5266.6667 | 3.8333 | 1373.913 | 0.67978 | 4366.6667 | 2.7167 | 1607.362 | 0.72195 | 4233.3333 | 2.4 | 1763.8889 | 0.72727 | 4066.6667 | 2.0667 | 1967.7419 | 0.73364 | 3633.3333 | 1.6833 | 2158.4158 | 0.7489 | 3133.3333 | 1.2833 | 2441.5584 | 0.76446
| -3 |  | 2.7164 | max | 16277.7778 | 2.9444 | 5528.3019 | 3.6122 | 16077.7778 | 2.7222 | 5906.1224 | 3.072 | 15833.3333 | 2.5 | 6333.3333 | 2.7892 | 15633.3333 | 2.2778 | 6863.4146 | 2.5018 | 14877.7778 | 2.2278 | 6678.3042 | 2.2677 | 14133.3333 | 2.1278 | 6642.2977 | 2.0197
|  | 8877.2727 | 41.2656 | nom | 14000 | 3.2056 | 4367.4177 | 2457.5868 | 14000 | 2.9556 | 4736.8421 | 2889.7142 | 14000 | 2.7056 | 5174.538 | 3182.7725 | 14000 | 2.4556 | 5701.3575 | 3548.413 | 14000 | 2.3278 | 6014.3198 | 3914.6121 | 14000 | 2.15 | 6511.6279 | 4395.4057
|  |  | 100 | mid | 11200 | 3.4278 | 3267.423 | 1 | 11200 | 3.1778 | 3524.4755 | 1 | 11200 | 2.9278 | 3825.4269 | 1 | 11200 | 2.6778 | 4182.5726 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1
|  |  | 3268.0121 | min | 5322.2222 | 3.8944 | 1366.6191 | 0.60483 | 4488.8889 | 2.8722 | 1562.8627 | 0.6539 | 4311.1111 | 2.5167 | 1713.0243 | 0.66283 | 4088.8889 | 2.1389 | 1911.6883 | 0.67337 | 3644.4444 | 1.7444 | 2089.172 | 0.69258 | 3144.4444 | 1.3278 | 2368.2008 | 0.71166
| -2 |  | 2.8102 | max | 16322.2222 | 3.0056 | 5430.6839 | 3.7001 | 16122.2222 | 2.7778 | 5804 | 3.1412 | 15866.6667 | 2.55 | 6222.2222 | 2.8356 | 15666.6667 | 2.3222 | 6746.4115 | 2.5243 | 14922.2222 | 2.2722 | 6567.2372 | 2.2791 | 14166.6667 | 2.1722 | 6521.7391 | 2.0163
|  | 8454.5455 | 40.4086 | nom | 14000 | 3.2444 | 4315.0685 | 2284.9278 | 14000 | 2.9944 | 4675.3247 | 2691.5008 | 14000 | 2.7444 | 5101.2146 | 2981.5496 | 14000 | 2.4944 | 5612.4722 | 3349.2977 | 14000 | 2.3722 | 5901.6393 | 3709.6087 | 14000 | 2.2 | 6363.6364 | 4193.1024
|  |  | 100 | mid | 11200 | 3.4722 | 3225.6 | 1 | 11200 | 3.2222 | 3475.8621 | 1 | 11200 | 2.9722 | 3768.2243 | 1 | 11200 | 2.7222 | 4114.2857 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1
|  |  | 3008.5468 | min | 5377.7778 | 3.9556 | 1359.5506 | 0.52845 | 4611.1111 | 3.0278 | 1522.9358 | 0.58332 | 4388.8889 | 2.6333 | 1666.6667 | 0.59692 | 4111.1111 | 2.2111 | 1859.2965 | 0.61271 | 3655.5556 | 1.8056 | 2024.6154 | 0.6361 | 3155.5556 | 1.3722 | 2299.5951 | 0.65871
| -1 |  | 2.9219 | max | 16366.6667 | 3.0667 | 5336.9565 | 3.7914 | 16166.6667 | 2.8333 | 5705.8824 | 3.2258 | 15900 | 2.6 | 6115.3846 | 2.8912 | 15700 | 2.3667 | 6633.8028 | 2.55 | 14966.6667 | 2.3167 | 6460.4317 | 2.2916 | 14200 | 2.2167 | 6406.015 | 2.0122
|  | 8031.8182 | 39.5417 | nom | 14000 | 3.2833 | 4263.9594 | 2118.4505 | 14000 | 3.0333 | 4615.3846 | 2489.8381 | 14000 | 2.7833 | 5029.9401 | 2778.028 | 14000 | 2.5333 | 5526.3158 | 3149.7635 | 14000 | 2.4167 | 5793.1034 | 3504.9062 | 14000 | 2.25 | 6222.2222 | 3991.5734
|  |  | 100 | mid | 11200 | 3.5167 | 3184.8341 | 1 | 11200 | 3.2667 | 3428.5714 | 1 | 11200 | 3.0167 | 3712.7072 | 1 | 11200 | 2.7667 | 4048.1928 | 1 | 11200 | 2.6 | 4307.6923 | 1 | 11200 | 2.4 | 4666.6667 | 1
|  |  | 2748.8636 | min | 5433.3333 | 4.0167 | 1352.6971 | 0.4506 | 4733.3333 | 3.1833 | 1486.911 | 0.51007 | 4466.6667 | 2.75 | 1624.2424 | 0.52948 | 4133.3333 | 2.2833 | 1810.219 | 0.55167 | 3666.6667 | 1.8667 | 1964.2857 | 0.57944 | 3166.6667 | 1.4167 | 2235.2941 | 0.60562
| 0 |  | 3.0552 | max | 16411.1111 | 3.1278 | 5246.8917 | 3.886 | 16211.1111 | 2.8889 | 5611.5385 | 3.3268 | 15933.3333 | 2.65 | 6012.5786 | 2.9562 | 15733.3333 | 2.4111 | 6525.3456 | 2.5789 | 15011.1111 | 2.3611 | 6357.6471 | 2.3052 | 14233.3333 | 2.2611 | 6294.8403 | 2.0074
|  | 7609.0909 | 38.6641 | nom | 14000 | 3.3222 | 4214.0468 | 1958.0933 | 14000 | 3.0722 | 4556.962 | 2287.1874 | 14000 | 2.8222 | 4960.6299 | 2573.942 | 14000 | 2.5722 | 5442.7646 | 2950.5278 | 14000 | 2.4611 | 5688.4876 | 3300.7943 | 14000 | 2.3 | 6086.9565 | 3790.6087
|  |  | 100 | mid | 11200 | 3.5611 | 3145.0858 | 1 | 11200 | 3.3111 | 3382.5503 | 1 | 11200 | 3.0611 | 3658.8022 | 1 | 11200 | 2.8111 | 3984.1897 | 1 | 11200 | 2.65 | 4226.4151 | 1 | 11200 | 2.45 | 4571.4286 | 1
|  |  | 2490.5183 | min | 5488.8889 | 4.0778 | 1346.049 | 0.37124 | 4855.5556 | 3.3389 | 1454.2429 | 0.43401 | 4544.4444 | 2.8667 | 1585.2713 | 0.46046 | 4155.5556 | 2.3556 | 1764.1509 | 0.49025 | 3677.7778 | 1.9278 | 1907.781 | 0.52263 | 3177.7778 | 1.4611 | 2174.9049 | 0.55238
| 1 |  | 3.2153 | max | 16455.5556 | 3.1889 | 5160.2787 | 3.9841 | 16255.5556 | 2.9444 | 5520.7547 | 3.4451 | 15966.6667 | 2.7 | 5913.5802 | 3.031 | 15766.6667 | 2.4556 | 6420.8145 | 2.6111 | 15055.5556 | 2.4056 | 6258.6605 | 2.32 | 14266.6667 | 2.3056 | 6187.9518 | 2.0018
|  | 7186.3636 | 37.7753 | nom | 14000 | 3.3611 | 4165.2893 | 1803.7827 | 14000 | 3.1111 | 4500 | 2085.939 | 14000 | 2.8611 | 4893.2039 | 2370.972 | 14000 | 2.6111 | 5361.7021 | 2752.2846 | 14000 | 2.5056 | 5587.5831 | 3097.5562 | 14000 | 2.35 | 5957.4468 | 3589.9963
|  |  | 100 | mid | 11200 | 3.6056 | 3106.3174 | 1 | 11200 | 3.3556 | 3337.7483 | 1 | 11200 | 3.1056 | 3606.4401 | 1 | 11200 | 2.8556 | 3922.179 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.5 | 4480 | 1
|  |  | 2235.0796 | min | 5544.4444 | 4.1389 | 1339.5973 | 0.29032 | 4977.7778 | 3.4944 | 1424.4833 | 0.35495 | 4622.2222 | 2.9833 | 1549.3482 | 0.38982 | 4177.7778 | 2.4278 | 1720.8238 | 0.42844 | 3688.8889 | 1.9889 | 1854.7486 | 0.46564 | 3188.8889 | 1.5056 | 2118.0812 | 0.49899
14kW-Maximum heating CAP | 2 |  | 3.4072 | max | 16500 | 3.25 | 5076.9231 | 4.0857 | 16300 | 3 | 5433.3333 | 3.5818 | 16000 | 2.75 | 5818.1818 | 3.1159 | 15800 | 2.5 | 6320 | 2.6465 | 15100 | 2.45 | 6163.2653 | 2.3359 | 14300 | 2.35 | 6085.1064 | 1.9955
|  | 6763.6364 | 36.8742 | nom | 14000 | 3.4 | 4117.6471 | 1655.4355 | 14000 | 3.15 | 4444.4444 | 1888.3249 | 14000 | 2.9 | 4827.5862 | 2170.7027 | 14000 | 2.65 | 5283.0189 | 2555.6973 | 14000 | 2.55 | 5490.1961 | 2895.4674 | 14000 | 2.4 | 5833.3333 | 3389.5216
|  |  | 100 | mid | 11200 | 3.65 | 3068.4932 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 3.15 | 3555.5556 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.55 | 4392.1569 | 1
|  |  | 1985.1238 | min | 5600 | 4.2 | 1333.3333 | 0.20779 | 5100 | 3.65 | 1397.2603 | 0.27273 | 4700 | 3.1 | 1516.129 | 0.31748 | 4200 | 2.5 | 1680 | 0.36623 | 3700 | 2.05 | 1804.878 | 0.40848 | 3200 | 1.55 | 2064.5161 | 0.44545
| 3 |  | 3.6763 | max | 16560 | 3.54 | 4677.9661 | 4.5628 | 16360 | 3.25 | 5033.8462 | 3.7806 | 16080 | 2.96 | 5432.4324 | 3.2377 | 15860 | 2.66 | 5962.406 | 2.6986 | 15160 | 2.54 | 5968.5039 | 2.3499 | 14360 | 2.38 | 6033.6134 | 1.9741
|  | 6340.9091 | 35.9601 | nom | 14000 | 3.7 | 3783.7838 | 1389.7043 | 14000 | 3.41 | 4105.5718 | 1677.229 | 14000 | 3.12 | 4487.1795 | 1958.4609 | 14000 | 2.82 | 4964.539 | 2349.7265 | 14000 | 2.67 | 5243.4457 | 2698.3541 | 14000 | 2.47 | 5668.0162 | 3212.0564
|  |  | 100 | mid | 11200 | 3.97 | 2821.1587 | 1 | 11200 | 3.68 | 3043.4783 | 1 | 11200 | 3.39 | 3303.8348 | 1 | 11200 | 3.09 | 3624.5955 | 1 | 11200 | 2.88 | 3888.8889 | 1 | 11200 | 2.62 | 4274.8092 | 1
|  |  | 1724.7878 | min | 5380 | 4.68 | 1149.5726 | 0.1651 | 4920 | 3.81 | 1291.3386 | 0.22626 | 4500 | 3.18 | 1415.0943 | 0.27476 | 4000 | 2.51 | 1593.6255 | 0.32513 | 3500 | 2.04 | 1715.6863 | 0.36895 | 3000 | 1.53 | 1960.7843 | 0.40743
| 4 |  | 3.9642 | max | 16620 | 3.83 | 4339.4256 | 5.0508 | 16420 | 3.5 | 4691.4286 | 3.9682 | 16160 | 3.17 | 5097.7918 | 3.3468 | 15920 | 2.82 | 5645.3901 | 2.7375 | 15220 | 2.63 | 5787.0722 | 2.3548 | 14420 | 2.41 | 5983.4025 | 1.948
|  | 5918.1818 | 35.0318 | nom | 14000 | 4 | 3500 | 1171.7335 | 14000 | 3.67 | 3814.7139 | 1491.4111 | 14000 | 3.34 | 4191.6168 | 1768.3253 | 14000 | 2.99 | 4682.2742 | 2161.8589 | 14000 | 2.79 | 5017.9211 | 2513.2556 | 14000 | 2.54 | 5511.811 | 3038.0338
|  |  | 100 | mid | 11200 | 4.29 | 2610.7226 | 1 | 11200 | 3.96 | 2828.2828 | 1 | 11200 | 3.63 | 3085.3994 | 1 | 11200 | 3.28 | 3414.6341 | 1 | 11200 | 3.01 | 3720.9302 | 1 | 11200 | 2.69 | 4163.5688 | 1
|  |  | 1492.897 | min | 5160 | 5.16 | 1000 | 0.12553 | 4740 | 3.97 | 1193.9547 | 0.18238 | 4300 | 3.26 | 1319.0184 | 0.23452 | 3800 | 2.52 | 1507.9365 | 0.28624 | 3300 | 2.03 | 1625.6158 | 0.33142 | 2800 | 1.51 | 1854.3046 | 0.37121
| 5 |  | 4.2735 | max | 16680 | 4.12 | 4048.5437 | 5.5486 | 16480 | 3.75 | 4394.6667 | 4.1455 | 16240 | 3.38 | 4804.7337 | 3.4442 | 15980 | 2.98 | 5362.4161 | 2.7644 | 15280 | 2.72 | 5617.6471 | 2.3512 | 14480 | 2.44 | 5934.4262 | 1.9176
|  | 5495.4545 | 34.088 | nom | 14000 | 4.3 | 3255.814 | 990.4205 | 14000 | 3.93 | 3562.341 | 1325.6443 | 14000 | 3.56 | 3932.5843 | 1595.5827 | 14000 | 3.16 | 4430.3797 | 1987.9104 | 14000 | 2.91 | 4810.9966 | 2337.2746 | 14000 | 2.61 | 5363.9847 | 2865.8212
|  |  | 100 | mid | 11200 | 4.61 | 2429.5011 | 1 | 11200 | 4.24 | 2641.5094 | 1 | 11200 | 3.87 | 2894.0568 | 1 | 11200 | 3.47 | 3227.6657 | 1 | 11200 | 3.14 | 3566.879 | 1 | 11200 | 2.76 | 4057.971 | 1
|  |  | 1285.9503 | min | 4940 | 5.64 | 875.8865 | 0.088731 | 4560 | 4.13 | 1104.1162 | 0.14088 | 4100 | 3.34 | 1227.5449 | 0.19654 | 3600 | 2.53 | 1422.9249 | 0.2494 | 3100 | 2.02 | 1534.6535 | 0.29574 | 2600 | 1.49 | 1744.9664 | 0.33668
| 6 |  | 4.6396 | max | 16740 | 4.41 | 3795.9184 | 6.0552 | 16540 | 4 | 4135 | 4.3134 | 16320 | 3.59 | 4545.961 | 3.5308 | 16040 | 3.14 | 5108.2803 | 2.7802 | 15340 | 2.81 | 5459.0747 | 2.3398 | 14540 | 2.47 | 5886.6397 | 1.8831
|  | 5072.7273 | 33.1273 | nom | 14000 | 4.6 | 3043.4783 | 837.7439 | 14000 | 4.19 | 3341.2888 | 1176.0496 | 14000 | 3.78 | 3703.7037 | 1436.6886 | 14000 | 3.33 | 4204.2042 | 1824.5996 | 14000 | 3.03 | 4620.462 | 2167.9844 | 14000 | 2.68 | 5223.8806 | 2693.8776
|  |  | 100 | mid | 11200 | 4.93 | 2271.8053 | 1 | 11200 | 4.52 | 2477.8761 | 1 | 11200 | 4.11 | 2725.0608 | 1 | 11200 | 3.66 | 3060.1093 | 1 | 11200 | 3.27 | 3425.0765 | 1 | 11200 | 2.83 | 3957.5972 | 1
|  |  | 1093.3654 | min | 4720 | 6.12 | 771.2418 | 0.054433 | 4380 | 4.29 | 1020.979 | 0.10157 | 3900 | 3.42 | 1140.3509 | 0.16065 | 3400 | 2.54 | 1338.5827 | 0.21445 | 2900 | 2.01 | 1442.7861 | 0.26177 | 2400 | 1.47 | 1632.6531 | 0.30372
| 7 |  | 5.0706 | max | 16800 | 4.7 | 3574.4681 | 6.5698 | 16600 | 4.25 | 3905.8824 | 4.4725 | 16400 | 3.8 | 4315.7895 | 3.6077 | 16100 | 3.3 | 4878.7879 | 2.7856 | 15400 | 2.9 | 5310.3448 | 2.3212 | 14600 | 2.5 | 5840 | 1.8447
|  | 4650 | 32.148 | nom | 14000 | 4.9 | 2857.1429 | 707.7867 | 14000 | 4.45 | 3146.0674 | 1039.687 | 14000 | 4 | 3500 | 1288.9217 | 14000 | 3.5 | 4000 | 1669.2843 | 14000 | 3.15 | 4444.4444 | 2003.2945 | 14000 | 2.75 | 5090.9091 | 2520.7047
|  |  | 100 | mid | 11200 | 5.25 | 2133.3333 | 1 | 11200 | 4.8 | 2333.3333 | 1 | 11200 | 4.35 | 2574.7126 | 1 | 11200 | 3.85 | 2909.0909 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 2.9 | 3862.069 | 1
|  |  | 917.0426 | min | 4500 | 6.6 | 681.8182 | 0.022388 | 4200 | 4.45 | 943.8202 | 0.064286 | 3700 | 3.5 | 1057.1429 | 0.12667 | 3200 | 2.55 | 1254.902 | 0.18125 | 2700 | 2 | 1350 | 0.22941 | 2200 | 1.45 | 1517.2414 | 0.27222
| 8 |  | 5.2218 | max | 16860 | 4.81 | 3505.1975 | 6.31 | 16640 | 4.38 | 3799.0868 | 4.54 | 16440 | 3.93 | 4183.2061 | 3.7421 | 16160 | 3.48 | 4643.6782 | 2.9993 | 15440 | 3.06 | 5045.7516 | 2.4992 | 14640 | 2.64 | 5545.4545 | 1.9943
|  | 4227.2727 | 31.1478 | nom | 14000 | 5.02 | 2788.8446 | 669.9323 | 14000 | 4.59 | 3050.1089 | 931.1173 | 14000 | 4.16 | 3365.3846 | 1129.6461 | 14000 | 3.69 | 3794.0379 | 1409.4039 | 14000 | 3.32 | 4216.8675 | 1691.4319 | 14000 | 2.9 | 4827.5862 | 2119.7165
|  |  | 89.4989 | mid | 11200 | 5.37 | 2085.6611 | 0 | 11200 | 4.95 | 2262.6263 | 0 | 11200 | 4.53 | 2472.4062 | 1 | 11200 | 4.06 | 2758.6207 | 1 | 11200 | 3.58 | 3128.4916 | 1 | 11200 | 3.06 | 3660.1307 | 1
|  |  | 809.5377 | min | 4920 | 6.31 | 779.7147 | 0 | 4600 | 4.54 | 1013.2159 | 0 | 4120 | 3.73 | 1104.5576 | 0.015152 | 3640 | 2.91 | 1250.8591 | 0.077682 | 3200 | 2.34 | 1367.5214 | 0.12841 | 2760 | 1.77 | 1559.322 | 0.17385
| 9 |  | 5.3077 | max | 16920 | 4.92 | 3439.0244 | 6.02 | 16680 | 4.51 | 3698.4479 | 4.63 | 16480 | 4.06 | 4059.1133 | 3.96 | 16220 | 3.66 | 4431.694 | 3.27 | 15480 | 3.22 | 4807.4534 | 2.6951 | 14680 | 2.78 | 5280.5755 | 2.1595
|  | 3804.5455 | 30.1243 | nom | 14000 | 5.14 | 2723.7354 | 631.9843 | 14000 | 4.73 | 2959.8309 | 821.7161 | 14000 | 4.32 | 3240.7407 | 960.7438 | 14000 | 3.88 | 3608.2474 | 1163.4696 | 14000 | 3.49 | 4011.4613 | 1411.6766 | 14000 | 3.05 | 4590.1639 | 1761.7843
|  |  | 73.6491 | mid | 11200 | 5.49 | 2040.0729 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.71 | 2377.9193 | 0 | 11200 | 4.27 | 2622.9508 | 0 | 11200 | 3.76 | 2978.7234 | 1 | 11200 | 3.22 | 3478.2609 | 1
|  |  | 716.7939 | min | 5340 | 6.02 | 887.0432 | 0 | 5000 | 4.63 | 1079.9136 | 0 | 4540 | 3.96 | 1146.4646 | 0 | 4080 | 3.27 | 1247.7064 | 0 | 3700 | 2.68 | 1380.597 | 0.013939 | 3320 | 2.09 | 1588.5167 | 0.061491
| 10 |  | 5.3185 | max | 16980 | 5.03 | 3375.7455 | 5.73 | 16720 | 4.64 | 3603.4483 | 4.72 | 16520 | 4.19 | 3942.7208 | 4.19 | 16280 | 3.84 | 4239.5833 | 3.63 | 15520 | 3.38 | 4591.716 | 3.02 | 14720 | 2.92 | 5041.0959 | 2.41
|  | 3381.8182 | 29.0741 | nom | 14000 | 5.26 | 2661.597 | 590.1951 | 14000 | 4.87 | 2874.7433 | 716.4869 | 14000 | 4.48 | 3125 | 807.1165 | 14000 | 4.07 | 3439.8034 | 931.6304 | 14000 | 3.66 | 3825.1366 | 1119.8073 | 14000 | 3.2 | 4375 | 1403.2441
|  |  | 60.2462 | mid | 11200 | 5.61 | 1996.4349 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.89 | 2290.3885 | 0 | 11200 | 4.48 | 2500 | 0 | 11200 | 3.94 | 2842.6396 | 0 | 11200 | 3.38 | 3313.6095 | 0
|  |  | 635.8573 | min | 5760 | 5.73 | 1005.2356 | 0 | 5400 | 4.72 | 1144.0678 | 0 | 4960 | 4.19 | 1183.7709 | 0 | 4520 | 3.63 | 1245.1791 | 0 | 4200 | 3.02 | 1390.7285 | 0 | 3880 | 2.41 | 1609.9585 | 0
| 11 |  | 5.2514 | max | 17040 | 5.14 | 3315.1751 | 5.44 | 16760 | 4.77 | 3513.6268 | 4.81 | 16560 | 4.32 | 3833.3333 | 4.42 | 16340 | 4.02 | 4064.6766 | 3.99 | 15560 | 3.54 | 4395.4802 | 3.36 | 14760 | 3.06 | 4823.5294 | 2.73
|  | 2959.0909 | 27.9931 | nom | 14000 | 5.38 | 2602.2305 | 543.9505 | 14000 | 5.01 | 2794.4112 | 615.1956 | 14000 | 4.64 | 3017.2414 | 669.4776 | 14000 | 4.26 | 3286.385 | 741.6268 | 14000 | 3.83 | 3655.3525 | 880.6818 | 14000 | 3.35 | 4179.1045 | 1083.9161
|  |  | 48.7795 | mid | 11200 | 5.73 | 1954.6248 | 0 | 11200 | 5.4 | 2074.0741 | 0 | 11200 | 5.07 | 2209.073 | 0 | 11200 | 4.69 | 2388.0597 | 0 | 11200 | 4.12 | 2718.4466 | 0 | 11200 | 3.54 | 3163.8418 | 0
|  |  | 563.4821 | min | 6180 | 5.44 | 1136.0294 | 0 | 5800 | 4.81 | 1205.8212 | 0 | 5380 | 4.42 | 1217.1946 | 0 | 4960 | 3.99 | 1243.1078 | 0 | 4700 | 3.36 | 1398.8095 | 0 | 4440 | 2.73 | 1626.3736 | 0
| 12 |  | 5.1031 | max | 17100 | 5.25 | 3257.1429 | 5.15 | 16800 | 4.9 | 3428.5714 | 4.9 | 16600 | 4.45 | 3730.3371 | 4.65 | 16400 | 4.2 | 3904.7619 | 4.35 | 15600 | 3.7 | 4216.2162 | 3.7 | 14800 | 3.2 | 4625 | 3.05
|  | 2536.3636 | 26.8757 | nom | 14000 | 5.5 | 2545.4545 | 492.4978 | 14000 | 5.15 | 2718.4466 | 517.6252 | 14000 | 4.8 | 2916.6667 | 545.4545 | 14000 | 4.45 | 3146.0674 | 583.0721 | 14000 | 4 | 3500 | 685.5037 | 14000 | 3.5 | 4000 | 831.5946
|  |  | 38.8716 | mid | 11200 | 5.85 | 1914.5299 | 0 | 11200 | 5.55 | 2018.018 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.9 | 2285.7143 | 0 | 11200 | 4.3 | 2604.6512 | 0 | 11200 | 3.7 | 3027.027 | 0
|  |  | 497.0233 | min | 6600 | 5.15 | 1281.5534 | 0 | 6200 | 4.9 | 1265.3061 | 0 | 5800 | 4.65 | 1247.3118 | 0 | 5400 | 4.35 | 1241.3793 | 0 | 5200 | 3.7 | 1405.4054 | 0 | 5000 | 3.05 | 1639.3443 | 0
| 13 |  | 5.1369 | max | 17566.6667 | 5.2833 | 3324.9211 | 5.15 | 17266.6667 | 4.9333 | 3500 | 4.9667 | 17033.3333 | 4.55 | 3743.5897 | 4.7833 | 16833.3333 | 4.3 | 3914.7287 | 4.55 | 16033.3333 | 3.8 | 4219.2982 | 3.9167 | 15200 | 3.3 | 4606.0606 | 3.2667
|  | 2113.6364 | 25.7142 | nom | 14000 | 5.5 | 2545.4545 | 410.4148 | 14000 | 5.1833 | 2700.9646 | 425.5644 | 14000 | 4.8667 | 2876.7123 | 441.8752 | 14000 | 4.55 | 3076.9231 | 464.5355 | 14000 | 4.1 | 3414.6341 | 539.6518 | 14000 | 3.6167 | 3870.9677 | 647.0315
|  |  | 31.6932 | mid | 11200 | 5.9 | 1898.3051 | 0 | 11200 | 5.5833 | 2005.9701 | 0 | 11200 | 5.3167 | 2106.5831 | 0 | 11200 | 5.0167 | 2232.5581 | 0 | 11200 | 4.4167 | 2535.8491 | 0 | 11200 | 3.8167 | 2934.4978 | 0
|  |  | 411.461 | min | 6700 | 5.15 | 1300.9709 | 0 | 6266.6667 | 4.9667 | 1261.745 | 0 | 5833.3333 | 4.7833 | 1219.5122 | 0 | 5400 | 4.55 | 1186.8132 | 0 | 5233.3333 | 3.9167 | 1336.1702 | 0 | 5066.6667 | 3.2667 | 1551.0204 | 0
| 14 |  | 5.15 | max | 18033.3333 | 5.3167 | 3391.8495 | 5.15 | 17733.3333 | 4.9667 | 3570.4698 | 5.0333 | 17466.6667 | 4.65 | 3756.2724 | 4.9167 | 17266.6667 | 4.4 | 3924.2424 | 4.75 | 16466.6667 | 3.9 | 4222.2222 | 4.1333 | 15600 | 3.4 | 4588.2353 | 3.4833
|  | 1690.9091 | 24.4975 | nom | 14000 | 5.5 | 2545.4545 | 328.3319 | 14000 | 5.2167 | 2683.7061 | 335.9422 | 14000 | 4.9333 | 2837.8378 | 343.9137 | 14000 | 4.65 | 3010.7527 | 355.9809 | 14000 | 4.2 | 3333.3333 | 409.0909 | 14000 | 3.7333 | 3750 | 485.4284
|  |  | 24.8663 | mid | 11200 | 5.95 | 1882.3529 | 0 | 11200 | 5.6167 | 1994.0653 | 0 | 11200 | 5.3833 | 2080.4954 | 0 | 11200 | 5.1333 | 2181.8182 | 0 | 11200 | 4.5333 | 2470.5882 | 0 | 11200 | 3.9333 | 2847.4576 | 0
|  |  | 328.3319 | min | 6800 | 5.15 | 1320.3883 | 0 | 6333.3333 | 5.0333 | 1258.2781 | 0 | 5866.6667 | 4.9167 | 1193.2203 | 0 | 5400 | 4.75 | 1136.8421 | 0 | 5266.6667 | 4.1333 | 1274.1935 | 0 | 5133.3333 | 3.4833 | 1473.6842 | 0
| 15 |  | 5.15 | max | 18500 | 5.35 | 3457.9439 | 5.15 | 18200 | 5 | 3640 | 5.1 | 17900 | 4.75 | 3768.4211 | 5.05 | 17700 | 4.5 | 3933.3333 | 4.95 | 16900 | 4 | 4225 | 4.35 | 16000 | 3.5 | 4571.4286 | 3.7
|  | 1268.1818 | 23.2076 | nom | 14000 | 5.5 | 2545.4545 | 246.2489 | 14000 | 5.25 | 2666.6667 | 248.6631 | 14000 | 5 | 2800 | 251.1251 | 14000 | 4.75 | 2947.3684 | 256.1983 | 14000 | 4.3 | 3255.814 | 291.5361 | 14000 | 3.85 | 3636.3636 | 342.7518
|  |  | 18.3794 | mid | 11200 | 6 | 1866.6667 | 0 | 11200 | 5.65 | 1982.3009 | 0 | 11200 | 5.45 | 2055.0459 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.65 | 2408.6022 | 0 | 11200 | 4.05 | 2765.4321 | 0
|  |  | 246.2489 | min | 6900 | 5.15 | 1339.8058 | 0 | 6400 | 5.1 | 1254.902 | 0 | 5900 | 5.05 | 1168.3168 | 0 | 5400 | 4.95 | 1090.9091 | 0 | 5300 | 4.35 | 1218.3908 | 0 | 5200 | 3.7 | 1405.4054 | 0
| 16 |  | 6.92 | max | 19020 | 5.73 | 3319.3717 | 6.92 | 18720 | 5.3 | 3532.0755 | 5.68 | 18420 | 4.95 | 3721.2121 | 5.37 | 18200 | 4.59 | 3965.1416 | 5.02 | 17380 | 4.08 | 4259.8039 | 4.36 | 16460 | 3.56 | 4623.5955 | 3.65
|  | 845.4545 | 21.8123 | nom | 14000 | 5.93 | 2360.8769 | 122.1755 | 14000 | 5.57 | 2513.465 | 148.8476 | 14000 | 5.21 | 2687.1401 | 157.4403 | 14000 | 4.85 | 2886.5979 | 168.4172 | 14000 | 4.39 | 3189.0661 | 193.9116 | 14000 | 3.92 | 3571.4286 | 231.6314
|  |  | 12.1125 | mid | 11200 | 6.42 | 1744.5483 | 0 | 11200 | 5.99 | 1869.783 | 0 | 11200 | 5.68 | 1971.831 | 0 | 11200 | 5.36 | 2089.5522 | 0 | 11200 | 4.74 | 2362.8692 | 0 | 11200 | 4.12 | 2718.4466 | 0
|  |  | 122.1755 | min | 6980 | 6.92 | 1008.6705 | 0 | 6460 | 5.68 | 1137.3239 | 0 | 6000 | 5.37 | 1117.3184 | 0 | 5520 | 5.02 | 1099.6016 | 0 | 5360 | 4.36 | 1229.3578 | 0 | 5180 | 3.65 | 1419.1781 | 0
| 17 |  | 8.69 | max | 19540 | 6.11 | 3198.036 | 8.69 | 19240 | 5.6 | 3435.7143 | 6.26 | 18940 | 5.15 | 3677.6699 | 5.69 | 18700 | 4.68 | 3995.7265 | 5.09 | 17860 | 4.16 | 4293.2692 | 4.37 | 16920 | 3.62 | 4674.0331 | 3.6
|  | 422.7273 | 20.2368 | nom | 14000 | 6.36 | 2201.2579 | 48.6453 | 14000 | 5.89 | 2376.91 | 67.5283 | 14000 | 5.42 | 2583.0258 | 74.293 | 14000 | 4.95 | 2828.2828 | 83.0505 | 14000 | 4.48 | 3125 | 96.7339 | 14000 | 3.99 | 3508.7719 | 117.4242
|  |  | 5.9876 | mid | 11200 | 6.84 | 1637.4269 | 0 | 11200 | 6.33 | 1769.3523 | 0 | 11200 | 5.91 | 1895.0931 | 0 | 11200 | 5.47 | 2047.532 | 0 | 11200 | 4.83 | 2318.8406 | 0 | 11200 | 4.19 | 2673.031 | 0
|  |  | 48.6453 | min | 7060 | 8.69 | 812.4281 | 0 | 6520 | 6.26 | 1041.5335 | 0 | 6100 | 5.69 | 1072.0562 | 0 | 5640 | 5.09 | 1108.055 | 0 | 5420 | 4.37 | 1240.2746 | 0 | 5160 | 3.6 | 1433.3333 | 0
| 18 |  | 10.46 | max | 20060 | 6.49 | 3090.9091 | 10.46 | 19760 | 5.9 | 3349.1525 | 6.84 | 19460 | 5.35 | 3637.3832 | 6.01 | 19200 | 4.77 | 4025.1572 | 5.16 | 18340 | 4.24 | 4325.4717 | 4.38 | 17380 | 3.68 | 4722.8261 | 3.55
|  | 0 | 18 | nom | 14000 | 6.79 | 2061.8557 | 0 | 14000 | 6.21 | 2254.4283 | 0 | 14000 | 5.63 | 2486.6785 | 0 | 14000 | 5.05 | 2772.2772 | 0 | 14000 | 4.57 | 3063.4573 | 0 | 14000 | 4.06 | 3448.2759 | 0
|  |  | 0 | mid | 11200 | 7.26 | 1542.6997 | 0 | 11200 | 6.67 | 1679.1604 | 0 | 11200 | 6.14 | 1824.1042 | 0 | 11200 | 5.58 | 2007.1685 | 0 | 11200 | 4.92 | 2276.4228 | 0 | 11200 | 4.26 | 2629.108 | 0
|  |  | 0 | min | 7140 | 10.46 | 682.6004 | 0 | 6580 | 6.84 | 961.9883 | 0 | 6200 | 6.01 | 1031.614 | 0 | 5760 | 5.16 | 1116.2791 | 0 | 5480 | 4.38 | 1251.1416 | 0 | 5140 | 3.55 | 1447.8873 | 0
| 19 |  | #NUM! | max | 20580 | 6.87 | 2995.6332 | 12.23 | 20280 | 6.2 | 3270.9677 | 7.42 | 19980 | 5.55 | 3600 | 6.33 | 19700 | 4.86 | 4053.4979 | 5.23 | 18820 | 4.32 | 4356.4815 | 4.39 | 17840 | 3.74 | 4770.0535 | 3.5
|  | -422.7273 | #NUM! | nom | 14000 | 7.22 | 1939.0582 | -34.5648 | 14000 | 6.53 | 2143.951 | -56.9713 | 14000 | 5.84 | 2397.2603 | -66.7816 | 14000 | 5.15 | 2718.4466 | -80.8274 | 14000 | 4.66 | 3004.2918 | -96.2932 | 14000 | 4.13 | 3389.8305 | -120.7792
|  |  |  | mid | 11200 | 7.68 | 1458.3333 | 0 | 11200 | 7.01 | 1597.7175 | 0 | 11200 | 6.37 | 1758.2418 | 0 | 11200 | 5.69 | 1968.3656 | 0 | 11200 | 5.01 | 2235.5289 | 0 | 11200 | 4.33 | 2586.6051 | 0
|  |  | #NUM! | min | 7220 | 12.23 | 590.3516 | 0 | 6640 | 7.42 | 894.8787 | 0 | 6300 | 6.33 | 995.2607 | 0 | 5880 | 5.23 | 1124.283 | 0 | 5540 | 4.39 | 1261.959 | 0 | 5120 | 3.5 | 1462.8571 | 0
| 20 |  | #NUM! | max | 21100 | 7.25 | 2910.3448 | 14 | 20800 | 6.5 | 3200 | 8 | 20500 | 5.75 | 3565.2174 | 6.65 | 20200 | 4.95 | 4080.8081 | 5.3 | 19300 | 4.4 | 4386.3636 | 4.4 | 18300 | 3.8 | 4815.7895 | 3.45
|  | -845.4545 | #NUM! | nom | 14000 | 7.65 | 1830.0654 | -60.3896 | 14000 | 6.85 | 2043.7956 | -105.6818 | 14000 | 6.05 | 2314.0496 | -127.136 | 14000 | 5.25 | 2666.6667 | -159.5197 | 14000 | 4.75 | 2947.3684 | -192.1488 | 14000 | 4.2 | 3333.3333 | -245.0593
|  |  |  | mid | 11200 | 8.1 | 1382.716 | 0 | 11200 | 7.35 | 1523.8095 | 0 | 11200 | 6.6 | 1696.9697 | 0 | 11200 | 5.8 | 1931.0345 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.4 | 2545.4545 | 0
|  |  | #NUM! | min | 7300 | 14 | 521.4286 | 0 | 6700 | 8 | 837.5 | 0 | 6400 | 6.65 | 962.406 | 0 | 6000 | 5.3 | 1132.0755 | 0 | 5600 | 4.4 | 1272.7273 | 0 | 5100 | 3.45 | 1478.2609 | 0
Indoor Temp. |  | 19
LWT |  |  | 25 CAP: 25; 35 CAP: 35; 40 CAP: 40; 45 CAP: 45; 50 CAP: 50; 55 CAP: 55
Outdoor air temperature[℃] |  | Heating Demand | COP | CL | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP
|  |  | LWT |  |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI
| -15 |  | 0.92248 | max | - | - | - | - | 14000 | 1.85 | 7567.5676 | 1.7941 | 13500 | 1.7 | 7941.1765 | 1.5604 | 13100 | 1.55 | 8451.6129 | 1.3379 | 12600 | 1.45 | 8689.6552 | 1.1176 | 12200 | 1.3 | 9384.6154 | 0.75682
|  | 14372.7273 | 52.7042 | nom | - | - | - | - | 11000 | 2.3 | 4782.6087 | 8011.1477 | 11000 | 2.1 | 5238.0952 | 9211.1396 | 11000 | 1.9 | 5789.4737 | 10742.9219 | 11000 | 1.75 | 6285.7143 | 12860.1932 | 11000 | 1.6 | 6875 | 18990.991
|  |  | 100 | mid | - | - | - | - | 8800 | 2.5 | 3520 | 3 | 8800 | 2.3 | 3826.087 | 3 | 8800 | 2.1 | 4190.4762 | 3 | 8800 | 1.9 | 4631.5789 | 3 | 8800 | 1.7 | 5176.4706 | 3
|  |  | 15580.4922 | min | - | - | - | - | 7800 | 2.35 | 3319.1489 | 1.1242 | 7200 | 2 | 3600 | 1.3491 | 6500 | 1.6 | 4062.5 | 1.6061 | 5700 | 1.3 | 4384.6154 | 2.108 | 4800 | 1 | 4800 | 2.8106
| -14 |  | 1.7183 | max | 14280 | 2.08 | 6865.3846 | 2.6409 | 14080 | 1.93 | 7295.3368 | 2.3436 | 13640 | 1.78 | 7662.9213 | 2.1241 | 13280 | 1.62 | 8197.5309 | 1.9045 | 12880 | 1.53 | 8418.3007 | 1.773 | 12560 | 1.39 | 9035.9712 | 1.6318
|  | 13950 | 51.939 | nom | 14000 | 2.64 | 5303.0303 | 5282.3044 | 14000 | 2.34 | 5982.906 | 5952.4535 | 14000 | 2.12 | 6603.7736 | 6567.4653 | 14000 | 1.9 | 7368.4211 | 7324.8945 | 14000 | 1.77 | 7909.6045 | 7867.8618 | 14000 | 1.63 | 8588.9571 | 8548.9166
|  |  | 100 | mid | 11200 | 2.69 | 4163.5688 | 2 | 11200 | 2.54 | 4409.4488 | 2 | 11200 | 2.35 | 4765.9574 | 2 | 11200 | 2.15 | 5209.3023 | 2 | 11200 | 1.94 | 5773.1959 | 2 | 11200 | 1.73 | 6473.9884 | 2
|  |  | 8118.6865 | min | 7720 | 2.59 | 2980.695 | 0.98214 | 7420 | 2.34 | 3170.9402 | 0.98214 | 6880 | 2.01 | 3422.8856 | 0.98214 | 6260 | 1.63 | 3840.4908 | 0.98214 | 5480 | 1.33 | 4120.3008 | 0.98214 | 4640 | 1.02 | 4549.0196 | 0.98214
| -13 |  | 1.7881 | max | 14360 | 2.16 | 6648.1481 | 2.6884 | 14160 | 2.01 | 7044.7761 | 2.4138 | 13780 | 1.86 | 7408.6022 | 2.1839 | 13460 | 1.69 | 7964.497 | 1.9506 | 13160 | 1.61 | 8173.913 | 1.8221 | 12920 | 1.48 | 8729.7297 | 1.6769
|  | 13527.2727 | 51.1685 | nom | 14000 | 2.68 | 5223.8806 | 5031.641 | 14000 | 2.38 | 5882.3529 | 5604.2182 | 14000 | 2.14 | 6542.0561 | 6194.1009 | 14000 | 1.9 | 7368.4211 | 6934.7537 | 14000 | 1.79 | 7821.2291 | 7424.0912 | 14000 | 1.66 | 8433.7349 | 8066.9145
|  |  | 100 | mid | 11200 | 2.73 | 4102.5641 | 2 | 11200 | 2.58 | 4341.0853 | 2 | 11200 | 2.4 | 4666.6667 | 2 | 11200 | 2.2 | 5090.9091 | 2 | 11200 | 1.98 | 5656.5657 | 2 | 11200 | 1.76 | 6363.6364 | 2
|  |  | 7564.9712 | min | 7340 | 2.58 | 2844.9612 | 0.83117 | 7040 | 2.33 | 3021.4592 | 0.83117 | 6560 | 2.02 | 3247.5248 | 0.83117 | 6020 | 1.66 | 3626.506 | 0.83117 | 5260 | 1.36 | 3867.6471 | 0.83117 | 4480 | 1.04 | 4307.6923 | 0.83117
| -12 |  | 1.865 | max | 14440 | 2.24 | 6446.4286 | 2.736 | 14240 | 2.09 | 6813.3971 | 2.484 | 13920 | 1.94 | 7175.2577 | 2.2527 | 13640 | 1.76 | 7750 | 2.0119 | 13440 | 1.69 | 7952.6627 | 1.8772 | 13280 | 1.57 | 8458.5987 | 1.722
|  | 13104.5455 | 50.3924 | nom | 14000 | 2.72 | 5147.0588 | 4789.6901 | 14000 | 2.42 | 5785.124 | 5275.6647 | 14000 | 2.16 | 6481.4815 | 5817.1494 | 14000 | 1.9 | 7368.4211 | 6513.4143 | 14000 | 1.81 | 7734.8066 | 6981.0521 | 14000 | 1.69 | 8284.0237 | 7610.1589
|  |  | 100 | mid | 11200 | 2.77 | 4043.3213 | 2 | 11200 | 2.62 | 4274.8092 | 2 | 11200 | 2.45 | 4571.4286 | 2 | 11200 | 2.25 | 4977.7778 | 2 | 11200 | 2.02 | 5544.5545 | 2 | 11200 | 1.79 | 6256.9832 | 2
|  |  | 7026.6378 | min | 6960 | 2.57 | 2708.1712 | 0.68019 | 6660 | 2.32 | 2870.6897 | 0.68019 | 6240 | 2.03 | 3073.8916 | 0.68019 | 5780 | 1.69 | 3420.1183 | 0.68019 | 5040 | 1.39 | 3625.8993 | 0.68019 | 4320 | 1.06 | 4075.4717 | 0.68019
| -11 |  | 1.95 | max | 14520 | 2.32 | 6258.6207 | 2.7835 | 14320 | 2.17 | 6599.0783 | 2.5542 | 14060 | 2.02 | 6960.396 | 2.3306 | 13820 | 1.83 | 7551.9126 | 2.0883 | 13720 | 1.77 | 7751.4124 | 1.9383 | 13640 | 1.66 | 8216.8675 | 1.7671
|  | 12681.8182 | 49.6105 | nom | 14000 | 2.76 | 5072.4638 | 4556.0053 | 14000 | 2.46 | 5691.0569 | 4965.1701 | 14000 | 2.18 | 6422.0183 | 5441.324 | 14000 | 1.9 | 7368.4211 | 6072.7612 | 14000 | 1.83 | 7650.2732 | 6542.8232 | 14000 | 1.72 | 8139.5349 | 7176.717
|  |  | 100 | mid | 11200 | 2.81 | 3985.7651 | 2 | 11200 | 2.66 | 4210.5263 | 2 | 11200 | 2.5 | 4480 | 2 | 11200 | 2.3 | 4869.5652 | 2 | 11200 | 2.06 | 5436.8932 | 2 | 11200 | 1.82 | 6153.8462 | 2
|  |  | 6503.606 | min | 6580 | 2.56 | 2570.3125 | 0.52922 | 6280 | 2.31 | 2718.6147 | 0.52922 | 5920 | 2.04 | 2901.9608 | 0.52922 | 5540 | 1.72 | 3220.9302 | 0.52922 | 4820 | 1.42 | 3394.3662 | 0.52922 | 4160 | 1.08 | 3851.8519 | 0.52922
| -10 |  | 2.0465 | max | 14600 | 2.4 | 6083.3333 | 2.8311 | 14400 | 2.25 | 6400 | 2.6244 | 14200 | 2.1 | 6761.9048 | 2.4176 | 14000 | 1.9 | 7368.4211 | 2.1798 | 14000 | 1.85 | 7567.5676 | 2.0054 | 14000 | 1.75 | 8000 | 1.8122
|  | 12259.0909 | 48.8225 | nom | 14000 | 2.8 | 5000 | 4330.17 | 14000 | 2.5 | 5600 | 4671.2854 | 14000 | 2.2 | 6363.6364 | 5070.7403 | 14000 | 1.9 | 7368.4211 | 5623.9806 | 14000 | 1.85 | 7567.5676 | 6112.9235 | 14000 | 1.75 | 8000 | 6764.8482
|  |  | 100 | mid | 11200 | 2.85 | 3929.8246 | 2 | 11200 | 2.7 | 4148.1481 | 2 | 11200 | 2.55 | 4392.1569 | 2 | 11200 | 2.35 | 4765.9574 | 2 | 11200 | 2.1 | 5333.3333 | 2 | 11200 | 1.85 | 6054.0541 | 2
|  |  | 5990.282 | min | 6200 | 2.55 | 2431.3725 | 0.37825 | 5900 | 2.3 | 2565.2174 | 0.37825 | 5600 | 2.05 | 2731.7073 | 0.37825 | 5300 | 1.75 | 3028.5714 | 0.37825 | 4600 | 1.45 | 3172.4138 | 0.37825 | 4000 | 1.1 | 3636.3636 | 0.37825
| -9 |  | 2.196 | max | 15100 | 2.5 | 6040 | 2.9606 | 14900 | 2.3333 | 6385.7143 | 2.7545 | 14700 | 2.1667 | 6784.6154 | 2.5485 | 14500 | 1.9667 | 7372.8814 | 2.3167 | 14233.3333 | 1.9167 | 7426.087 | 2.1174 | 14000 | 1.8167 | 7706.422 | 1.9068
|  | 11836.3636 | 48.0283 | nom | 14000 | 2.8833 | 4855.4913 | 3997.9529 | 14000 | 2.6 | 5384.6154 | 4297.0297 | 14000 | 2.3167 | 6043.1655 | 4644.4709 | 14000 | 2.0333 | 6885.2459 | 5109.2217 | 14000 | 1.95 | 7179.4872 | 5589.9821 | 14000 | 1.8167 | 7706.422 | 6207.3897
|  |  | 100 | mid | 11200 | 2.9833 | 3754.1899 | 2 | 11200 | 2.8 | 4000 | 2 | 11200 | 2.6167 | 4280.2548 | 2 | 11200 | 2.4 | 4666.6667 | 2 | 11200 | 2.1667 | 5169.2308 | 2 | 11200 | 1.9333 | 5793.1034 | 2
|  |  | 5389.9811 | min | 5833.3333 | 2.9167 | 2000 | 0.22727 | 5266.6667 | 2.2833 | 2306.5693 | 0.22727 | 5066.6667 | 2.05 | 2471.5447 | 0.22727 | 4866.6667 | 1.7833 | 2728.972 | 0.22727 | 4266.6667 | 1.4667 | 2909.0909 | 0.22727 | 3700 | 1.1167 | 3313.4328 | 0.22727
| -8 |  | 2.3353 | max | 15600 | 2.6 | 6000 | 3.1052 | 15400 | 2.4167 | 6372.4138 | 2.8847 | 15200 | 2.2333 | 6805.9701 | 2.6643 | 15000 | 2.0333 | 7377.0492 | 2.4284 | 14466.6667 | 1.9833 | 7294.1176 | 2.2193 | 14000 | 1.8833 | 7433.6283 | 2.0065
|  | 11413.6364 | 47.2275 | nom | 14000 | 2.9667 | 4719.1011 | 3675.6267 | 14000 | 2.7 | 5185.1852 | 3956.556 | 14000 | 2.4333 | 5753.4247 | 4283.9821 | 14000 | 2.1667 | 6461.5385 | 4700.0992 | 14000 | 2.05 | 6829.2683 | 5142.7944 | 14000 | 1.8833 | 7433.6283 | 5688.3495
|  |  | 100 | mid | 11200 | 3.1167 | 3593.5829 | 2 | 11200 | 2.9 | 3862.069 | 2 | 11200 | 2.6833 | 4173.913 | 2 | 11200 | 2.45 | 4571.4286 | 2 | 11200 | 2.2333 | 5014.9254 | 2 | 11200 | 2.0167 | 5553.719 | 2
|  |  | 4887.5293 | min | 5466.6667 | 3.2833 | 1664.9746 | 0.076299 | 4633.3333 | 2.2667 | 2044.1176 | 0.076299 | 4533.3333 | 2.05 | 2211.3821 | 0.076299 | 4433.3333 | 1.8167 | 2440.367 | 0.076299 | 3933.3333 | 1.4833 | 2651.6854 | 0.076299 | 3400 | 1.1333 | 3000 | 0.076299
| -7 |  | 2.4234 | max | 16100 | 2.7 | 5962.963 | 3.2637 | 15900 | 2.5 | 6360 | 2.9782 | 15700 | 2.3 | 6826.087 | 2.7297 | 15500 | 2.1 | 7380.9524 | 2.4811 | 14700 | 2.05 | 7170.7317 | 2.278 | 14000 | 1.95 | 7179.4872 | 2.0755
|  | 10990.9091 | 46.4198 | nom | 14000 | 3.05 | 4590.1639 | 3367.6111 | 14000 | 2.8 | 5000 | 3690.4293 | 14000 | 2.55 | 5490.1961 | 4026.4582 | 14000 | 2.3 | 6086.9565 | 4429.8109 | 14000 | 2.15 | 6511.6279 | 4824.8267 | 14000 | 1.95 | 7179.4872 | 5295.6063
|  |  | 100 | mid | 11200 | 3.25 | 3446.1538 | 1 | 11200 | 3 | 3733.3333 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1 | 11200 | 2.1 | 5333.3333 | 1
|  |  | 4535.2467 | min | 5100 | 3.65 | 1397.2603 | 0.96572 | 4000 | 2.25 | 1777.7778 | 0.97096 | 4000 | 2.05 | 1951.2195 | 0.97096 | 4000 | 1.85 | 2162.1622 | 0.97096 | 3600 | 1.5 | 2400 | 0.97249 | 3100 | 1.15 | 2695.6522 | 0.97419
| -6 |  | 2.4648 | max | 16144.4444 | 2.7611 | 5847.0825 | 3.338 | 15944.4444 | 2.5556 | 6239.1304 | 2.9874 | 15733.3333 | 2.35 | 6695.0355 | 2.7388 | 15533.3333 | 2.1444 | 7243.5233 | 2.4897 | 14744.4444 | 2.0944 | 7039.7878 | 2.2843 | 14033.3333 | 1.9944 | 7036.2117 | 2.0754
|  | 10568.1818 | 45.6049 | nom | 14000 | 3.0889 | 4532.3741 | 3166.0239 | 14000 | 2.8389 | 4931.5068 | 3537.5707 | 14000 | 2.5889 | 5407.7253 | 3858.7557 | 14000 | 2.3389 | 5985.7482 | 4244.8058 | 14000 | 2.1944 | 6379.7468 | 4626.4006 | 14000 | 2 | 7000 | 5092.211
|  |  | 100 | mid | 11200 | 3.2944 | 3399.6627 | 1 | 11200 | 3.0444 | 3678.8321 | 1 | 11200 | 2.7944 | 4007.9523 | 1 | 11200 | 2.5444 | 4401.7467 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.15 | 5209.3023 | 1
|  |  | 4287.59 | min | 5155.5556 | 3.7111 | 1389.2216 | 0.89547 | 4122.2222 | 2.4056 | 1713.6259 | 0.91073 | 4077.7778 | 2.1667 | 1882.0513 | 0.91129 | 4022.2222 | 1.9222 | 2092.4855 | 0.91198 | 3611.1111 | 1.5611 | 2313.1673 | 0.91674 | 3111.1111 | 1.1944 | 2604.6512 | 0.92189
| -5 |  | 2.5124 | max | 16188.8889 | 2.8222 | 5736.2205 | 3.4152 | 15988.8889 | 2.6111 | 6123.4043 | 3.0089 | 15766.6667 | 2.4 | 6569.4444 | 2.7557 | 15566.6667 | 2.1889 | 7111.6751 | 2.5013 | 14788.8889 | 2.1389 | 6914.2857 | 2.2918 | 14066.6667 | 2.0389 | 6899.1826 | 2.0745
|  | 10145.4545 | 44.7824 | nom | 14000 | 3.1278 | 4476.0213 | 2970.6837 | 14000 | 2.8778 | 4864.8649 | 3371.8471 | 14000 | 2.6278 | 5327.6956 | 3681.5947 | 14000 | 2.3778 | 5887.8505 | 4056.1002 | 14000 | 2.2389 | 6253.1017 | 4426.9229 | 14000 | 2.05 | 6829.2683 | 4890.4882
|  |  | 100 | mid | 11200 | 3.3389 | 3354.4093 | 1 | 11200 | 3.0889 | 3625.8993 | 1 | 11200 | 2.8389 | 3945.2055 | 1 | 11200 | 2.5889 | 4326.1803 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.2 | 5090.9091 | 1
|  |  | 4038.2264 | min | 5211.1111 | 3.7722 | 1381.4433 | 0.82392 | 4244.4444 | 2.5611 | 1657.2668 | 0.84839 | 4155.5556 | 2.2833 | 1819.9513 | 0.8503 | 4044.4444 | 1.9944 | 2027.8552 | 0.85263 | 3622.2222 | 1.6222 | 2232.8767 | 0.86084 | 3122.2222 | 1.2389 | 2520.1794 | 0.86945
| -4 |  | 2.5715 | max | 16233.3333 | 2.8833 | 5630.0578 | 3.4954 | 16033.3333 | 2.6667 | 6012.5 | 3.0433 | 15800 | 2.45 | 6448.9796 | 2.7808 | 15600 | 2.2333 | 6985.0746 | 2.516 | 14833.3333 | 2.1833 | 6793.8931 | 2.3003 | 14100 | 2.0833 | 6768 | 2.073
|  | 9722.7273 | 43.952 | nom | 14000 | 3.1667 | 4421.0526 | 2781.5988 | 14000 | 2.9167 | 4800 | 3194.844 | 14000 | 2.6667 | 5250 | 3496.3235 | 14000 | 2.4167 | 5793.1034 | 3864.3899 | 14000 | 2.2833 | 6131.3869 | 4226.684 | 14000 | 2.1 | 6666.6667 | 4690.2369
|  |  | 100 | mid | 11200 | 3.3833 | 3310.3448 | 1 | 11200 | 3.1333 | 3574.4681 | 1 | 11200 | 2.8833 | 3884.3931 | 1 | 11200 | 2.6333 | 4253.1646 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.25 | 4977.7778 | 1
|  |  | 3780.9657 | min | 5266.6667 | 3.8333 | 1373.913 | 0.75102 | 4366.6667 | 2.7167 | 1607.362 | 0.78381 | 4233.3333 | 2.4 | 1763.8889 | 0.78795 | 4066.6667 | 2.0667 | 1967.7419 | 0.79291 | 3633.3333 | 1.6833 | 2158.4158 | 0.80477 | 3133.3333 | 1.2833 | 2441.5584 | 0.81687
| -3 |  | 2.6397 | max | 16277.7778 | 2.9444 | 5528.3019 | 3.5786 | 16077.7778 | 2.7222 | 5906.1224 | 3.0913 | 15833.3333 | 2.5 | 6333.3333 | 2.8144 | 15633.3333 | 2.2778 | 6863.4146 | 2.5338 | 14877.7778 | 2.2278 | 6678.3042 | 2.31 | 14133.3333 | 2.1278 | 6642.2977 | 2.0707
|  | 9300 | 43.1133 | nom | 14000 | 3.2056 | 4367.4177 | 2598.761 | 14000 | 2.9556 | 4736.8421 | 3008.4711 | 14000 | 2.7056 | 5174.538 | 3304.4453 | 14000 | 2.4556 | 5701.3575 | 3670.3861 | 14000 | 2.3278 | 6014.3198 | 4025.974 | 14000 | 2.15 | 6511.6279 | 4491.2573
|  |  | 100 | mid | 11200 | 3.4278 | 3267.423 | 1 | 11200 | 3.1778 | 3524.4755 | 1 | 11200 | 2.9278 | 3825.4269 | 1 | 11200 | 2.6778 | 4182.5726 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1
|  |  | 3523.1594 | min | 5322.2222 | 3.8944 | 1366.6191 | 0.67675 | 4488.8889 | 2.8722 | 1562.8627 | 0.71689 | 4311.1111 | 2.5167 | 1713.0243 | 0.72419 | 4088.8889 | 2.1389 | 1911.6883 | 0.73281 | 3644.4444 | 1.7444 | 2089.172 | 0.74853 | 3144.4444 | 1.3278 | 2368.2008 | 0.76414
| -2 |  | 2.7199 | max | 16322.2222 | 3.0056 | 5430.6839 | 3.665 | 16122.2222 | 2.7778 | 5804 | 3.1537 | 15866.6667 | 2.55 | 6222.2222 | 2.8567 | 15666.6667 | 2.3222 | 6746.4115 | 2.5548 | 14922.2222 | 2.2722 | 6567.2372 | 2.3208 | 14166.6667 | 2.1722 | 6521.7391 | 2.0677
|  | 8877.2727 | 42.2656 | nom | 14000 | 3.2444 | 4315.0685 | 2422.1463 | 14000 | 2.9944 | 4675.3247 | 2814.8966 | 14000 | 2.7444 | 5101.2146 | 3107.5769 | 14000 | 2.4944 | 5612.4722 | 3474.8068 | 14000 | 2.3722 | 5901.6393 | 3825.0818 | 14000 | 2.2 | 6363.6364 | 4293.3503
|  |  | 100 | mid | 11200 | 3.4722 | 3225.6 | 1 | 11200 | 3.2222 | 3475.8621 | 1 | 11200 | 2.9722 | 3768.2243 | 1 | 11200 | 2.7222 | 4114.2857 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1
|  |  | 3263.8776 | min | 5377.7778 | 3.9556 | 1359.5506 | 0.60106 | 4611.1111 | 3.0278 | 1522.9358 | 0.64748 | 4388.8889 | 2.6333 | 1666.6667 | 0.65898 | 4111.1111 | 2.2111 | 1859.2965 | 0.67234 | 3655.5556 | 1.8056 | 2024.6154 | 0.69213 | 3155.5556 | 1.3722 | 2299.5951 | 0.71126
| -1 |  | 2.8152 | max | 16366.6667 | 3.0667 | 5336.9565 | 3.7547 | 16166.6667 | 2.8333 | 5705.8824 | 3.2313 | 15900 | 2.6 | 6115.3846 | 2.9079 | 15700 | 2.3667 | 6633.8028 | 2.5789 | 14966.6667 | 2.3167 | 6460.4317 | 2.3327 | 14200 | 2.2167 | 6406.015 | 2.0639
|  | 8454.5455 | 41.4086 | nom | 14000 | 3.2833 | 4263.9594 | 2251.7162 | 14000 | 3.0333 | 4615.3846 | 2616.4637 | 14000 | 2.7833 | 5029.9401 | 2907.4044 | 14000 | 2.5333 | 5526.3158 | 3278.3687 | 14000 | 2.4167 | 5793.1034 | 3624.293 | 14000 | 2.25 | 6222.2222 | 4096.3173
|  |  | 100 | mid | 11200 | 3.5167 | 3184.8341 | 1 | 11200 | 3.2667 | 3428.5714 | 1 | 11200 | 3.0167 | 3712.7072 | 1 | 11200 | 2.7667 | 4048.1928 | 1 | 11200 | 2.6 | 4307.6923 | 1 | 11200 | 2.4 | 4666.6667 | 1
|  |  | 3003.1412 | min | 5433.3333 | 4.0167 | 1352.6971 | 0.52391 | 4733.3333 | 3.1833 | 1486.911 | 0.57545 | 4466.6667 | 2.75 | 1624.2424 | 0.59226 | 4133.3333 | 2.2833 | 1810.219 | 0.61149 | 3666.6667 | 1.8667 | 1964.2857 | 0.63556 | 3166.6667 | 1.4167 | 2235.2941 | 0.65824
| 0 |  | 2.9293 | max | 16411.1111 | 3.1278 | 5246.8917 | 3.8477 | 16211.1111 | 2.8889 | 5611.5385 | 3.325 | 15933.3333 | 2.65 | 6012.5786 | 2.9686 | 15733.3333 | 2.4111 | 6525.3456 | 2.6062 | 15011.1111 | 2.3611 | 6357.6471 | 2.3458 | 14233.3333 | 2.2611 | 6294.8403 | 2.0595
|  | 8031.8182 | 40.5417 | nom | 14000 | 3.3222 | 4214.0468 | 2087.419 | 14000 | 3.0722 | 4556.962 | 2415.5973 | 14000 | 2.8222 | 4960.6299 | 2705.6354 | 14000 | 2.5722 | 5442.7646 | 3081.778 | 14000 | 2.4611 | 5688.4876 | 3423.8893 | 14000 | 2.3 | 6086.9565 | 3899.9587
|  |  | 100 | mid | 11200 | 3.5611 | 3145.0858 | 1 | 11200 | 3.3111 | 3382.5503 | 1 | 11200 | 3.0611 | 3658.8022 | 1 | 11200 | 2.8111 | 3984.1897 | 1 | 11200 | 2.65 | 4226.4151 | 1 | 11200 | 2.45 | 4571.4286 | 1
|  |  | 2741.8914 | min | 5488.8889 | 4.0778 | 1346.049 | 0.44526 | 4855.5556 | 3.3389 | 1454.2429 | 0.50064 | 4544.4444 | 2.8667 | 1585.2713 | 0.52398 | 4155.5556 | 2.3556 | 1764.1509 | 0.55026 | 3677.7778 | 1.9278 | 1907.781 | 0.57882 | 3177.7778 | 1.4611 | 2174.9049 | 0.60507
| 1 |  | 3.0655 | max | 16455.5556 | 3.1889 | 5160.2787 | 3.9442 | 16255.5556 | 2.9444 | 5520.7547 | 3.4357 | 15966.6667 | 2.7 | 5913.5802 | 3.0388 | 15766.6667 | 2.4556 | 6420.8145 | 2.6368 | 15055.5556 | 2.4056 | 6258.6605 | 2.36 | 14266.6667 | 2.3056 | 6187.9518 | 2.0542
|  | 7609.0909 | 39.6641 | nom | 14000 | 3.3611 | 4165.2893 | 1929.191 | 14000 | 3.1111 | 4500 | 2214.7071 | 14000 | 2.8611 | 4893.2039 | 2503.952 | 14000 | 2.6111 | 5361.7021 | 2885.7232 | 14000 | 2.5056 | 5587.5831 | 3224.147 | 14000 | 2.35 | 5957.4468 | 3704.074
|  |  | 100 | mid | 11200 | 3.6056 | 3106.3174 | 1 | 11200 | 3.3556 | 3337.7483 | 1 | 11200 | 3.1056 | 3606.4401 | 1 | 11200 | 2.8556 | 3922.179 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.5 | 4480 | 1
|  |  | 2482.1764 | min | 5544.4444 | 4.1389 | 1339.5973 | 0.36507 | 4977.7778 | 3.4944 | 1424.4833 | 0.42289 | 4622.2222 | 2.9833 | 1549.3482 | 0.45408 | 4177.7778 | 2.4278 | 1720.8238 | 0.48864 | 3688.8889 | 1.9889 | 1854.7486 | 0.52192 | 3188.8889 | 1.5056 | 2118.0812 | 0.55176
14kW-Maximum heating CAP | 2 |  | 3.2282 | max | 16500 | 3.25 | 5076.9231 | 4.0442 | 16300 | 3 | 5433.3333 | 3.5645 | 16000 | 2.75 | 5818.1818 | 3.1191 | 15800 | 2.5 | 6320 | 2.6706 | 15100 | 2.45 | 6163.2653 | 2.3754 | 14300 | 2.35 | 6085.1064 | 2.0483
|  | 7186.3636 | 38.7753 | nom | 14000 | 3.4 | 4117.6471 | 1776.9571 | 14000 | 3.15 | 4444.4444 | 2016.0968 | 14000 | 2.9 | 4827.5862 | 2303.9672 | 14000 | 2.65 | 5283.0189 | 2690.8675 | 14000 | 2.55 | 5490.1961 | 3025.3355 | 14000 | 2.4 | 5833.3333 | 3508.4605
|  |  | 100 | mid | 11200 | 3.65 | 3068.4932 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 3.15 | 3555.5556 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.55 | 4392.1569 | 1
|  |  | 2226.1089 | min | 5600 | 4.2 | 1333.3333 | 0.28328 | 5100 | 3.65 | 1397.2603 | 0.34203 | 4700 | 3.1 | 1516.129 | 0.38252 | 4200 | 2.5 | 1680 | 0.42662 | 3700 | 2.05 | 1804.878 | 0.46485 | 3200 | 1.55 | 2064.5161 | 0.4983
| 3 |  | 3.4724 | max | 16560 | 3.54 | 4677.9661 | 4.5112 | 16360 | 3.25 | 5033.8462 | 3.7718 | 16080 | 2.96 | 5432.4324 | 3.2509 | 15860 | 2.66 | 5962.406 | 2.7326 | 15160 | 2.54 | 5968.5039 | 2.396 | 14360 | 2.38 | 6033.6134 | 2.0303
|  | 6763.6364 | 37.8742 | nom | 14000 | 3.7 | 3783.7838 | 1499.2968 | 14000 | 3.41 | 4105.5718 | 1793.1949 | 14000 | 3.12 | 4487.1795 | 2080.5109 | 14000 | 2.82 | 4964.539 | 2475.1414 | 14000 | 2.67 | 5243.4457 | 2822.8477 | 14000 | 2.47 | 5668.0162 | 3331.3675
|  |  | 100 | mid | 11200 | 3.97 | 2821.1587 | 1 | 11200 | 3.68 | 3043.4783 | 1 | 11200 | 3.39 | 3303.8348 | 1 | 11200 | 3.09 | 3624.5955 | 1 | 11200 | 2.88 | 3888.8889 | 1 | 11200 | 2.62 | 4274.8092 | 1
|  |  | 1947.8239 | min | 5380 | 4.68 | 1149.5726 | 0.23774 | 4920 | 3.81 | 1291.3386 | 0.29357 | 4500 | 3.18 | 1415.0943 | 0.33786 | 4000 | 2.51 | 1593.6255 | 0.38384 | 3500 | 2.04 | 1715.6863 | 0.42385 | 3000 | 1.53 | 1960.7843 | 0.45898
| 4 |  | 3.7331 | max | 16620 | 3.83 | 4339.4256 | 4.9899 | 16420 | 3.5 | 4691.4286 | 3.9675 | 16160 | 3.17 | 5097.7918 | 3.3694 | 15920 | 2.82 | 5645.3901 | 2.781 | 15220 | 2.63 | 5787.0722 | 2.4072 | 14420 | 2.41 | 5983.4025 | 2.0074
|  | 6340.9091 | 36.9601 | nom | 14000 | 4 | 3500 | 1270.7482 | 14000 | 3.67 | 3814.7139 | 1598.204 | 14000 | 3.34 | 4191.6168 | 1881.8881 | 14000 | 2.99 | 4682.2742 | 2280.1166 | 14000 | 2.79 | 5017.9211 | 2634.1138 | 14000 | 2.54 | 5511.811 | 3158.746
|  |  | 100 | mid | 11200 | 4.29 | 2610.7226 | 1 | 11200 | 3.96 | 2828.2828 | 1 | 11200 | 3.63 | 3085.3994 | 1 | 11200 | 3.28 | 3414.6341 | 1 | 11200 | 3.01 | 3720.9302 | 1 | 11200 | 2.69 | 4163.5688 | 1
|  |  | 1698.5812 | min | 5160 | 5.16 | 1000 | 0.19551 | 4740 | 3.97 | 1193.9547 | 0.24782 | 4300 | 3.26 | 1319.0184 | 0.29578 | 3800 | 2.52 | 1507.9365 | 0.34337 | 3300 | 2.03 | 1625.6158 | 0.38493 | 2800 | 1.51 | 1854.3046 | 0.42154
| 5 |  | 4.0128 | max | 16680 | 4.12 | 4048.5437 | 5.4791 | 16480 | 3.75 | 4394.6667 | 4.1525 | 16240 | 3.38 | 4804.7337 | 3.4757 | 15980 | 2.98 | 5362.4161 | 2.8167 | 15280 | 2.72 | 5617.6471 | 2.4097 | 14480 | 2.44 | 5934.4262 | 1.98
|  | 5918.1818 | 36.0318 | nom | 14000 | 4.3 | 3255.814 | 1080.1468 | 14000 | 3.93 | 3562.341 | 1425.2093 | 14000 | 3.56 | 3932.5843 | 1702.7194 | 14000 | 3.16 | 4430.3797 | 2101.088 | 14000 | 2.91 | 4810.9966 | 2456.0088 | 14000 | 2.61 | 5363.9847 | 2988.9648
|  |  | 100 | mid | 11200 | 4.61 | 2429.5011 | 1 | 11200 | 4.24 | 2641.5094 | 1 | 11200 | 3.87 | 2894.0568 | 1 | 11200 | 3.47 | 3227.6657 | 1 | 11200 | 3.14 | 3566.879 | 1 | 11200 | 2.76 | 4057.971 | 1
|  |  | 1474.8102 | min | 4940 | 5.64 | 875.8865 | 0.15626 | 4560 | 4.13 | 1104.1162 | 0.20455 | 4100 | 3.34 | 1227.5449 | 0.25608 | 3600 | 2.53 | 1422.9249 | 0.30502 | 3100 | 2.02 | 1534.6535 | 0.34792 | 2600 | 1.49 | 1744.9664 | 0.38584
| 6 |  | 4.3143 | max | 16740 | 4.41 | 3795.9184 | 5.9776 | 16540 | 4 | 4135 | 4.3276 | 16320 | 3.59 | 4545.961 | 3.5708 | 16040 | 3.14 | 5108.2803 | 2.8409 | 15340 | 2.81 | 5459.0747 | 2.404 | 14540 | 2.47 | 5886.6397 | 1.9484
|  | 5495.4545 | 35.088 | nom | 14000 | 4.6 | 3043.4783 | 919.3422 | 14000 | 4.19 | 3341.2888 | 1269.8567 | 14000 | 3.78 | 3703.7037 | 1538.9967 | 14000 | 3.33 | 4204.2042 | 1934.4159 | 14000 | 3.03 | 4620.462 | 2285.9545 | 14000 | 2.68 | 5223.8806 | 2820.5128
|  |  | 100 | mid | 11200 | 4.93 | 2271.8053 | 1 | 11200 | 4.52 | 2477.8761 | 1 | 11200 | 4.11 | 2725.0608 | 1 | 11200 | 3.66 | 3060.1093 | 1 | 11200 | 3.27 | 3425.0765 | 1 | 11200 | 2.83 | 3957.5972 | 1
|  |  | 1273.7781 | min | 4720 | 6.12 | 771.2418 | 0.11967 | 4380 | 4.29 | 1020.979 | 0.16356 | 3900 | 3.42 | 1140.3509 | 0.21856 | 3400 | 2.54 | 1338.5827 | 0.26865 | 2900 | 2.01 | 1442.7861 | 0.31271 | 2400 | 1.47 | 1632.6531 | 0.35176
| 7 |  | 4.6674 | max | 16800 | 4.7 | 3574.4681 | 6.4846 | 16600 | 4.25 | 3905.8824 | 4.4936 | 16400 | 3.8 | 4315.7895 | 3.6556 | 16100 | 3.3 | 4878.7879 | 2.8543 | 15400 | 2.9 | 5310.3448 | 2.3908 | 14600 | 2.5 | 5840 | 1.9128
|  | 5072.7273 | 34.1273 | nom | 14000 | 4.9 | 2857.1429 | 782.273 | 14000 | 4.45 | 3146.0674 | 1128.8691 | 14000 | 4 | 3500 | 1387.6685 | 14000 | 3.5 | 4000 | 1777.2116 | 14000 | 3.15 | 4444.4444 | 2121.7679 | 14000 | 2.75 | 5090.9091 | 2651.9512
|  |  | 100 | mid | 11200 | 5.25 | 2133.3333 | 1 | 11200 | 4.8 | 2333.3333 | 1 | 11200 | 4.35 | 2574.7126 | 1 | 11200 | 3.85 | 2909.0909 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 2.9 | 3862.069 | 1
|  |  | 1086.8468 | min | 4500 | 6.6 | 681.8182 | 0.085482 | 4200 | 4.45 | 943.8202 | 0.12468 | 3700 | 3.5 | 1057.1429 | 0.18303 | 3200 | 2.55 | 1254.902 | 0.23409 | 2700 | 2 | 1350 | 0.27914 | 2200 | 1.45 | 1517.2414 | 0.31919
| 8 |  | 4.8703 | max | 16860 | 4.81 | 3505.1975 | 6.31 | 16640 | 4.38 | 3799.0868 | 4.5431 | 16440 | 3.93 | 4183.2061 | 3.7899 | 16160 | 3.48 | 4643.6782 | 3.0636 | 15440 | 3.06 | 5045.7516 | 2.5648 | 14640 | 2.64 | 5545.4545 | 2.0589
|  | 4650 | 33.148 | nom | 14000 | 5.02 | 2788.8446 | 736.9255 | 14000 | 4.59 | 3050.1089 | 1023.5288 | 14000 | 4.16 | 3365.3846 | 1226.9495 | 14000 | 3.69 | 3794.0379 | 1517.8036 | 14000 | 3.32 | 4216.8675 | 1813.0422 | 14000 | 2.9 | 4827.5862 | 2258.5156
|  |  | 100 | mid | 11200 | 5.37 | 2085.6611 | 0 | 11200 | 4.95 | 2262.6263 | 1 | 11200 | 4.53 | 2472.4062 | 1 | 11200 | 4.06 | 2758.6207 | 1 | 11200 | 3.58 | 3128.4916 | 1 | 11200 | 3.06 | 3660.1307 | 1
|  |  | 954.7591 | min | 4920 | 6.31 | 779.7147 | 0 | 4600 | 4.54 | 1013.2159 | 0.0075758 | 4120 | 3.73 | 1104.5576 | 0.074859 | 3640 | 2.91 | 1250.8591 | 0.1336 | 3200 | 2.34 | 1367.5214 | 0.18125 | 2760 | 1.77 | 1559.322 | 0.22393
| 9 |  | 5.0265 | max | 16920 | 4.92 | 3439.0244 | 6.02 | 16680 | 4.51 | 3698.4479 | 4.63 | 16480 | 4.06 | 4059.1133 | 3.96 | 16220 | 3.66 | 4431.694 | 3.2907 | 15480 | 3.22 | 4807.4534 | 2.7559 | 14680 | 2.78 | 5280.5755 | 2.2201
|  | 4227.2727 | 32.1478 | nom | 14000 | 5.14 | 2723.7354 | 702.2048 | 14000 | 4.73 | 2959.8309 | 913.0179 | 14000 | 4.32 | 3240.7407 | 1067.4931 | 14000 | 3.88 | 3608.2474 | 1284.6181 | 14000 | 3.49 | 4011.4613 | 1533.884 | 14000 | 3.05 | 4590.1639 | 1904.0878
|  |  | 82.9369 | mid | 11200 | 5.49 | 2040.0729 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.71 | 2377.9193 | 0 | 11200 | 4.27 | 2622.9508 | 1 | 11200 | 3.76 | 2978.7234 | 1 | 11200 | 3.22 | 3478.2609 | 1
|  |  | 841.0052 | min | 5340 | 6.02 | 887.0432 | 0 | 5000 | 4.63 | 1079.9136 | 0 | 4540 | 3.96 | 1146.4646 | 0 | 4080 | 3.27 | 1247.7064 | 0.020684 | 3700 | 2.68 | 1380.597 | 0.070303 | 3320 | 2.09 | 1588.5167 | 0.11514
| 10 |  | 5.1114 | max | 16980 | 5.03 | 3375.7455 | 5.73 | 16720 | 4.64 | 3603.4483 | 4.72 | 16520 | 4.19 | 3942.7208 | 4.19 | 16280 | 3.84 | 4239.5833 | 3.63 | 15520 | 3.38 | 4591.716 | 3.02 | 14720 | 2.92 | 5041.0959 | 2.41
|  | 3804.5455 | 31.1243 | nom | 14000 | 5.26 | 2661.597 | 663.9695 | 14000 | 4.87 | 2874.7433 | 806.0478 | 14000 | 4.48 | 3125 | 908.0061 | 14000 | 4.07 | 3439.8034 | 1048.0841 | 14000 | 3.66 | 3825.1366 | 1259.7833 | 14000 | 3.2 | 4375 | 1578.6496
|  |  | 68.68 | mid | 11200 | 5.61 | 1996.4349 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.89 | 2290.3885 | 0 | 11200 | 4.48 | 2500 | 0 | 11200 | 3.94 | 2842.6396 | 0 | 11200 | 3.38 | 3313.6095 | 0
|  |  | 744.3185 | min | 5760 | 5.73 | 1005.2356 | 0 | 5400 | 4.72 | 1144.0678 | 0 | 4960 | 4.19 | 1183.7709 | 0 | 4520 | 3.63 | 1245.1791 | 0 | 4200 | 3.02 | 1390.7285 | 0 | 3880 | 2.41 | 1609.9585 | 0
| 11 |  | 5.1203 | max | 17040 | 5.14 | 3315.1751 | 5.44 | 16760 | 4.77 | 3513.6268 | 4.81 | 16560 | 4.32 | 3833.3333 | 4.42 | 16340 | 4.02 | 4064.6766 | 3.99 | 15560 | 3.54 | 4395.4802 | 3.36 | 14760 | 3.06 | 4823.5294 | 2.73
|  | 3381.8182 | 30.0741 | nom | 14000 | 5.38 | 2602.2305 | 621.6578 | 14000 | 5.01 | 2794.4112 | 703.0807 | 14000 | 4.64 | 3017.2414 | 765.1172 | 14000 | 4.26 | 3286.385 | 847.5735 | 14000 | 3.83 | 3655.3525 | 1006.4935 | 14000 | 3.35 | 4179.1045 | 1238.7612
|  |  | 56.4843 | mid | 11200 | 5.73 | 1954.6248 | 0 | 11200 | 5.4 | 2074.0741 | 0 | 11200 | 5.07 | 2209.073 | 0 | 11200 | 4.69 | 2388.0597 | 0 | 11200 | 4.12 | 2718.4466 | 0 | 11200 | 3.54 | 3163.8418 | 0
|  |  | 660.4684 | min | 6180 | 5.44 | 1136.0294 | 0 | 5800 | 4.81 | 1205.8212 | 0 | 5380 | 4.42 | 1217.1946 | 0 | 4960 | 3.99 | 1243.1078 | 0 | 4700 | 3.36 | 1398.8095 | 0 | 4440 | 2.73 | 1626.3736 | 0
| 12 |  | 5.0502 | max | 17100 | 5.25 | 3257.1429 | 5.15 | 16800 | 4.9 | 3428.5714 | 4.9 | 16600 | 4.45 | 3730.3371 | 4.65 | 16400 | 4.2 | 3904.7619 | 4.35 | 15600 | 3.7 | 4216.2162 | 3.7 | 14800 | 3.2 | 4625 | 3.05
|  | 2959.0909 | 28.9931 | nom | 14000 | 5.5 | 2545.4545 | 574.5808 | 14000 | 5.15 | 2718.4466 | 603.8961 | 14000 | 4.8 | 2916.6667 | 636.3636 | 14000 | 4.45 | 3146.0674 | 680.2508 | 14000 | 4 | 3500 | 799.7543 | 14000 | 3.5 | 4000 | 970.1937
|  |  | 45.9466 | mid | 11200 | 5.85 | 1914.5299 | 0 | 11200 | 5.55 | 2018.018 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.9 | 2285.7143 | 0 | 11200 | 4.3 | 2604.6512 | 0 | 11200 | 3.7 | 3027.027 | 0
|  |  | 585.9385 | min | 6600 | 5.15 | 1281.5534 | 0 | 6200 | 4.9 | 1265.3061 | 0 | 5800 | 4.65 | 1247.3118 | 0 | 5400 | 4.35 | 1241.3793 | 0 | 5200 | 3.7 | 1405.4054 | 0 | 5000 | 3.05 | 1639.3443 | 0
| 13 |  | 5.0973 | max | 17566.6667 | 5.2833 | 3324.9211 | 5.15 | 17266.6667 | 4.9333 | 3500 | 4.9667 | 17033.3333 | 4.55 | 3743.5897 | 4.7833 | 16833.3333 | 4.3 | 3914.7287 | 4.55 | 16033.3333 | 3.8 | 4219.2982 | 3.9167 | 15200 | 3.3 | 4606.0606 | 3.2667
|  | 2536.3636 | 27.8757 | nom | 14000 | 5.5 | 2545.4545 | 492.4978 | 14000 | 5.1833 | 2700.9646 | 510.6772 | 14000 | 4.8667 | 2876.7123 | 530.2502 | 14000 | 4.55 | 3076.9231 | 557.4426 | 14000 | 4.1 | 3414.6341 | 647.5822 | 14000 | 3.6167 | 3870.9677 | 776.4378
|  |  | 38.5736 | mid | 11200 | 5.9 | 1898.3051 | 0 | 11200 | 5.5833 | 2005.9701 | 0 | 11200 | 5.3167 | 2106.5831 | 0 | 11200 | 5.0167 | 2232.5581 | 0 | 11200 | 4.4167 | 2535.8491 | 0 | 11200 | 3.8167 | 2934.4978 | 0
|  |  | 497.5916 | min | 6700 | 5.15 | 1300.9709 | 0 | 6266.6667 | 4.9667 | 1261.745 | 0 | 5833.3333 | 4.7833 | 1219.5122 | 0 | 5400 | 4.55 | 1186.8132 | 0 | 5233.3333 | 3.9167 | 1336.1702 | 0 | 5066.6667 | 3.2667 | 1551.0204 | 0
| 14 |  | 5.13 | max | 18033.3333 | 5.3167 | 3391.8495 | 5.15 | 17733.3333 | 4.9667 | 3570.4698 | 5.0333 | 17466.6667 | 4.65 | 3756.2724 | 4.9167 | 17266.6667 | 4.4 | 3924.2424 | 4.75 | 16466.6667 | 3.9 | 4222.2222 | 4.1333 | 15600 | 3.4 | 4588.2353 | 3.4833
|  | 2113.6364 | 26.7142 | nom | 14000 | 5.5 | 2545.4545 | 410.4148 | 14000 | 5.2167 | 2683.7061 | 419.9278 | 14000 | 4.9333 | 2837.8378 | 429.8921 | 14000 | 4.65 | 3010.7527 | 444.9761 | 14000 | 4.2 | 3333.3333 | 511.3636 | 14000 | 3.7333 | 3750 | 606.7856
|  |  | 31.4529 | mid | 11200 | 5.95 | 1882.3529 | 0 | 11200 | 5.6167 | 1994.0653 | 0 | 11200 | 5.3833 | 2080.4954 | 0 | 11200 | 5.1333 | 2181.8182 | 0 | 11200 | 4.5333 | 2470.5882 | 0 | 11200 | 3.9333 | 2847.4576 | 0
|  |  | 412.0148 | min | 6800 | 5.15 | 1320.3883 | 0 | 6333.3333 | 5.0333 | 1258.2781 | 0 | 5866.6667 | 4.9167 | 1193.2203 | 0 | 5400 | 4.75 | 1136.8421 | 0 | 5266.6667 | 4.1333 | 1274.1935 | 0 | 5133.3333 | 3.4833 | 1473.6842 | 0
| 15 |  | 5.1475 | max | 18500 | 5.35 | 3457.9439 | 5.15 | 18200 | 5 | 3640 | 5.1 | 17900 | 4.75 | 3768.4211 | 5.05 | 17700 | 4.5 | 3933.3333 | 4.95 | 16900 | 4 | 4225 | 4.35 | 16000 | 3.5 | 4571.4286 | 3.7
|  | 1690.9091 | 25.4975 | nom | 14000 | 5.5 | 2545.4545 | 328.3319 | 14000 | 5.25 | 2666.6667 | 331.5508 | 14000 | 5 | 2800 | 334.8335 | 14000 | 4.75 | 2947.3684 | 341.5978 | 14000 | 4.3 | 3255.814 | 388.7147 | 14000 | 3.85 | 3636.3636 | 457.0025
|  |  | 24.5946 | mid | 11200 | 6 | 1866.6667 | 0 | 11200 | 5.65 | 1982.3009 | 0 | 11200 | 5.45 | 2055.0459 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.65 | 2408.6022 | 0 | 11200 | 4.05 | 2765.4321 | 0
|  |  | 328.4905 | min | 6900 | 5.15 | 1339.8058 | 0 | 6400 | 5.1 | 1254.902 | 0 | 5900 | 5.05 | 1168.3168 | 0 | 5400 | 4.95 | 1090.9091 | 0 | 5300 | 4.35 | 1218.3908 | 0 | 5200 | 3.7 | 1405.4054 | 0
| 16 |  | 6.92 | max | 19020 | 5.73 | 3319.3717 | 6.92 | 18720 | 5.3 | 3532.0755 | 5.68 | 18420 | 4.95 | 3721.2121 | 5.37 | 18200 | 4.59 | 3965.1416 | 5.02 | 17380 | 4.08 | 4259.8039 | 4.36 | 16460 | 3.56 | 4623.5955 | 3.65
|  | 1268.1818 | 24.2076 | nom | 14000 | 5.93 | 2360.8769 | 183.2633 | 14000 | 5.57 | 2513.465 | 223.2714 | 14000 | 5.21 | 2687.1401 | 236.1605 | 14000 | 4.85 | 2886.5979 | 252.6259 | 14000 | 4.39 | 3189.0661 | 290.8674 | 14000 | 3.92 | 3571.4286 | 347.4471
|  |  | 18.1688 | mid | 11200 | 6.42 | 1744.5483 | 0 | 11200 | 5.99 | 1869.783 | 0 | 11200 | 5.68 | 1971.831 | 0 | 11200 | 5.36 | 2089.5522 | 0 | 11200 | 4.74 | 2362.8692 | 0 | 11200 | 4.12 | 2718.4466 | 0
|  |  | 183.2633 | min | 6980 | 6.92 | 1008.6705 | 0 | 6460 | 5.68 | 1137.3239 | 0 | 6000 | 5.37 | 1117.3184 | 0 | 5520 | 5.02 | 1099.6016 | 0 | 5360 | 4.36 | 1229.3578 | 0 | 5180 | 3.65 | 1419.1781 | 0
| 17 |  | 8.69 | max | 19540 | 6.11 | 3198.036 | 8.69 | 19240 | 5.6 | 3435.7143 | 6.26 | 18940 | 5.15 | 3677.6699 | 5.69 | 18700 | 4.68 | 3995.7265 | 5.09 | 17860 | 4.16 | 4293.2692 | 4.37 | 16920 | 3.62 | 4674.0331 | 3.6
|  | 845.4545 | 22.8123 | nom | 14000 | 6.36 | 2201.2579 | 97.2905 | 14000 | 5.89 | 2376.91 | 135.0566 | 14000 | 5.42 | 2583.0258 | 148.586 | 14000 | 4.95 | 2828.2828 | 166.1011 | 14000 | 4.48 | 3125 | 193.4679 | 14000 | 3.99 | 3508.7719 | 234.8485
|  |  | 11.9753 | mid | 11200 | 6.84 | 1637.4269 | 0 | 11200 | 6.33 | 1769.3523 | 0 | 11200 | 5.91 | 1895.0931 | 0 | 11200 | 5.47 | 2047.532 | 0 | 11200 | 4.83 | 2318.8406 | 0 | 11200 | 4.19 | 2673.031 | 0
|  |  | 97.2905 | min | 7060 | 8.69 | 812.4281 | 0 | 6520 | 6.26 | 1041.5335 | 0 | 6100 | 5.69 | 1072.0562 | 0 | 5640 | 5.09 | 1108.055 | 0 | 5420 | 4.37 | 1240.2746 | 0 | 5160 | 3.6 | 1433.3333 | 0
| 18 |  | 10.46 | max | 20060 | 6.49 | 3090.9091 | 10.46 | 19760 | 5.9 | 3349.1525 | 6.84 | 19460 | 5.35 | 3637.3832 | 6.01 | 19200 | 4.77 | 4025.1572 | 5.16 | 18340 | 4.24 | 4325.4717 | 4.38 | 17380 | 3.68 | 4722.8261 | 3.55
|  | 422.7273 | 21.2368 | nom | 14000 | 6.79 | 2061.8557 | 40.4137 | 14000 | 6.21 | 2254.4283 | 61.8022 | 14000 | 5.63 | 2486.6785 | 70.3373 | 14000 | 5.05 | 2772.2772 | 81.9239 | 14000 | 4.57 | 3063.4573 | 96.5131 | 14000 | 4.06 | 3448.2759 | 119.0781
|  |  | 5.9206 | mid | 11200 | 7.26 | 1542.6997 | 0 | 11200 | 6.67 | 1679.1604 | 0 | 11200 | 6.14 | 1824.1042 | 0 | 11200 | 5.58 | 2007.1685 | 0 | 11200 | 4.92 | 2276.4228 | 0 | 11200 | 4.26 | 2629.108 | 0
|  |  | 40.4137 | min | 7140 | 10.46 | 682.6004 | 0 | 6580 | 6.84 | 961.9883 | 0 | 6200 | 6.01 | 1031.614 | 0 | 5760 | 5.16 | 1116.2791 | 0 | 5480 | 4.38 | 1251.1416 | 0 | 5140 | 3.55 | 1447.8873 | 0
| 19 |  | 12.23 | max | 20580 | 6.87 | 2995.6332 | 12.23 | 20280 | 6.2 | 3270.9677 | 7.42 | 19980 | 5.55 | 3600 | 6.33 | 19700 | 4.86 | 4053.4979 | 5.23 | 18820 | 4.32 | 4356.4815 | 4.39 | 17840 | 3.74 | 4770.0535 | 3.5
|  | 0 | 19 | nom | 14000 | 7.22 | 1939.0582 | 0 | 14000 | 6.53 | 2143.951 | 0 | 14000 | 5.84 | 2397.2603 | 0 | 14000 | 5.15 | 2718.4466 | 0 | 14000 | 4.66 | 3004.2918 | 0 | 14000 | 4.13 | 3389.8305 | 0
|  |  | 0 | mid | 11200 | 7.68 | 1458.3333 | 0 | 11200 | 7.01 | 1597.7175 | 0 | 11200 | 6.37 | 1758.2418 | 0 | 11200 | 5.69 | 1968.3656 | 0 | 11200 | 5.01 | 2235.5289 | 0 | 11200 | 4.33 | 2586.6051 | 0
|  |  | 0 | min | 7220 | 12.23 | 590.3516 | 0 | 6640 | 7.42 | 894.8787 | 0 | 6300 | 6.33 | 995.2607 | 0 | 5880 | 5.23 | 1124.283 | 0 | 5540 | 4.39 | 1261.959 | 0 | 5120 | 3.5 | 1462.8571 | 0
| 20 |  | #NUM! | max | 21100 | 7.25 | 2910.3448 | 14 | 20800 | 6.5 | 3200 | 8 | 20500 | 5.75 | 3565.2174 | 6.65 | 20200 | 4.95 | 4080.8081 | 5.3 | 19300 | 4.4 | 4386.3636 | 4.4 | 18300 | 3.8 | 4815.7895 | 3.45
|  | -422.7273 | #NUM! | nom | 14000 | 7.65 | 1830.0654 | -30.1948 | 14000 | 6.85 | 2043.7956 | -52.8409 | 14000 | 6.05 | 2314.0496 | -63.568 | 14000 | 5.25 | 2666.6667 | -79.7599 | 14000 | 4.75 | 2947.3684 | -96.0744 | 14000 | 4.2 | 3333.3333 | -122.5296
|  |  |  | mid | 11200 | 8.1 | 1382.716 | 0 | 11200 | 7.35 | 1523.8095 | 0 | 11200 | 6.6 | 1696.9697 | 0 | 11200 | 5.8 | 1931.0345 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.4 | 2545.4545 | 0
|  |  | #NUM! | min | 7300 | 14 | 521.4286 | 0 | 6700 | 8 | 837.5 | 0 | 6400 | 6.65 | 962.406 | 0 | 6000 | 5.3 | 1132.0755 | 0 | 5600 | 4.4 | 1272.7273 | 0 | 5100 | 3.45 | 1478.2609 | 0
Indoor Temp. |  | 20
LWT |  |  | 25 CAP: 25; 35 CAP: 35; 40 CAP: 40; 45 CAP: 45; 50 CAP: 50; 55 CAP: 55
Outdoor air temperature[℃] |  | Heating Demand | COP | CL | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP
|  |  | LWT |  |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI
| -15 |  | 0.69263 | max | - | - | - | - | 14000 | 1.85 | 7567.5676 | 1.7307 | 13500 | 1.7 | 7941.1765 | 1.4927 | 13100 | 1.55 | 8451.6129 | 1.2674 | 12600 | 1.45 | 8689.6552 | 1.0384 | 12200 | 1.3 | 9384.6154 | 0.65114
|  | 14795.4545 | 54.4642 | nom | - | - | - | - | 11000 | 2.3 | 4782.6087 | 8548.9166 | 11000 | 2.1 | 5238.0952 | 9911.6931 | 11000 | 1.9 | 5789.4737 | 11673.6402 | 11000 | 1.75 | 6285.7143 | 14248.974 | 11000 | 1.6 | 6875 | 22722.5131
|  |  | 100 | mid | - | - | - | - | 8800 | 2.5 | 3520 | 3 | 8800 | 2.3 | 3826.087 | 3 | 8800 | 2.1 | 4190.4762 | 3 | 8800 | 1.9 | 4631.5789 | 3 | 8800 | 1.7 | 5176.4706 | 3
|  |  | 21361.1688 | min | - | - | - | - | 7800 | 2.35 | 3319.1489 | 1.2652 | 7200 | 2 | 3600 | 1.5182 | 6500 | 1.6 | 4062.5 | 1.8074 | 5700 | 1.3 | 4384.6154 | 2.3722 | 4800 | 1 | 4800 | 3.1629
| -14 |  | 1.733 | max | 14280 | 2.08 | 6865.3846 | 1.8945 | 14080 | 1.93 | 7295.3368 | 0.42977 | 13640 | 1.78 | 7662.9213 | 2.472 | 13280 | 1.62 | 8197.5309 | 2.0449 | 12880 | 1.53 | 8418.3007 | 1.8499 | 12560 | 1.39 | 9035.9712 | 1.6921
|  | 14372.7273 | 53.7042 | nom | 14000 | 2.64 | 5303.0303 | 7586.3724 | 14000 | 2.34 | 5982.906 | 33442.623 | 14000 | 2.12 | 6603.7736 | 5814.1625 | 14000 | 1.9 | 7368.4211 | 7028.4021 | 14000 | 1.77 | 7909.6045 | 7769.5872 | 14000 | 1.63 | 8588.9571 | 8493.9112
|  |  | 100 | mid | 11200 | 2.69 | 4163.5688 | 3 | 11200 | 2.54 | 4409.4488 | 3 | 11200 | 2.35 | 4765.9574 | 3 | 11200 | 2.15 | 5209.3023 | 3 | 11200 | 1.94 | 5773.1959 | 3 | 11200 | 1.73 | 6473.9884 | 3
|  |  | 8293.534 | min | 7720 | 2.59 | 2980.695 | 1.3312 | 7420 | 2.34 | 3170.9402 | 4.6591 | 6880 | 2.01 | 3422.8856 | -1.0354 | 6260 | 1.63 | 3840.4908 | -0.51768 | 5480 | 1.33 | 4120.3008 | -0.33279 | 4640 | 1.02 | 4549.0196 | -0.25884
| -13 |  | 1.716 | max | 14360 | 2.16 | 6648.1481 | 2.6809 | 14160 | 2.01 | 7044.7761 | 2.3836 | 13780 | 1.86 | 7408.6022 | 2.1446 | 13460 | 1.69 | 7964.497 | 1.9054 | 13160 | 1.61 | 8173.913 | 1.7934 | 12920 | 1.48 | 8729.7297 | 1.6618
|  | 13950 | 52.939 | nom | 14000 | 2.68 | 5223.8806 | 5203.4903 | 14000 | 2.38 | 5882.3529 | 5852.5622 | 14000 | 2.14 | 6542.0561 | 6504.5795 | 14000 | 1.9 | 7368.4211 | 7321.462 | 14000 | 1.79 | 7821.2291 | 7778.5522 | 14000 | 1.66 | 8433.7349 | 8394.5841
|  |  | 100 | mid | 11200 | 2.73 | 4102.5641 | 2 | 11200 | 2.58 | 4341.0853 | 2 | 11200 | 2.4 | 4666.6667 | 2 | 11200 | 2.2 | 5090.9091 | 2 | 11200 | 1.98 | 5656.5657 | 2 | 11200 | 1.76 | 6363.6364 | 2
|  |  | 8129.2119 | min | 7340 | 2.58 | 2844.9612 | 0.98214 | 7040 | 2.33 | 3021.4592 | 0.98214 | 6560 | 2.02 | 3247.5248 | 0.98214 | 6020 | 1.66 | 3626.506 | 0.98214 | 5260 | 1.36 | 3867.6471 | 0.98214 | 4480 | 1.04 | 4307.6923 | 0.98214
| -12 |  | 1.7854 | max | 14440 | 2.24 | 6446.4286 | 2.7284 | 14240 | 2.09 | 6813.3971 | 2.4538 | 13920 | 1.94 | 7175.2577 | 2.209 | 13640 | 1.76 | 7750 | 1.9591 | 13440 | 1.69 | 7952.6627 | 1.8455 | 13280 | 1.57 | 8458.5987 | 1.7069
|  | 13527.2727 | 52.1685 | nom | 14000 | 2.72 | 5147.0588 | 4957.8752 | 14000 | 2.42 | 5785.124 | 5512.8612 | 14000 | 2.16 | 6481.4815 | 6123.8168 | 14000 | 1.9 | 7368.4211 | 6904.8724 | 14000 | 1.81 | 7734.8066 | 7330.0493 | 14000 | 1.69 | 8284.0237 | 7925.1312
|  |  | 100 | mid | 11200 | 2.77 | 4043.3213 | 2 | 11200 | 2.62 | 4274.8092 | 2 | 11200 | 2.45 | 4571.4286 | 2 | 11200 | 2.25 | 4977.7778 | 2 | 11200 | 2.02 | 5544.5545 | 2 | 11200 | 1.79 | 6256.9832 | 2
|  |  | 7576.7921 | min | 6960 | 2.57 | 2708.1712 | 0.83117 | 6660 | 2.32 | 2870.6897 | 0.83117 | 6240 | 2.03 | 3073.8916 | 0.83117 | 5780 | 1.69 | 3420.1183 | 0.83117 | 5040 | 1.39 | 3625.8993 | 0.83117 | 4320 | 1.06 | 4075.4717 | 0.83117
| -11 |  | 1.8613 | max | 14520 | 2.32 | 6258.6207 | 2.776 | 14320 | 2.17 | 6599.0783 | 2.524 | 14060 | 2.02 | 6960.396 | 2.2823 | 13820 | 1.83 | 7551.9126 | 2.0279 | 13720 | 1.77 | 7751.4124 | 1.9036 | 13640 | 1.66 | 8216.8675 | 1.752
|  | 13104.5455 | 51.3924 | nom | 14000 | 2.76 | 5072.4638 | 4720.6741 | 14000 | 2.46 | 5691.0569 | 5192.0554 | 14000 | 2.18 | 6422.0183 | 5741.7207 | 14000 | 1.9 | 7368.4211 | 6462.0557 | 14000 | 1.83 | 7650.2732 | 6884.2477 | 14000 | 1.72 | 8139.5349 | 7479.8466
|  |  | 100 | mid | 11200 | 2.81 | 3985.7651 | 2 | 11200 | 2.66 | 4210.5263 | 2 | 11200 | 2.5 | 4480 | 2 | 11200 | 2.3 | 4869.5652 | 2 | 11200 | 2.06 | 5436.8932 | 2 | 11200 | 1.82 | 6153.8462 | 2
|  |  | 7040.3638 | min | 6580 | 2.56 | 2570.3125 | 0.68019 | 6280 | 2.31 | 2718.6147 | 0.68019 | 5920 | 2.04 | 2901.9608 | 0.68019 | 5540 | 1.72 | 3220.9302 | 0.68019 | 4820 | 1.42 | 3394.3662 | 0.68019 | 4160 | 1.08 | 3851.8519 | 0.68019
| -10 |  | 1.9469 | max | 14600 | 2.4 | 6083.3333 | 2.8235 | 14400 | 2.25 | 6400 | 2.5942 | 14200 | 2.1 | 6761.9048 | 2.3648 | 14000 | 1.9 | 7368.4211 | 2.1119 | 14000 | 1.85 | 7567.5676 | 1.9677 | 14000 | 1.75 | 8000 | 1.7971
|  | 12681.8182 | 50.6105 | nom | 14000 | 2.8 | 5000 | 4491.4621 | 14000 | 2.5 | 5600 | 4888.6108 | 14000 | 2.2 | 6363.6364 | 5362.8063 | 14000 | 1.9 | 7368.4211 | 6005.0734 | 14000 | 1.85 | 7567.5676 | 6445.0128 | 14000 | 1.75 | 8000 | 7056.9106
|  |  | 100 | mid | 11200 | 2.85 | 3929.8246 | 2 | 11200 | 2.7 | 4148.1481 | 2 | 11200 | 2.55 | 4392.1569 | 2 | 11200 | 2.35 | 4765.9574 | 2 | 11200 | 2.1 | 5333.3333 | 2 | 11200 | 1.85 | 6054.0541 | 2
|  |  | 6513.9757 | min | 6200 | 2.55 | 2431.3725 | 0.52922 | 5900 | 2.3 | 2565.2174 | 0.52922 | 5600 | 2.05 | 2731.7073 | 0.52922 | 5300 | 1.75 | 3028.5714 | 0.52922 | 4600 | 1.45 | 3172.4138 | 0.52922 | 4000 | 1.1 | 3636.3636 | 0.52922
| -9 |  | 2.091 | max | 15100 | 2.5 | 6040 | 2.9455 | 14900 | 2.3333 | 6385.7143 | 2.7244 | 14700 | 2.1667 | 6784.6154 | 2.5032 | 14500 | 1.9667 | 7372.8814 | 2.2613 | 14233.3333 | 1.9167 | 7426.087 | 2.0847 | 14000 | 1.8167 | 7706.422 | 1.8892
|  | 12259.0909 | 49.8225 | nom | 14000 | 2.8833 | 4855.4913 | 4161.9606 | 14000 | 2.6 | 5384.6154 | 4499.8212 | 14000 | 2.3167 | 6043.1655 | 4897.3821 | 14000 | 2.0333 | 6885.2459 | 5421.2353 | 14000 | 1.95 | 7179.4872 | 5880.4688 | 14000 | 1.8167 | 7706.422 | 6489.0226
|  |  | 100 | mid | 11200 | 2.9833 | 3754.1899 | 2 | 11200 | 2.8 | 4000 | 2 | 11200 | 2.6167 | 4280.2548 | 2 | 11200 | 2.4 | 4666.6667 | 2 | 11200 | 2.1667 | 5169.2308 | 2 | 11200 | 1.9333 | 5793.1034 | 2
|  |  | 5862.842 | min | 5833.3333 | 2.9167 | 2000 | 0.37825 | 5266.6667 | 2.2833 | 2306.5693 | 0.37825 | 5066.6667 | 2.05 | 2471.5447 | 0.37825 | 4866.6667 | 1.7833 | 2728.972 | 0.37825 | 4266.6667 | 1.4667 | 2909.0909 | 0.37825 | 3700 | 1.1167 | 3313.4328 | 0.37825
| -8 |  | 2.2294 | max | 15600 | 2.6 | 6000 | 3.0826 | 15400 | 2.4167 | 6372.4138 | 2.8545 | 15200 | 2.2333 | 6805.9701 | 2.6265 | 15000 | 2.0333 | 7377.0492 | 2.3856 | 14466.6667 | 1.9833 | 7294.1176 | 2.1917 | 14000 | 1.8833 | 7433.6283 | 1.9864
|  | 11836.3636 | 49.0283 | nom | 14000 | 2.9667 | 4719.1011 | 3839.7641 | 14000 | 2.7 | 5185.1852 | 4146.4968 | 14000 | 2.4333 | 5753.4247 | 4506.4898 | 14000 | 2.1667 | 6461.5385 | 4961.5751 | 14000 | 2.05 | 6829.2683 | 5400.6222 | 14000 | 1.8833 | 7433.6283 | 5958.8101
|  |  | 100 | mid | 11200 | 3.1167 | 3593.5829 | 2 | 11200 | 2.9 | 3862.069 | 2 | 11200 | 2.6833 | 4173.913 | 2 | 11200 | 2.45 | 4571.4286 | 2 | 11200 | 2.2333 | 5014.9254 | 2 | 11200 | 2.0167 | 5553.719 | 2
|  |  | 5309.3175 | min | 5466.6667 | 3.2833 | 1664.9746 | 0.22727 | 4633.3333 | 2.2667 | 2044.1176 | 0.22727 | 4533.3333 | 2.05 | 2211.3821 | 0.22727 | 4433.3333 | 1.8167 | 2440.367 | 0.22727 | 3933.3333 | 1.4833 | 2651.6854 | 0.22727 | 3400 | 1.1333 | 3000 | 0.22727
| -7 |  | 2.3581 | max | 16100 | 2.7 | 5962.963 | 3.2347 | 15900 | 2.5 | 6360 | 2.9847 | 15700 | 2.3 | 6826.087 | 2.7347 | 15500 | 2.1 | 7380.9524 | 2.4847 | 14700 | 2.05 | 7170.7317 | 2.2886 | 14000 | 1.95 | 7179.4872 | 2.0886
|  | 11413.6364 | 48.2275 | nom | 14000 | 3.05 | 4590.1639 | 3528.4553 | 14000 | 2.8 | 5000 | 3823.9965 | 14000 | 2.55 | 5490.1961 | 4173.5724 | 14000 | 2.3 | 6086.9565 | 4593.4927 | 14000 | 2.15 | 6511.6279 | 4987.2672 | 14000 | 1.95 | 7179.4872 | 5464.8478
|  |  | 100 | mid | 11200 | 3.25 | 3446.1538 | 2 | 11200 | 3 | 3733.3333 | 2 | 11200 | 2.75 | 4072.7273 | 2 | 11200 | 2.5 | 4480 | 2 | 11200 | 2.3 | 4869.5652 | 2 | 11200 | 2.1 | 5333.3333 | 2
|  |  | 4840.1762 | min | 5100 | 3.65 | 1397.2603 | 0.076299 | 4000 | 2.25 | 1777.7778 | 0.076299 | 4000 | 2.05 | 1951.2195 | 0.076299 | 4000 | 1.85 | 2162.1622 | 0.076299 | 3600 | 1.5 | 2400 | 0.076299 | 3100 | 1.15 | 2695.6522 | 0.076299
| -6 |  | 2.4305 | max | 16144.4444 | 2.7611 | 5847.0825 | 3.3089 | 15944.4444 | 2.5556 | 6239.1304 | 3.0256 | 15733.3333 | 2.35 | 6695.0355 | 2.776 | 15533.3333 | 2.1444 | 7243.5233 | 2.5263 | 14744.4444 | 2.0944 | 7039.7878 | 2.3283 | 14033.3333 | 1.9944 | 7036.2117 | 2.1253
|  | 10990.9091 | 47.4198 | nom | 14000 | 3.0889 | 4532.3741 | 3321.6625 | 14000 | 2.8389 | 4931.5068 | 3632.6733 | 14000 | 2.5889 | 5407.7253 | 3959.2406 | 14000 | 2.3389 | 5985.7482 | 4350.5628 | 14000 | 2.1944 | 6379.7468 | 4720.6449 | 14000 | 2 | 7000 | 5171.4632
|  |  | 100 | mid | 11200 | 3.2944 | 3399.6627 | 1 | 11200 | 3.0444 | 3678.8321 | 1 | 11200 | 2.7944 | 4007.9523 | 1 | 11200 | 2.5444 | 4401.7467 | 1 | 11200 | 2.35 | 4765.9574 | 1 | 11200 | 2.15 | 5209.3023 | 1
|  |  | 4522.1355 | min | 5155.5556 | 3.7111 | 1389.2216 | 0.96541 | 4122.2222 | 2.4056 | 1713.6259 | 0.97046 | 4077.7778 | 2.1667 | 1882.0513 | 0.97064 | 4022.2222 | 1.9222 | 2092.4855 | 0.97087 | 3611.1111 | 1.5611 | 2313.1673 | 0.97245 | 3111.1111 | 1.1944 | 2604.6512 | 0.97415
| -5 |  | 2.4718 | max | 16188.8889 | 2.8222 | 5736.2205 | 3.3846 | 15988.8889 | 2.6111 | 6123.4043 | 3.0409 | 15766.6667 | 2.4 | 6569.4444 | 2.7891 | 15566.6667 | 2.1889 | 7111.6751 | 2.5364 | 14788.8889 | 2.1389 | 6914.2857 | 2.3352 | 14066.6667 | 2.0389 | 6899.1826 | 2.1248
|  | 10568.1818 | 46.6049 | nom | 14000 | 3.1278 | 4476.0213 | 3122.4271 | 14000 | 2.8778 | 4864.8649 | 3475.2925 | 14000 | 2.6278 | 5327.6956 | 3789.1541 | 14000 | 2.3778 | 5887.8505 | 4166.6055 | 14000 | 2.2389 | 6253.1017 | 4525.696 | 14000 | 2.05 | 6829.2683 | 4973.6718
|  |  | 100 | mid | 11200 | 3.3389 | 3354.4093 | 1 | 11200 | 3.0889 | 3625.8993 | 1 | 11200 | 2.8389 | 3945.2055 | 1 | 11200 | 2.5889 | 4326.1803 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.2 | 5090.9091 | 1
|  |  | 4275.4939 | min | 5211.1111 | 3.7722 | 1381.4433 | 0.8945 | 4244.4444 | 2.5611 | 1657.2668 | 0.90916 | 4155.5556 | 2.2833 | 1819.9513 | 0.91031 | 4044.4444 | 1.9944 | 2027.8552 | 0.9117 | 3622.2222 | 1.6222 | 2232.8767 | 0.91662 | 3122.2222 | 1.2389 | 2520.1794 | 0.92178
| -4 |  | 2.5173 | max | 16233.3333 | 2.8833 | 5630.0578 | 3.4633 | 16033.3333 | 2.6667 | 6012.5 | 3.069 | 15800 | 2.45 | 6448.9796 | 2.8102 | 15600 | 2.2333 | 6985.0746 | 2.5496 | 14833.3333 | 2.1833 | 6793.8931 | 2.3432 | 14100 | 2.0833 | 6768 | 2.1236
|  | 10145.4545 | 45.7824 | nom | 14000 | 3.1667 | 4421.0526 | 2929.4074 | 14000 | 2.9167 | 4800 | 3305.7509 | 14000 | 2.6667 | 5250 | 3610.2622 | 14000 | 2.4167 | 5793.1034 | 3979.2946 | 14000 | 2.2833 | 6131.3869 | 4329.8324 | 14000 | 2.1 | 6666.6667 | 4777.4142
|  |  | 100 | mid | 11200 | 3.3833 | 3310.3448 | 1 | 11200 | 3.1333 | 3574.4681 | 1 | 11200 | 2.8833 | 3884.3931 | 1 | 11200 | 2.6333 | 4253.1646 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.25 | 4977.7778 | 1
|  |  | 4030.3557 | min | 5266.6667 | 3.8333 | 1373.913 | 0.82227 | 4366.6667 | 2.7167 | 1607.362 | 0.84568 | 4233.3333 | 2.4 | 1763.8889 | 0.84863 | 4066.6667 | 2.0667 | 1967.7419 | 0.85217 | 3633.3333 | 1.6833 | 2158.4158 | 0.86063 | 3133.3333 | 1.2833 | 2441.5584 | 0.86927
| -3 |  | 2.5685 | max | 16277.7778 | 2.9444 | 5528.3019 | 3.5451 | 16077.7778 | 2.7222 | 5906.1224 | 3.1105 | 15833.3333 | 2.5 | 6333.3333 | 2.8396 | 15633.3333 | 2.2778 | 6863.4146 | 2.5658 | 14877.7778 | 2.2278 | 6678.3042 | 2.3523 | 14133.3333 | 2.1278 | 6642.2977 | 2.1217
|  | 9722.7273 | 44.952 | nom | 14000 | 3.2056 | 4367.4177 | 2742.6083 | 14000 | 2.9556 | 4736.8421 | 3125.7584 | 14000 | 2.7056 | 5174.538 | 3423.9561 | 14000 | 2.4556 | 5701.3575 | 3789.3134 | 14000 | 2.3278 | 6014.3198 | 4133.3333 | 14000 | 2.15 | 6511.6279 | 4582.4992
|  |  | 100 | mid | 11200 | 3.4278 | 3267.423 | 1 | 11200 | 3.1778 | 3524.4755 | 1 | 11200 | 2.9278 | 3825.4269 | 1 | 11200 | 2.6778 | 4182.5726 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1
|  |  | 3785.4389 | min | 5322.2222 | 3.8944 | 1366.6191 | 0.74867 | 4488.8889 | 2.8722 | 1562.8627 | 0.77988 | 4311.1111 | 2.5167 | 1713.0243 | 0.78556 | 4088.8889 | 2.1389 | 1911.6883 | 0.79226 | 3644.4444 | 1.7444 | 2089.172 | 0.80448 | 3144.4444 | 1.3278 | 2368.2008 | 0.81661
| -2 |  | 2.6371 | max | 16322.2222 | 3.0056 | 5430.6839 | 3.63 | 16122.2222 | 2.7778 | 5804 | 3.1662 | 15866.6667 | 2.55 | 6222.2222 | 2.8777 | 15666.6667 | 2.3222 | 6746.4115 | 2.5852 | 14922.2222 | 2.2722 | 6567.2372 | 2.3625 | 14166.6667 | 2.1722 | 6521.7391 | 2.1191
|  | 9300 | 44.1133 | nom | 14000 | 3.2444 | 4315.0685 | 2562.0179 | 14000 | 2.9944 | 4675.3247 | 2937.3201 | 14000 | 2.7444 | 5101.2146 | 3231.762 | 14000 | 2.4944 | 5612.4722 | 3597.3566 | 14000 | 2.3722 | 5901.6393 | 3936.4773 | 14000 | 2.2 | 6363.6364 | 4388.7368
|  |  | 100 | mid | 11200 | 3.4722 | 3225.6 | 1 | 11200 | 3.2222 | 3475.8621 | 1 | 11200 | 2.9722 | 3768.2243 | 1 | 11200 | 2.7222 | 4114.2857 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1
|  |  | 3526.6038 | min | 5377.7778 | 3.9556 | 1359.5506 | 0.67366 | 4611.1111 | 3.0278 | 1522.9358 | 0.71164 | 4388.8889 | 2.6333 | 1666.6667 | 0.72104 | 4111.1111 | 2.2111 | 1859.2965 | 0.73197 | 3655.5556 | 1.8056 | 2024.6154 | 0.74816 | 3155.5556 | 1.3722 | 2299.5951 | 0.76381
| -1 |  | 2.7177 | max | 16366.6667 | 3.0667 | 5336.9565 | 3.7181 | 16166.6667 | 2.8333 | 5705.8824 | 3.2367 | 15900 | 2.6 | 6115.3846 | 2.9247 | 15700 | 2.3667 | 6633.8028 | 2.6078 | 14966.6667 | 2.3167 | 6460.4317 | 2.3739 | 14200 | 2.2167 | 6406.015 | 2.1157
|  | 8877.2727 | 43.2656 | nom | 14000 | 3.2833 | 4263.9594 | 2387.6093 | 14000 | 3.0333 | 4615.3846 | 2742.6631 | 14000 | 2.7833 | 5029.9401 | 3035.2997 | 14000 | 2.5333 | 5526.3158 | 3404.1221 | 14000 | 2.4167 | 5793.1034 | 3739.5408 | 14000 | 2.25 | 6222.2222 | 4195.9375
|  |  | 100 | mid | 11200 | 3.5167 | 3184.8341 | 1 | 11200 | 3.2667 | 3428.5714 | 1 | 11200 | 3.0167 | 3712.7072 | 1 | 11200 | 2.7667 | 4048.1928 | 1 | 11200 | 2.6 | 4307.6923 | 1 | 11200 | 2.4 | 4666.6667 | 1
|  |  | 3266.4449 | min | 5433.3333 | 4.0167 | 1352.6971 | 0.59721 | 4733.3333 | 3.1833 | 1486.911 | 0.64082 | 4466.6667 | 2.75 | 1624.2424 | 0.65504 | 4133.3333 | 2.2833 | 1810.219 | 0.67131 | 3666.6667 | 1.8667 | 1964.2857 | 0.69167 | 3166.6667 | 1.4167 | 2235.2941 | 0.71086
| 0 |  | 2.8136 | max | 16411.1111 | 3.1278 | 5246.8917 | 3.8095 | 16211.1111 | 2.8889 | 5611.5385 | 3.3231 | 15933.3333 | 2.65 | 6012.5786 | 2.9809 | 15733.3333 | 2.4111 | 6525.3456 | 2.6336 | 15011.1111 | 2.3611 | 6357.6471 | 2.3864 | 14233.3333 | 2.2611 | 6294.8403 | 2.1116
|  | 8454.5455 | 42.4086 | nom | 14000 | 3.3222 | 4214.0468 | 2219.3414 | 14000 | 3.0722 | 4556.962 | 2544.1501 | 14000 | 2.8222 | 4960.6299 | 2836.2376 | 14000 | 2.5722 | 5442.7646 | 3210.3033 | 14000 | 2.4611 | 5688.4876 | 3542.7973 | 14000 | 2.3 | 6086.9565 | 4003.9117
|  |  | 100 | mid | 11200 | 3.5611 | 3145.0858 | 1 | 11200 | 3.3111 | 3382.5503 | 1 | 11200 | 3.0611 | 3658.8022 | 1 | 11200 | 2.8111 | 3984.1897 | 1 | 11200 | 2.65 | 4226.4151 | 1 | 11200 | 2.45 | 4571.4286 | 1
|  |  | 3004.906 | min | 5488.8889 | 4.0778 | 1346.049 | 0.51928 | 4855.5556 | 3.3389 | 1454.2429 | 0.56727 | 4544.4444 | 2.8667 | 1585.2713 | 0.58749 | 4155.5556 | 2.3556 | 1764.1509 | 0.61027 | 3677.7778 | 1.9278 | 1907.781 | 0.63502 | 3177.7778 | 1.4611 | 2174.9049 | 0.65777
| 1 |  | 2.9282 | max | 16455.5556 | 3.1889 | 5160.2787 | 3.9043 | 16255.5556 | 2.9444 | 5520.7547 | 3.4263 | 15966.6667 | 2.7 | 5913.5802 | 3.0467 | 15766.6667 | 2.4556 | 6420.8145 | 2.6626 | 15055.5556 | 2.4056 | 6258.6605 | 2.4001 | 14266.6667 | 2.3056 | 6187.9518 | 2.1067
|  | 8031.8182 | 41.5417 | nom | 14000 | 3.3611 | 4165.2893 | 2057.1602 | 14000 | 3.1111 | 4500 | 2344.1845 | 14000 | 2.8611 | 4893.2039 | 2636.2463 | 14000 | 2.6111 | 5361.7021 | 3016.5806 | 14000 | 2.5056 | 5587.5831 | 3346.5159 | 14000 | 2.35 | 5957.4468 | 3812.4689
|  |  | 100 | mid | 11200 | 3.6056 | 3106.3174 | 1 | 11200 | 3.3556 | 3337.7483 | 1 | 11200 | 3.1056 | 3606.4401 | 1 | 11200 | 2.8556 | 3922.179 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.5 | 4480 | 1
|  |  | 2742.8772 | min | 5544.4444 | 4.1389 | 1339.5973 | 0.43981 | 4977.7778 | 3.4944 | 1424.4833 | 0.49083 | 4622.2222 | 2.9833 | 1549.3482 | 0.51835 | 4177.7778 | 2.4278 | 1720.8238 | 0.54883 | 3688.8889 | 1.9889 | 1854.7486 | 0.5782 | 3188.8889 | 1.5056 | 2118.0812 | 0.60453
14kW-Maximum heating CAP | 2 |  | 3.0656 | max | 16500 | 3.25 | 5076.9231 | 4.0027 | 16300 | 3 | 5433.3333 | 3.5472 | 16000 | 2.75 | 5818.1818 | 3.1224 | 15800 | 2.5 | 6320 | 2.6948 | 15100 | 2.45 | 6163.2653 | 2.4148 | 14300 | 2.35 | 6085.1064 | 2.1011
|  | 7609.0909 | 40.6641 | nom | 14000 | 3.4 | 4117.6471 | 1900.9997 | 14000 | 3.15 | 4444.4444 | 2145.1169 | 14000 | 2.9 | 4827.5862 | 2436.9541 | 14000 | 2.65 | 5283.0189 | 2823.6145 | 14000 | 2.55 | 5490.1961 | 3150.96 | 14000 | 2.4 | 5833.3333 | 3621.417
|  |  | 100 | mid | 11200 | 3.65 | 3068.4932 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 3.15 | 3555.5556 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.55 | 4392.1569 | 1
|  |  | 2482.1016 | min | 5600 | 4.2 | 1333.3333 | 0.35877 | 5100 | 3.65 | 1397.2603 | 0.41133 | 4700 | 3.1 | 1516.129 | 0.44755 | 4200 | 2.5 | 1680 | 0.48701 | 3700 | 2.05 | 1804.878 | 0.52121 | 3200 | 1.55 | 2064.5161 | 0.55114
| 3 |  | 3.2866 | max | 16560 | 3.54 | 4677.9661 | 4.4596 | 16360 | 3.25 | 5033.8462 | 3.7631 | 16080 | 2.96 | 5432.4324 | 3.2642 | 15860 | 2.66 | 5962.406 | 2.7667 | 15160 | 2.54 | 5968.5039 | 2.4421 | 14360 | 2.38 | 6033.6134 | 2.0865
|  | 7186.3636 | 39.7753 | nom | 14000 | 3.7 | 3783.7838 | 1611.4238 | 14000 | 3.41 | 4105.5718 | 1909.7001 | 14000 | 3.12 | 4487.1795 | 2201.57 | 14000 | 2.82 | 4964.539 | 2597.469 | 14000 | 2.67 | 5243.4457 | 2942.6396 | 14000 | 2.47 | 5668.0162 | 3444.2523
|  |  | 100 | mid | 11200 | 3.97 | 2821.1587 | 1 | 11200 | 3.68 | 3043.4783 | 1 | 11200 | 3.39 | 3303.8348 | 1 | 11200 | 3.09 | 3624.5955 | 1 | 11200 | 2.88 | 3888.8889 | 1 | 11200 | 2.62 | 4274.8092 | 1
|  |  | 2186.5494 | min | 5380 | 4.68 | 1149.5726 | 0.31037 | 4920 | 3.81 | 1291.3386 | 0.36089 | 4500 | 3.18 | 1415.0943 | 0.40095 | 4000 | 2.51 | 1593.6255 | 0.44255 | 3500 | 2.04 | 1715.6863 | 0.47875 | 3000 | 1.53 | 1960.7843 | 0.51053
| 4 |  | 3.5215 | max | 16620 | 3.83 | 4339.4256 | 4.929 | 16420 | 3.5 | 4691.4286 | 3.9669 | 16160 | 3.17 | 5097.7918 | 3.3921 | 15920 | 2.82 | 5645.3901 | 2.8244 | 15220 | 2.63 | 5787.0722 | 2.4597 | 14420 | 2.41 | 5983.4025 | 2.0668
|  | 6763.6364 | 38.8742 | nom | 14000 | 4 | 3500 | 1372.2092 | 14000 | 3.67 | 3814.7139 | 1705.0321 | 14000 | 3.34 | 4191.6168 | 1993.9331 | 14000 | 2.99 | 4682.2742 | 2394.7387 | 14000 | 2.79 | 5017.9211 | 2749.8187 | 14000 | 2.54 | 5511.811 | 3272.5216
|  |  | 100 | mid | 11200 | 4.29 | 2610.7226 | 1 | 11200 | 3.96 | 2828.2828 | 1 | 11200 | 3.63 | 3085.3994 | 1 | 11200 | 3.28 | 3414.6341 | 1 | 11200 | 3.01 | 3720.9302 | 1 | 11200 | 2.69 | 4163.5688 | 1
|  |  | 1920.6596 | min | 5160 | 5.16 | 1000 | 0.2655 | 4740 | 3.97 | 1193.9547 | 0.31326 | 4300 | 3.26 | 1319.0184 | 0.35705 | 3800 | 2.52 | 1507.9365 | 0.40049 | 3300 | 2.03 | 1625.6158 | 0.43843 | 2800 | 1.51 | 1854.3046 | 0.47186
| 5 |  | 3.7734 | max | 16680 | 4.12 | 4048.5437 | 5.4095 | 16480 | 3.75 | 4394.6667 | 4.1595 | 16240 | 3.38 | 4804.7337 | 3.5073 | 15980 | 2.98 | 5362.4161 | 2.869 | 15280 | 2.72 | 5617.6471 | 2.4681 | 14480 | 2.44 | 5934.4262 | 2.0424
|  | 6340.9091 | 37.9601 | nom | 14000 | 4.3 | 3255.814 | 1172.1805 | 14000 | 3.93 | 3562.341 | 1524.4391 | 14000 | 3.56 | 3932.5843 | 1807.9283 | 14000 | 3.16 | 4430.3797 | 2210.1405 | 14000 | 2.91 | 4810.9966 | 2569.1192 | 14000 | 2.61 | 5363.9847 | 3104.5807
|  |  | 100 | mid | 11200 | 4.61 | 2429.5011 | 1 | 11200 | 4.24 | 2641.5094 | 1 | 11200 | 3.87 | 2894.0568 | 1 | 11200 | 3.47 | 3227.6657 | 1 | 11200 | 3.14 | 3566.879 | 1 | 11200 | 2.76 | 4057.971 | 1
|  |  | 1680.4349 | min | 4940 | 5.64 | 875.8865 | 0.22379 | 4560 | 4.13 | 1104.1162 | 0.26821 | 4100 | 3.34 | 1227.5449 | 0.31562 | 3600 | 2.53 | 1422.9249 | 0.36065 | 3100 | 2.02 | 1534.6535 | 0.40011 | 2600 | 1.49 | 1744.9664 | 0.43499
| 6 |  | 4.0448 | max | 16740 | 4.41 | 3795.9184 | 5.9 | 16540 | 4 | 4135 | 4.3419 | 16320 | 3.59 | 4545.961 | 3.6108 | 16040 | 3.14 | 5108.2803 | 2.9016 | 15340 | 2.81 | 5459.0747 | 2.4682 | 14540 | 2.47 | 5886.6397 | 2.0137
|  | 5918.1818 | 37.0318 | nom | 14000 | 4.6 | 3043.4783 | 1003.0879 | 14000 | 4.19 | 3341.2888 | 1363.0478 | 14000 | 3.78 | 3703.7037 | 1639.0406 | 14000 | 3.33 | 4204.2042 | 2039.6375 | 14000 | 3.03 | 4620.462 | 2397.7901 | 14000 | 2.68 | 5223.8806 | 2938.9313
|  |  | 100 | mid | 11200 | 4.93 | 2271.8053 | 1 | 11200 | 4.52 | 2477.8761 | 1 | 11200 | 4.11 | 2725.0608 | 1 | 11200 | 3.66 | 3060.1093 | 1 | 11200 | 3.27 | 3425.0765 | 1 | 11200 | 2.83 | 3957.5972 | 1
|  |  | 1463.1648 | min | 4720 | 6.12 | 771.2418 | 0.1849 | 4380 | 4.29 | 1020.979 | 0.22554 | 3900 | 3.42 | 1140.3509 | 0.27646 | 3400 | 2.54 | 1338.5827 | 0.32284 | 2900 | 2.01 | 1442.7861 | 0.36364 | 2400 | 1.47 | 1632.6531 | 0.39979
| 7 |  | 4.3382 | max | 16800 | 4.7 | 3574.4681 | 6.3994 | 16600 | 4.25 | 3905.8824 | 4.5148 | 16400 | 3.8 | 4315.7895 | 3.7035 | 16100 | 3.3 | 4878.7879 | 2.923 | 15400 | 2.9 | 5310.3448 | 2.4604 | 14600 | 2.5 | 5840 | 1.9809
|  | 5495.4545 | 36.088 | nom | 14000 | 4.9 | 2857.1429 | 858.7421 | 14000 | 4.45 | 3146.0674 | 1217.2162 | 14000 | 4 | 3500 | 1483.8604 | 14000 | 3.5 | 4000 | 1880.0661 | 14000 | 3.15 | 4444.4444 | 2233.5362 | 14000 | 2.75 | 5090.9091 | 2774.173
|  |  | 100 | mid | 11200 | 5.25 | 2133.3333 | 1 | 11200 | 4.8 | 2333.3333 | 1 | 11200 | 4.35 | 2574.7126 | 1 | 11200 | 3.85 | 2909.0909 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 2.9 | 3862.069 | 1
|  |  | 1266.7495 | min | 4500 | 6.6 | 681.8182 | 0.14858 | 4200 | 4.45 | 943.8202 | 0.18506 | 3700 | 3.5 | 1057.1429 | 0.23939 | 3200 | 2.55 | 1254.902 | 0.28693 | 2700 | 2 | 1350 | 0.32888 | 2200 | 1.45 | 1517.2414 | 0.36616
| 8 |  | 4.5507 | max | 16860 | 4.81 | 3505.1975 | 6.2871 | 16640 | 4.38 | 3799.0868 | 4.5694 | 16440 | 3.93 | 4183.2061 | 3.8377 | 16160 | 3.48 | 4643.6782 | 3.1279 | 15440 | 3.06 | 5045.7516 | 2.6303 | 14640 | 2.64 | 5545.4545 | 2.1235
|  | 5072.7273 | 35.1273 | nom | 14000 | 5.02 | 2788.8446 | 806.8418 | 14000 | 4.59 | 3050.1089 | 1110.1599 | 14000 | 4.16 | 3365.3846 | 1321.8307 | 14000 | 3.69 | 3794.0379 | 1621.7463 | 14000 | 3.32 | 4216.8675 | 1928.5936 | 14000 | 2.9 | 4827.5862 | 2388.8683
|  |  | 100 | mid | 11200 | 5.37 | 2085.6611 | 1 | 11200 | 4.95 | 2262.6263 | 1 | 11200 | 4.53 | 2472.4062 | 1 | 11200 | 4.06 | 2758.6207 | 1 | 11200 | 3.58 | 3128.4916 | 1 | 11200 | 3.06 | 3660.1307 | 1
|  |  | 1114.7059 | min | 4920 | 6.31 | 779.7147 | 0.02432 | 4600 | 4.54 | 1013.2159 | 0.071625 | 4120 | 3.73 | 1104.5576 | 0.13457 | 3640 | 2.91 | 1250.8591 | 0.18951 | 3200 | 2.34 | 1367.5214 | 0.23409 | 2760 | 1.77 | 1559.322 | 0.27402
| 9 |  | 4.7484 | max | 16920 | 4.92 | 3439.0244 | 6.02 | 16680 | 4.51 | 3698.4479 | 4.63 | 16480 | 4.06 | 4059.1133 | 3.9724 | 16220 | 3.66 | 4431.694 | 3.3501 | 15480 | 3.22 | 4807.4534 | 2.8168 | 14680 | 2.78 | 5280.5755 | 2.2807
|  | 4650 | 34.148 | nom | 14000 | 5.14 | 2723.7354 | 772.4252 | 14000 | 4.73 | 2959.8309 | 1004.3197 | 14000 | 4.32 | 3240.7407 | 1170.5807 | 14000 | 3.88 | 3608.2474 | 1388.0364 | 14000 | 3.49 | 4011.4613 | 1650.8094 | 14000 | 3.05 | 4590.1639 | 2038.8268
|  |  | 92.4643 | mid | 11200 | 5.49 | 2040.0729 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.71 | 2377.9193 | 1 | 11200 | 4.27 | 2622.9508 | 1 | 11200 | 3.76 | 2978.7234 | 1 | 11200 | 3.22 | 3478.2609 | 1
|  |  | 979.2708 | min | 5340 | 6.02 | 887.0432 | 0 | 5000 | 4.63 | 1079.9136 | 0 | 4540 | 3.96 | 1146.4646 | 0.016517 | 4080 | 3.27 | 1247.7064 | 0.080056 | 3700 | 2.68 | 1380.597 | 0.12667 | 3320 | 2.09 | 1588.5167 | 0.16878
| 10 |  | 4.9071 | max | 16980 | 5.03 | 3375.7455 | 5.73 | 16720 | 4.64 | 3603.4483 | 4.72 | 16520 | 4.19 | 3942.7208 | 4.19 | 16280 | 3.84 | 4239.5833 | 3.63 | 15520 | 3.38 | 4591.716 | 3.0236 | 14720 | 2.92 | 5041.0959 | 2.456
|  | 4227.2727 | 33.1478 | nom | 14000 | 5.26 | 2661.597 | 737.7439 | 14000 | 4.87 | 2874.7433 | 895.6086 | 14000 | 4.48 | 3125 | 1008.8956 | 14000 | 4.07 | 3439.8034 | 1164.5379 | 14000 | 3.66 | 3825.1366 | 1398.0998 | 14000 | 3.2 | 4375 | 1721.1894
|  |  | 77.328 | mid | 11200 | 5.61 | 1996.4349 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.89 | 2290.3885 | 0 | 11200 | 4.48 | 2500 | 0 | 11200 | 3.94 | 2842.6396 | 1 | 11200 | 3.38 | 3313.6095 | 1
|  |  | 861.4658 | min | 5760 | 5.73 | 1005.2356 | 0 | 5400 | 4.72 | 1144.0678 | 0 | 4960 | 4.19 | 1183.7709 | 0 | 4520 | 3.63 | 1245.1791 | 0 | 4200 | 3.02 | 1390.7285 | 0.0038961 | 3880 | 2.41 | 1609.9585 | 0.047442
| 11 |  | 4.9912 | max | 17040 | 5.14 | 3315.1751 | 5.44 | 16760 | 4.77 | 3513.6268 | 4.81 | 16560 | 4.32 | 3833.3333 | 4.42 | 16340 | 4.02 | 4064.6766 | 3.99 | 15560 | 3.54 | 4395.4802 | 3.36 | 14760 | 3.06 | 4823.5294 | 2.73
|  | 3804.5455 | 32.1243 | nom | 14000 | 5.38 | 2602.2305 | 699.365 | 14000 | 5.01 | 2794.4112 | 790.9658 | 14000 | 4.64 | 3017.2414 | 860.7569 | 14000 | 4.26 | 3286.385 | 953.5202 | 14000 | 3.83 | 3655.3525 | 1132.3052 | 14000 | 3.35 | 4179.1045 | 1393.6064
|  |  | 64.3826 | mid | 11200 | 5.73 | 1954.6248 | 0 | 11200 | 5.4 | 2074.0741 | 0 | 11200 | 5.07 | 2209.073 | 0 | 11200 | 4.69 | 2388.0597 | 0 | 11200 | 4.12 | 2718.4466 | 0 | 11200 | 3.54 | 3163.8418 | 0
|  |  | 762.2551 | min | 6180 | 5.44 | 1136.0294 | 0 | 5800 | 4.81 | 1205.8212 | 0 | 5380 | 4.42 | 1217.1946 | 0 | 4960 | 3.99 | 1243.1078 | 0 | 4700 | 3.36 | 1398.8095 | 0 | 4440 | 2.73 | 1626.3736 | 0
| 12 |  | 4.9981 | max | 17100 | 5.25 | 3257.1429 | 5.15 | 16800 | 4.9 | 3428.5714 | 4.9 | 16600 | 4.45 | 3730.3371 | 4.65 | 16400 | 4.2 | 3904.7619 | 4.35 | 15600 | 3.7 | 4216.2162 | 3.7 | 14800 | 3.2 | 4625 | 3.05
|  | 3381.8182 | 31.0741 | nom | 14000 | 5.5 | 2545.4545 | 656.6637 | 14000 | 5.15 | 2718.4466 | 690.167 | 14000 | 4.8 | 2916.6667 | 727.2727 | 14000 | 4.45 | 3146.0674 | 777.4295 | 14000 | 4 | 3500 | 914.0049 | 14000 | 3.5 | 4000 | 1108.7928
|  |  | 53.198 | mid | 11200 | 5.85 | 1914.5299 | 0 | 11200 | 5.55 | 2018.018 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.9 | 2285.7143 | 0 | 11200 | 4.3 | 2604.6512 | 0 | 11200 | 3.7 | 3027.027 | 0
|  |  | 676.6143 | min | 6600 | 5.15 | 1281.5534 | 0 | 6200 | 4.9 | 1265.3061 | 0 | 5800 | 4.65 | 1247.3118 | 0 | 5400 | 4.35 | 1241.3793 | 0 | 5200 | 3.7 | 1405.4054 | 0 | 5000 | 3.05 | 1639.3443 | 0
| 13 |  | 5.0585 | max | 17566.6667 | 5.2833 | 3324.9211 | 5.15 | 17266.6667 | 4.9333 | 3500 | 4.9667 | 17033.3333 | 4.55 | 3743.5897 | 4.7833 | 16833.3333 | 4.3 | 3914.7287 | 4.55 | 16033.3333 | 3.8 | 4219.2982 | 3.9167 | 15200 | 3.3 | 4606.0606 | 3.2667
|  | 2959.0909 | 29.9931 | nom | 14000 | 5.5 | 2545.4545 | 574.5808 | 14000 | 5.1833 | 2700.9646 | 595.7901 | 14000 | 4.8667 | 2876.7123 | 618.6253 | 14000 | 4.55 | 3076.9231 | 650.3497 | 14000 | 4.1 | 3414.6341 | 755.5126 | 14000 | 3.6167 | 3870.9677 | 905.8442
|  |  | 45.6394 | mid | 11200 | 5.9 | 1898.3051 | 0 | 11200 | 5.5833 | 2005.9701 | 0 | 11200 | 5.3167 | 2106.5831 | 0 | 11200 | 5.0167 | 2232.5581 | 0 | 11200 | 4.4167 | 2535.8491 | 0 | 11200 | 3.8167 | 2934.4978 | 0
|  |  | 584.9785 | min | 6700 | 5.15 | 1300.9709 | 0 | 6266.6667 | 4.9667 | 1261.745 | 0 | 5833.3333 | 4.7833 | 1219.5122 | 0 | 5400 | 4.55 | 1186.8132 | 0 | 5233.3333 | 3.9167 | 1336.1702 | 0 | 5066.6667 | 3.2667 | 1551.0204 | 0
| 14 |  | 5.1048 | max | 18033.3333 | 5.3167 | 3391.8495 | 5.15 | 17733.3333 | 4.9667 | 3570.4698 | 5.0333 | 17466.6667 | 4.65 | 3756.2724 | 4.9167 | 17266.6667 | 4.4 | 3924.2424 | 4.75 | 16466.6667 | 3.9 | 4222.2222 | 4.1333 | 15600 | 3.4 | 4588.2353 | 3.4833
|  | 2536.3636 | 28.8757 | nom | 14000 | 5.5 | 2545.4545 | 492.4978 | 14000 | 5.2167 | 2683.7061 | 503.9133 | 14000 | 4.9333 | 2837.8378 | 515.8706 | 14000 | 4.65 | 3010.7527 | 533.9713 | 14000 | 4.2 | 3333.3333 | 613.6364 | 14000 | 3.7333 | 3750 | 728.1427
|  |  | 38.3187 | mid | 11200 | 5.95 | 1882.3529 | 0 | 11200 | 5.6167 | 1994.0653 | 0 | 11200 | 5.3833 | 2080.4954 | 0 | 11200 | 5.1333 | 2181.8182 | 0 | 11200 | 4.5333 | 2470.5882 | 0 | 11200 | 3.9333 | 2847.4576 | 0
|  |  | 496.8601 | min | 6800 | 5.15 | 1320.3883 | 0 | 6333.3333 | 5.0333 | 1258.2781 | 0 | 5866.6667 | 4.9167 | 1193.2203 | 0 | 5400 | 4.75 | 1136.8421 | 0 | 5266.6667 | 4.1333 | 1274.1935 | 0 | 5133.3333 | 3.4833 | 1473.6842 | 0
| 15 |  | 5.1364 | max | 18500 | 5.35 | 3457.9439 | 5.15 | 18200 | 5 | 3640 | 5.1 | 17900 | 4.75 | 3768.4211 | 5.05 | 17700 | 4.5 | 3933.3333 | 4.95 | 16900 | 4 | 4225 | 4.35 | 16000 | 3.5 | 4571.4286 | 3.7
|  | 2113.6364 | 27.7142 | nom | 14000 | 5.5 | 2545.4545 | 410.4148 | 14000 | 5.25 | 2666.6667 | 414.4385 | 14000 | 5 | 2800 | 418.5419 | 14000 | 4.75 | 2947.3684 | 426.9972 | 14000 | 4.3 | 3255.814 | 485.8934 | 14000 | 3.85 | 3636.3636 | 571.2531
|  |  | 31.247 | mid | 11200 | 6 | 1866.6667 | 0 | 11200 | 5.65 | 1982.3009 | 0 | 11200 | 5.45 | 2055.0459 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.65 | 2408.6022 | 0 | 11200 | 4.05 | 2765.4321 | 0
|  |  | 411.4992 | min | 6900 | 5.15 | 1339.8058 | 0 | 6400 | 5.1 | 1254.902 | 0 | 5900 | 5.05 | 1168.3168 | 0 | 5400 | 4.95 | 1090.9091 | 0 | 5300 | 4.35 | 1218.3908 | 0 | 5200 | 3.7 | 1405.4054 | 0
| 16 |  | 6.7343 | max | 19020 | 5.73 | 3319.3717 | 6.92 | 18720 | 5.3 | 3532.0755 | 5.68 | 18420 | 4.95 | 3721.2121 | 5.37 | 18200 | 4.59 | 3965.1416 | 5.02 | 17380 | 4.08 | 4259.8039 | 4.36 | 16460 | 3.56 | 4623.5955 | 3.65
|  | 1690.9091 | 26.4975 | nom | 14000 | 5.93 | 2360.8769 | 244.351 | 14000 | 5.57 | 2513.465 | 297.6953 | 14000 | 5.21 | 2687.1401 | 314.8807 | 14000 | 4.85 | 2886.5979 | 336.8345 | 14000 | 4.39 | 3189.0661 | 387.8232 | 14000 | 3.92 | 3571.4286 | 463.2628
|  |  | 24.4984 | mid | 11200 | 6.42 | 1744.5483 | 0 | 11200 | 5.99 | 1869.783 | 0 | 11200 | 5.68 | 1971.831 | 0 | 11200 | 5.36 | 2089.5522 | 0 | 11200 | 4.74 | 2362.8692 | 0 | 11200 | 4.12 | 2718.4466 | 0
|  |  | 251.0887 | min | 6980 | 6.92 | 1008.6705 | 0 | 6460 | 5.68 | 1137.3239 | 0 | 6000 | 5.37 | 1117.3184 | 0 | 5520 | 5.02 | 1099.6016 | 0 | 5360 | 4.36 | 1229.3578 | 0 | 5180 | 3.65 | 1419.1781 | 0
| 17 |  | 8.6395 | max | 19540 | 6.11 | 3198.036 | 8.69 | 19240 | 5.6 | 3435.7143 | 6.26 | 18940 | 5.15 | 3677.6699 | 5.69 | 18700 | 4.68 | 3995.7265 | 5.09 | 17860 | 4.16 | 4293.2692 | 4.37 | 16920 | 3.62 | 4674.0331 | 3.6
|  | 1268.1818 | 25.2076 | nom | 14000 | 6.36 | 2201.2579 | 145.9358 | 14000 | 5.89 | 2376.91 | 202.585 | 14000 | 5.42 | 2583.0258 | 222.8791 | 14000 | 4.95 | 2828.2828 | 249.1516 | 14000 | 4.48 | 3125 | 290.2018 | 14000 | 3.99 | 3508.7719 | 352.2727
|  |  | 17.9915 | mid | 11200 | 6.84 | 1637.4269 | 0 | 11200 | 6.33 | 1769.3523 | 0 | 11200 | 5.91 | 1895.0931 | 0 | 11200 | 5.47 | 2047.532 | 0 | 11200 | 4.83 | 2318.8406 | 0 | 11200 | 4.19 | 2673.031 | 0
|  |  | 146.788 | min | 7060 | 8.69 | 812.4281 | 0 | 6520 | 6.26 | 1041.5335 | 0 | 6100 | 5.69 | 1072.0562 | 0 | 5640 | 5.09 | 1108.055 | 0 | 5420 | 4.37 | 1240.2746 | 0 | 5160 | 3.6 | 1433.3333 | 0
| 18 |  | 10.46 | max | 20060 | 6.49 | 3090.9091 | 10.46 | 19760 | 5.9 | 3349.1525 | 6.84 | 19460 | 5.35 | 3637.3832 | 6.01 | 19200 | 4.77 | 4025.1572 | 5.16 | 18340 | 4.24 | 4325.4717 | 4.38 | 17380 | 3.68 | 4722.8261 | 3.55
|  | 845.4545 | 23.8123 | nom | 14000 | 6.79 | 2061.8557 | 80.8274 | 14000 | 6.21 | 2254.4283 | 123.6045 | 14000 | 5.63 | 2486.6785 | 140.6746 | 14000 | 5.05 | 2772.2772 | 163.8478 | 14000 | 4.57 | 3063.4573 | 193.0262 | 14000 | 4.06 | 3448.2759 | 238.1562
|  |  | 11.8411 | mid | 11200 | 7.26 | 1542.6997 | 0 | 11200 | 6.67 | 1679.1604 | 0 | 11200 | 6.14 | 1824.1042 | 0 | 11200 | 5.58 | 2007.1685 | 0 | 11200 | 4.92 | 2276.4228 | 0 | 11200 | 4.26 | 2629.108 | 0
|  |  | 80.8274 | min | 7140 | 10.46 | 682.6004 | 0 | 6580 | 6.84 | 961.9883 | 0 | 6200 | 6.01 | 1031.614 | 0 | 5760 | 5.16 | 1116.2791 | 0 | 5480 | 4.38 | 1251.1416 | 0 | 5140 | 3.55 | 1447.8873 | 0
| 19 |  | 12.23 | max | 20580 | 6.87 | 2995.6332 | 12.23 | 20280 | 6.2 | 3270.9677 | 7.42 | 19980 | 5.55 | 3600 | 6.33 | 19700 | 4.86 | 4053.4979 | 5.23 | 18820 | 4.32 | 4356.4815 | 4.39 | 17840 | 3.74 | 4770.0535 | 3.5
|  | 422.7273 | 22.2368 | nom | 14000 | 7.22 | 1939.0582 | 34.5648 | 14000 | 6.53 | 2143.951 | 56.9713 | 14000 | 5.84 | 2397.2603 | 66.7816 | 14000 | 5.15 | 2718.4466 | 80.8274 | 14000 | 4.66 | 3004.2918 | 96.2932 | 14000 | 4.13 | 3389.8305 | 120.7792
|  |  | 5.8549 | mid | 11200 | 7.68 | 1458.3333 | 0 | 11200 | 7.01 | 1597.7175 | 0 | 11200 | 6.37 | 1758.2418 | 0 | 11200 | 5.69 | 1968.3656 | 0 | 11200 | 5.01 | 2235.5289 | 0 | 11200 | 4.33 | 2586.6051 | 0
|  |  | 34.5648 | min | 7220 | 12.23 | 590.3516 | 0 | 6640 | 7.42 | 894.8787 | 0 | 6300 | 6.33 | 995.2607 | 0 | 5880 | 5.23 | 1124.283 | 0 | 5540 | 4.39 | 1261.959 | 0 | 5120 | 3.5 | 1462.8571 | 0
| 20 |  | 14 | max | 21100 | 7.25 | 2910.3448 | 14 | 20800 | 6.5 | 3200 | 8 | 20500 | 5.75 | 3565.2174 | 6.65 | 20200 | 4.95 | 4080.8081 | 5.3 | 19300 | 4.4 | 4386.3636 | 4.4 | 18300 | 3.8 | 4815.7895 | 3.45
|  | 0 | 20 | nom | 14000 | 7.65 | 1830.0654 | 0 | 14000 | 6.85 | 2043.7956 | 0 | 14000 | 6.05 | 2314.0496 | 0 | 14000 | 5.25 | 2666.6667 | 0 | 14000 | 4.75 | 2947.3684 | 0 | 14000 | 4.2 | 3333.3333 | 0
|  |  | 0 | mid | 11200 | 8.1 | 1382.716 | 0 | 11200 | 7.35 | 1523.8095 | 0 | 11200 | 6.6 | 1696.9697 | 0 | 11200 | 5.8 | 1931.0345 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.4 | 2545.4545 | 0
|  |  | 0 | min | 7300 | 14 | 521.4286 | 0 | 6700 | 8 | 837.5 | 0 | 6400 | 6.65 | 962.406 | 0 | 6000 | 5.3 | 1132.0755 | 0 | 5600 | 4.4 | 1272.7273 | 0 | 5100 | 3.45 | 1478.2609 | 0
Indoor Temp. |  | 21
LWT |  |  | 25 CAP: 25; 35 CAP: 35; 40 CAP: 40; 45 CAP: 45; 50 CAP: 50; 55 CAP: 55
Outdoor air temperature[℃] |  | Heating Demand | COP | CL | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP
|  |  | LWT |  |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI
| -15 |  | 0.4446 | max | - | - | - | - | 14000 | 1.85 | 7567.5676 | 1.6673 | 13500 | 1.7 | 7941.1765 | 1.4251 | 13100 | 1.55 | 8451.6129 | 1.197 | 12600 | 1.45 | 8689.6552 | 0.95909 | 12200 | 1.3 | 9384.6154 | 0.54545
|  | 15218.1818 | 56.2192 | nom | - | - | - | - | 11000 | 2.3 | 4782.6087 | 9127.59 | 11000 | 2.1 | 5238.0952 | 10678.7446 | 11000 | 1.9 | 5789.4737 | 12713.9241 | 11000 | 1.75 | 6285.7143 | 15867.2986 | 11000 | 1.6 | 6875 | 27900
|  |  | 100 | mid | - | - | - | - | 8800 | 2.5 | 3520 | 3 | 8800 | 2.3 | 3826.087 | 3 | 8800 | 2.1 | 4190.4762 | 3 | 8800 | 1.9 | 4631.5789 | 3 | 8800 | 1.7 | 5176.4706 | 3
|  |  | 34229.1149 | min | - | - | - | - | 7800 | 2.35 | 3319.1489 | 1.4061 | 7200 | 2 | 3600 | 1.6873 | 6500 | 1.6 | 4062.5 | 2.0087 | 5700 | 1.3 | 4384.6154 | 2.6364 | 4800 | 1 | 4800 | 3.5152
| -14 |  | 1.7461 | max | 14280 | 2.08 | 6865.3846 | 1.0491 | 14080 | 1.93 | 7295.3368 | -1.7367 | 13640 | 1.78 | 7662.9213 | 2.8713 | 13280 | 1.62 | 8197.5309 | 2.2093 | 12880 | 1.53 | 8418.3007 | 1.9405 | 12560 | 1.39 | 9035.9712 | 1.7626
|  | 14795.4545 | 55.4642 | nom | 14000 | 2.64 | 5303.0303 | 14103.1196 | 14000 | 2.34 | 5982.906 | -8519.2698 | 14000 | 2.12 | 6603.7736 | 5152.9437 | 14000 | 1.9 | 7368.4211 | 6696.7653 | 14000 | 1.77 | 7909.6045 | 7624.7365 | 14000 | 1.63 | 8588.9571 | 8394.2233
|  |  | 100 | mid | 11200 | 2.69 | 4163.5688 | 3 | 11200 | 2.54 | 4409.4488 | 3 | 11200 | 2.35 | 4765.9574 | 3 | 11200 | 2.15 | 5209.3023 | 3 | 11200 | 1.94 | 5773.1959 | 3 | 11200 | 1.73 | 6473.9884 | 3
|  |  | 8473.6098 | min | 7720 | 2.59 | 2980.695 | 2.8409 | 7420 | 2.34 | 3170.9402 | 9.9432 | 6880 | 2.01 | 3422.8856 | -2.2096 | 6260 | 1.63 | 3840.4908 | -1.1048 | 5480 | 1.33 | 4120.3008 | -0.71023 | 4640 | 1.02 | 4549.0196 | -0.5524
| -13 |  | 1.7309 | max | 14360 | 2.16 | 6648.1481 | 2.1416 | 14160 | 2.01 | 7044.7761 | 1.5181 | 13780 | 1.86 | 7408.6022 | 2.6144 | 13460 | 1.69 | 7964.497 | 2.0449 | 13160 | 1.61 | 8173.913 | 1.8699 | 12920 | 1.48 | 8729.7297 | 1.7221
|  | 14372.7273 | 54.7042 | nom | 14000 | 2.68 | 5223.8806 | 6711.1593 | 14000 | 2.38 | 5882.3529 | 9467.7745 | 14000 | 2.14 | 6542.0561 | 5497.5659 | 14000 | 1.9 | 7368.4211 | 7028.4021 | 14000 | 1.79 | 7821.2291 | 7686.4842 | 14000 | 1.66 | 8433.7349 | 8345.944
|  |  | 100 | mid | 11200 | 2.73 | 4102.5641 | 3 | 11200 | 2.58 | 4341.0853 | 3 | 11200 | 2.4 | 4666.6667 | 3 | 11200 | 2.2 | 5090.9091 | 3 | 11200 | 1.98 | 5656.5657 | 3 | 11200 | 1.76 | 6363.6364 | 3
|  |  | 8303.7948 | min | 7340 | 2.58 | 2844.9612 | 1.0354 | 7040 | 2.33 | 3021.4592 | 2.3295 | 6560 | 2.02 | 3247.5248 | -1.6942 | 6020 | 1.66 | 3626.506 | -0.69024 | 5260 | 1.36 | 3867.6471 | -0.44372 | 4480 | 1.04 | 4307.6923 | -0.34512
| -12 |  | 1.7177 | max | 14440 | 2.24 | 6446.4286 | 2.7209 | 14240 | 2.09 | 6813.3971 | 2.4236 | 13920 | 1.94 | 7175.2577 | 2.1652 | 13640 | 1.76 | 7750 | 1.9062 | 13440 | 1.69 | 7952.6627 | 1.8137 | 13280 | 1.57 | 8458.5987 | 1.6918
|  | 13950 | 53.939 | nom | 14000 | 2.72 | 5147.0588 | 5126.9935 | 14000 | 2.42 | 5785.124 | 5755.9682 | 14000 | 2.16 | 6481.4815 | 6442.8866 | 14000 | 1.9 | 7368.4211 | 7318.0328 | 14000 | 1.81 | 7734.8066 | 7691.2474 | 14000 | 1.69 | 8284.0237 | 8245.7251
|  |  | 100 | mid | 11200 | 2.77 | 4043.3213 | 2 | 11200 | 2.62 | 4274.8092 | 2 | 11200 | 2.45 | 4571.4286 | 2 | 11200 | 2.25 | 4977.7778 | 2 | 11200 | 2.02 | 5544.5545 | 2 | 11200 | 1.79 | 6256.9832 | 2
|  |  | 8121.4862 | min | 6960 | 2.57 | 2708.1712 | 0.98214 | 6660 | 2.32 | 2870.6897 | 0.98214 | 6240 | 2.03 | 3073.8916 | 0.98214 | 5780 | 1.69 | 3420.1183 | 0.98214 | 5040 | 1.39 | 3625.8993 | 0.98214 | 4320 | 1.06 | 4075.4717 | 0.98214
| -11 |  | 1.7852 | max | 14520 | 2.32 | 6258.6207 | 2.7684 | 14320 | 2.17 | 6599.0783 | 2.4938 | 14060 | 2.02 | 6960.396 | 2.234 | 13820 | 1.83 | 7551.9126 | 1.9675 | 13720 | 1.77 | 7751.4124 | 1.8688 | 13640 | 1.66 | 8216.8675 | 1.7369
|  | 13527.2727 | 53.1685 | nom | 14000 | 2.76 | 5072.4638 | 4886.241 | 14000 | 2.46 | 5691.0569 | 5424.435 | 14000 | 2.18 | 6422.0183 | 6055.1099 | 14000 | 1.9 | 7368.4211 | 6875.2475 | 14000 | 1.83 | 7650.2732 | 7238.36 | 14000 | 1.72 | 8139.5349 | 7788.2459
|  |  | 100 | mid | 11200 | 2.81 | 3985.7651 | 2 | 11200 | 2.66 | 4210.5263 | 2 | 11200 | 2.5 | 4480 | 2 | 11200 | 2.3 | 4869.5652 | 2 | 11200 | 2.06 | 5436.8932 | 2 | 11200 | 1.82 | 6153.8462 | 2
|  |  | 7577.3882 | min | 6580 | 2.56 | 2570.3125 | 0.83117 | 6280 | 2.31 | 2718.6147 | 0.83117 | 5920 | 2.04 | 2901.9608 | 0.83117 | 5540 | 1.72 | 3220.9302 | 0.83117 | 4820 | 1.42 | 3394.3662 | 0.83117 | 4160 | 1.08 | 3851.8519 | 0.83117
| -10 |  | 1.8592 | max | 14600 | 2.4 | 6083.3333 | 2.816 | 14400 | 2.25 | 6400 | 2.564 | 14200 | 2.1 | 6761.9048 | 2.3119 | 14000 | 1.9 | 7368.4211 | 2.0439 | 14000 | 1.85 | 7567.5676 | 1.93 | 14000 | 1.75 | 8000 | 1.782
|  | 13104.5455 | 52.3924 | nom | 14000 | 2.8 | 5000 | 4653.6189 | 14000 | 2.5 | 5600 | 5111.0548 | 14000 | 2.2 | 6363.6364 | 5668.2232 | 14000 | 1.9 | 7368.4211 | 6411.5007 | 14000 | 1.85 | 7567.5676 | 6790.0913 | 14000 | 1.75 | 8000 | 7353.9218
|  |  | 100 | mid | 11200 | 2.85 | 3929.8246 | 2 | 11200 | 2.7 | 4148.1481 | 2 | 11200 | 2.55 | 4392.1569 | 2 | 11200 | 2.35 | 4765.9574 | 2 | 11200 | 2.1 | 5333.3333 | 2 | 11200 | 1.85 | 6054.0541 | 2
|  |  | 7048.6739 | min | 6200 | 2.55 | 2431.3725 | 0.68019 | 5900 | 2.3 | 2565.2174 | 0.68019 | 5600 | 2.05 | 2731.7073 | 0.68019 | 5300 | 1.75 | 3028.5714 | 0.68019 | 4600 | 1.45 | 3172.4138 | 0.68019 | 4000 | 1.1 | 3636.3636 | 0.68019
| -9 |  | 1.9939 | max | 15100 | 2.5 | 6040 | 2.9304 | 14900 | 2.3333 | 6385.7143 | 2.6942 | 14700 | 2.1667 | 6784.6154 | 2.4579 | 14500 | 1.9667 | 7372.8814 | 2.206 | 14233.3333 | 1.9167 | 7426.087 | 2.052 | 14000 | 1.8167 | 7706.422 | 1.8716
|  | 12681.8182 | 51.6105 | nom | 14000 | 2.8833 | 4855.4913 | 4327.6582 | 14000 | 2.6 | 5384.6154 | 4707.1584 | 14000 | 2.3167 | 6043.1655 | 5159.6143 | 14000 | 2.0333 | 6885.2459 | 5748.9084 | 14000 | 1.95 | 7179.4872 | 6180.2168 | 14000 | 1.8167 | 7706.422 | 6775.9563
|  |  | 100 | mid | 11200 | 2.9833 | 3754.1899 | 2 | 11200 | 2.8 | 4000 | 2 | 11200 | 2.6167 | 4280.2548 | 2 | 11200 | 2.4 | 4666.6667 | 2 | 11200 | 2.1667 | 5169.2308 | 2 | 11200 | 1.9333 | 5793.1034 | 2
|  |  | 6360.3329 | min | 5833.3333 | 2.9167 | 2000 | 0.52922 | 5266.6667 | 2.2833 | 2306.5693 | 0.52922 | 5066.6667 | 2.05 | 2471.5447 | 0.52922 | 4866.6667 | 1.7833 | 2728.972 | 0.52922 | 4266.6667 | 1.4667 | 2909.0909 | 0.52922 | 3700 | 1.1167 | 3313.4328 | 0.52922
| -8 |  | 2.1315 | max | 15600 | 2.6 | 6000 | 3.0599 | 15400 | 2.4167 | 6372.4138 | 2.8244 | 15200 | 2.2333 | 6805.9701 | 2.5888 | 15000 | 2.0333 | 7377.0492 | 2.3428 | 14466.6667 | 1.9833 | 7294.1176 | 2.164 | 14000 | 1.8833 | 7433.6283 | 1.9662
|  | 12259.0909 | 50.8225 | nom | 14000 | 2.9667 | 4719.1011 | 4006.331 | 14000 | 2.7 | 5185.1852 | 4340.4989 | 14000 | 2.4333 | 5753.4247 | 4735.4856 | 14000 | 2.1667 | 6461.5385 | 5232.5992 | 14000 | 2.05 | 6829.2683 | 5665.0454 | 14000 | 1.8833 | 7433.6283 | 6234.8085
|  |  | 100 | mid | 11200 | 3.1167 | 3593.5829 | 2 | 11200 | 2.9 | 3862.069 | 2 | 11200 | 2.6833 | 4173.913 | 2 | 11200 | 2.45 | 4571.4286 | 2 | 11200 | 2.2333 | 5014.9254 | 2 | 11200 | 2.0167 | 5553.719 | 2
|  |  | 5751.5105 | min | 5466.6667 | 3.2833 | 1664.9746 | 0.37825 | 4633.3333 | 2.2667 | 2044.1176 | 0.37825 | 4533.3333 | 2.05 | 2211.3821 | 0.37825 | 4433.3333 | 1.8167 | 2440.367 | 0.37825 | 3933.3333 | 1.4833 | 2651.6854 | 0.37825 | 3400 | 1.1333 | 3000 | 0.37825
| -7 |  | 2.2648 | max | 16100 | 2.7 | 5962.963 | 3.2045 | 15900 | 2.5 | 6360 | 2.9545 | 15700 | 2.3 | 6826.087 | 2.7045 | 15500 | 2.1 | 7380.9524 | 2.4545 | 14700 | 2.05 | 7170.7317 | 2.2659 | 14000 | 1.95 | 7179.4872 | 2.0659
|  | 11836.3636 | 50.0283 | nom | 14000 | 3.05 | 4590.1639 | 3693.617 | 14000 | 2.8 | 5000 | 4006.1538 | 14000 | 2.55 | 5490.1961 | 4376.4706 | 14000 | 2.3 | 6086.9565 | 4822.2222 | 14000 | 2.15 | 6511.6279 | 5223.671 | 14000 | 1.95 | 7179.4872 | 5729.3729
|  |  | 100 | mid | 11200 | 3.25 | 3446.1538 | 2 | 11200 | 3 | 3733.3333 | 2 | 11200 | 2.75 | 4072.7273 | 2 | 11200 | 2.5 | 4480 | 2 | 11200 | 2.3 | 4869.5652 | 2 | 11200 | 2.1 | 5333.3333 | 2
|  |  | 5226.2819 | min | 5100 | 3.65 | 1397.2603 | 0.22727 | 4000 | 2.25 | 1777.7778 | 0.22727 | 4000 | 2.05 | 1951.2195 | 0.22727 | 4000 | 1.85 | 2162.1622 | 0.22727 | 3600 | 1.5 | 2400 | 0.22727 | 3100 | 1.15 | 2695.6522 | 0.22727
| -6 |  | 2.3676 | max | 16144.4444 | 2.7611 | 5847.0825 | 3.2788 | 15944.4444 | 2.5556 | 6239.1304 | 3.0288 | 15733.3333 | 2.35 | 6695.0355 | 2.7788 | 15533.3333 | 2.1444 | 7243.5233 | 2.5288 | 14744.4444 | 2.0944 | 7039.7878 | 2.3381 | 14033.3333 | 1.9944 | 7036.2117 | 2.1386
|  | 11413.6364 | 49.2275 | nom | 14000 | 3.0889 | 4532.3741 | 3481.0823 | 14000 | 2.8389 | 4931.5068 | 3768.4179 | 14000 | 2.5889 | 5407.7253 | 4107.4555 | 14000 | 2.3389 | 5985.7482 | 4513.5294 | 14000 | 2.1944 | 6379.7468 | 4881.5207 | 14000 | 2 | 7000 | 5337.0782
|  |  | 100 | mid | 11200 | 3.2944 | 3399.6627 | 2 | 11200 | 3.0444 | 3678.8321 | 2 | 11200 | 2.7944 | 4007.9523 | 2 | 11200 | 2.5444 | 4401.7467 | 2 | 11200 | 2.35 | 4765.9574 | 2 | 11200 | 2.15 | 5209.3023 | 2
|  |  | 4820.7942 | min | 5155.5556 | 3.7111 | 1389.2216 | 0.076299 | 4122.2222 | 2.4056 | 1713.6259 | 0.076299 | 4077.7778 | 2.1667 | 1882.0513 | 0.076299 | 4022.2222 | 1.9222 | 2092.4855 | 0.076299 | 3611.1111 | 1.5611 | 2313.1673 | 0.076299 | 3111.1111 | 1.1944 | 2604.6512 | 0.076299
| -5 |  | 2.4395 | max | 16188.8889 | 2.8222 | 5736.2205 | 3.354 | 15988.8889 | 2.6111 | 6123.4043 | 3.073 | 15766.6667 | 2.4 | 6569.4444 | 2.8224 | 15566.6667 | 2.1889 | 7111.6751 | 2.5715 | 14788.8889 | 2.1389 | 6914.2857 | 2.3785 | 14066.6667 | 2.0389 | 6899.1826 | 2.1751
|  | 10990.9091 | 48.4198 | nom | 14000 | 3.1278 | 4476.0213 | 3276.9381 | 14000 | 2.8778 | 4864.8649 | 3576.5784 | 14000 | 2.6278 | 5327.6956 | 3894.1726 | 14000 | 2.3778 | 5887.8505 | 4274.0925 | 14000 | 2.2389 | 6253.1017 | 4620.8655 | 14000 | 2.05 | 6829.2683 | 5053.0083
|  |  | 100 | mid | 11200 | 3.3389 | 3354.4093 | 1 | 11200 | 3.0889 | 3625.8993 | 1 | 11200 | 2.8389 | 3945.2055 | 1 | 11200 | 2.5889 | 4326.1803 | 1 | 11200 | 2.4 | 4666.6667 | 1 | 11200 | 2.2 | 5090.9091 | 1
|  |  | 4505.3411 | min | 5211.1111 | 3.7722 | 1381.4433 | 0.96509 | 4244.4444 | 2.5611 | 1657.2668 | 0.96994 | 4155.5556 | 2.2833 | 1819.9513 | 0.97032 | 4044.4444 | 1.9944 | 2027.8552 | 0.97078 | 3622.2222 | 1.6222 | 2232.8767 | 0.97241 | 3122.2222 | 1.2389 | 2520.1794 | 0.97412
| -4 |  | 2.4804 | max | 16233.3333 | 2.8833 | 5630.0578 | 3.4313 | 16033.3333 | 2.6667 | 6012.5 | 3.0948 | 15800 | 2.45 | 6448.9796 | 2.8395 | 15600 | 2.2333 | 6985.0746 | 2.5831 | 14833.3333 | 2.1833 | 6793.8931 | 2.386 | 14100 | 2.0833 | 6768 | 2.1743
|  | 10568.1818 | 47.6049 | nom | 14000 | 3.1667 | 4421.0526 | 3079.9782 | 14000 | 2.9167 | 4800 | 3414.8103 | 14000 | 2.6667 | 5250 | 3721.8473 | 14000 | 2.4167 | 5793.1034 | 4091.2118 | 14000 | 2.2833 | 6131.3869 | 4429.2776 | 14000 | 2.1 | 6666.6667 | 4860.5292
|  |  | 100 | mid | 11200 | 3.3833 | 3310.3448 | 1 | 11200 | 3.1333 | 3574.4681 | 1 | 11200 | 2.8833 | 3884.3931 | 1 | 11200 | 2.6333 | 4253.1646 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.25 | 4977.7778 | 1
|  |  | 4260.631 | min | 5266.6667 | 3.8333 | 1373.913 | 0.89351 | 4366.6667 | 2.7167 | 1607.362 | 0.90754 | 4233.3333 | 2.4 | 1763.8889 | 0.90931 | 4066.6667 | 2.0667 | 1967.7419 | 0.91143 | 3633.3333 | 1.6833 | 2158.4158 | 0.9165 | 3133.3333 | 1.2833 | 2441.5584 | 0.92168
| -3 |  | 2.5254 | max | 16277.7778 | 2.9444 | 5528.3019 | 3.5115 | 16077.7778 | 2.7222 | 5906.1224 | 3.1298 | 15833.3333 | 2.5 | 6333.3333 | 2.8648 | 15633.3333 | 2.2778 | 6863.4146 | 2.5979 | 14877.7778 | 2.2278 | 6678.3042 | 2.3945 | 14133.3333 | 2.1278 | 6642.2977 | 2.1727
|  | 10145.4545 | 46.7824 | nom | 14000 | 3.2056 | 4367.4177 | 2889.2053 | 14000 | 2.9556 | 4736.8421 | 3241.6031 | 14000 | 2.7056 | 5174.538 | 3541.3622 | 14000 | 2.4556 | 5701.3575 | 3905.3078 | 14000 | 2.3278 | 6014.3198 | 4236.9021 | 14000 | 2.15 | 6511.6279 | 4669.4561
|  |  | 100 | mid | 11200 | 3.4278 | 3267.423 | 1 | 11200 | 3.1778 | 3524.4755 | 1 | 11200 | 2.9278 | 3825.4269 | 1 | 11200 | 2.6778 | 4182.5726 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1
|  |  | 4017.393 | min | 5322.2222 | 3.8944 | 1366.6191 | 0.82059 | 4488.8889 | 2.8722 | 1562.8627 | 0.84287 | 4311.1111 | 2.5167 | 1713.0243 | 0.84692 | 4088.8889 | 2.1389 | 1911.6883 | 0.8517 | 3644.4444 | 1.7444 | 2089.172 | 0.86043 | 3144.4444 | 1.3278 | 2368.2008 | 0.86909
| -2 |  | 2.5754 | max | 16322.2222 | 3.0056 | 5430.6839 | 3.5949 | 16122.2222 | 2.7778 | 5804 | 3.1786 | 15866.6667 | 2.55 | 6222.2222 | 2.8987 | 15666.6667 | 2.3222 | 6746.4115 | 2.6157 | 14922.2222 | 2.2722 | 6567.2372 | 2.4042 | 14166.6667 | 2.1722 | 6521.7391 | 2.1704
|  | 9722.7273 | 45.952 | nom | 14000 | 3.2444 | 4315.0685 | 2704.6204 | 14000 | 2.9944 | 4675.3247 | 3058.7826 | 14000 | 2.7444 | 5101.2146 | 3354.1449 | 14000 | 2.4944 | 5612.4722 | 3717.0504 | 14000 | 2.3722 | 5901.6393 | 4044.0074 | 14000 | 2.2 | 6363.6364 | 4479.6071
|  |  | 100 | mid | 11200 | 3.4722 | 3225.6 | 1 | 11200 | 3.2222 | 3475.8621 | 1 | 11200 | 2.9722 | 3768.2243 | 1 | 11200 | 2.7222 | 4114.2857 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1
|  |  | 3775.1669 | min | 5377.7778 | 3.9556 | 1359.5506 | 0.74627 | 4611.1111 | 3.0278 | 1522.9358 | 0.77579 | 4388.8889 | 2.6333 | 1666.6667 | 0.78311 | 4111.1111 | 2.2111 | 1859.2965 | 0.79161 | 3655.5556 | 1.8056 | 2024.6154 | 0.80419 | 3155.5556 | 1.3722 | 2299.5951 | 0.81636
| -1 |  | 2.6317 | max | 16366.6667 | 3.0667 | 5336.9565 | 3.6814 | 16166.6667 | 2.8333 | 5705.8824 | 3.2422 | 15900 | 2.6 | 6115.3846 | 2.9414 | 15700 | 2.3667 | 6633.8028 | 2.6367 | 14966.6667 | 2.3167 | 6460.4317 | 2.415 | 14200 | 2.2167 | 6406.015 | 2.1674
|  | 9300 | 45.1133 | nom | 14000 | 3.2833 | 4263.9594 | 2526.2084 | 14000 | 3.0333 | 4615.3846 | 2868.4385 | 14000 | 2.7833 | 5029.9401 | 3161.7391 | 14000 | 2.5333 | 5526.3158 | 3527.1177 | 14000 | 2.4167 | 5793.1034 | 3850.8611 | 14000 | 2.25 | 6222.2222 | 4290.8012
|  |  | 100 | mid | 11200 | 3.5167 | 3184.8341 | 1 | 11200 | 3.2667 | 3428.5714 | 1 | 11200 | 3.0167 | 3712.7072 | 1 | 11200 | 2.7667 | 4048.1928 | 1 | 11200 | 2.6 | 4307.6923 | 1 | 11200 | 2.4 | 4666.6667 | 1
|  |  | 3533.8474 | min | 5433.3333 | 4.0167 | 1352.6971 | 0.67052 | 4733.3333 | 3.1833 | 1486.911 | 0.70619 | 4466.6667 | 2.75 | 1624.2424 | 0.71782 | 4133.3333 | 2.2833 | 1810.219 | 0.73113 | 3666.6667 | 1.8667 | 1964.2857 | 0.74779 | 3166.6667 | 1.4167 | 2235.2941 | 0.76349
| 0 |  | 2.7097 | max | 16411.1111 | 3.1278 | 5246.8917 | 3.7712 | 16211.1111 | 2.8889 | 5611.5385 | 3.3213 | 15933.3333 | 2.65 | 6012.5786 | 2.9933 | 15733.3333 | 2.4111 | 6525.3456 | 2.6609 | 15011.1111 | 2.3611 | 6357.6471 | 2.427 | 14233.3333 | 2.2611 | 6294.8403 | 2.1637
|  | 8877.2727 | 44.2656 | nom | 14000 | 3.3222 | 4214.0468 | 2353.9393 | 14000 | 3.0722 | 4556.962 | 2672.8463 | 14000 | 2.8222 | 4960.6299 | 2965.7621 | 14000 | 2.5722 | 5442.7646 | 3336.1878 | 14000 | 2.4611 | 5688.4876 | 3657.7283 | 14000 | 2.3 | 6086.9565 | 4102.8576
|  |  | 100 | mid | 11200 | 3.5611 | 3145.0858 | 1 | 11200 | 3.3111 | 3382.5503 | 1 | 11200 | 3.0611 | 3658.8022 | 1 | 11200 | 2.8111 | 3984.1897 | 1 | 11200 | 2.65 | 4226.4151 | 1 | 11200 | 2.45 | 4571.4286 | 1
|  |  | 3276.0892 | min | 5488.8889 | 4.0778 | 1346.049 | 0.5933 | 4855.5556 | 3.3389 | 1454.2429 | 0.6339 | 4544.4444 | 2.8667 | 1585.2713 | 0.65101 | 4155.5556 | 2.3556 | 1764.1509 | 0.67028 | 3677.7778 | 1.9278 | 1907.781 | 0.69122 | 3177.7778 | 1.4611 | 2174.9049 | 0.71046
| 1 |  | 2.8049 | max | 16455.5556 | 3.1889 | 5160.2787 | 3.8645 | 16255.5556 | 2.9444 | 5520.7547 | 3.4168 | 15966.6667 | 2.7 | 5913.5802 | 3.0545 | 15766.6667 | 2.4556 | 6420.8145 | 2.6883 | 15055.5556 | 2.4056 | 6258.6605 | 2.4401 | 14266.6667 | 2.3056 | 6187.9518 | 2.1592
|  | 8454.5455 | 43.4086 | nom | 14000 | 3.3611 | 4165.2893 | 2187.7695 | 14000 | 3.1111 | 4500 | 2474.377 | 14000 | 2.8611 | 4893.2039 | 2767.8602 | 14000 | 2.6111 | 5361.7021 | 3144.931 | 14000 | 2.5056 | 5587.5831 | 3464.8707 | 14000 | 2.35 | 5957.4468 | 3915.5951
|  |  | 100 | mid | 11200 | 3.6056 | 3106.3174 | 1 | 11200 | 3.3556 | 3337.7483 | 1 | 11200 | 3.1056 | 3606.4401 | 1 | 11200 | 2.8556 | 3922.179 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.5 | 4480 | 1
|  |  | 3014.2369 | min | 5544.4444 | 4.1389 | 1339.5973 | 0.51456 | 4977.7778 | 3.4944 | 1424.4833 | 0.55877 | 4622.2222 | 2.9833 | 1549.3482 | 0.58262 | 4177.7778 | 2.4278 | 1720.8238 | 0.60903 | 3688.8889 | 1.9889 | 1854.7486 | 0.63448 | 3188.8889 | 1.5056 | 2118.0812 | 0.65729
14kW-Maximum heating CAP | 2 |  | 2.9189 | max | 16500 | 3.25 | 5076.9231 | 3.9612 | 16300 | 3 | 5433.3333 | 3.5298 | 16000 | 2.75 | 5818.1818 | 3.1256 | 15800 | 2.5 | 6320 | 2.719 | 15100 | 2.45 | 6163.2653 | 2.4543 | 14300 | 2.35 | 6085.1064 | 2.154
|  | 8031.8182 | 42.5417 | nom | 14000 | 3.4 | 4117.6471 | 2027.6426 | 14000 | 3.15 | 4444.4444 | 2275.4035 | 14000 | 2.9 | 4827.5862 | 2569.6643 | 14000 | 2.65 | 5283.0189 | 2954.0027 | 14000 | 2.55 | 5490.1961 | 3272.5454 | 14000 | 2.4 | 5833.3333 | 3728.8314
|  |  | 100 | mid | 11200 | 3.65 | 3068.4932 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 3.15 | 3555.5556 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.55 | 4392.1569 | 1
|  |  | 2751.6549 | min | 5600 | 4.2 | 1333.3333 | 0.43425 | 5100 | 3.65 | 1397.2603 | 0.48063 | 4700 | 3.1 | 1516.129 | 0.51259 | 4200 | 2.5 | 1680 | 0.5474 | 3700 | 2.05 | 1804.878 | 0.57758 | 3200 | 1.55 | 2064.5161 | 0.60398
| 3 |  | 3.1188 | max | 16560 | 3.54 | 4677.9661 | 4.4081 | 16360 | 3.25 | 5033.8462 | 3.7543 | 16080 | 2.96 | 5432.4324 | 3.2774 | 15860 | 2.66 | 5962.406 | 2.8007 | 15160 | 2.54 | 5968.5039 | 2.4883 | 14360 | 2.38 | 6033.6134 | 2.1427
|  | 7609.0909 | 41.6641 | nom | 14000 | 3.7 | 3783.7838 | 1726.1744 | 14000 | 3.41 | 4105.5718 | 2026.7485 | 14000 | 3.12 | 4487.1795 | 2321.6504 | 14000 | 2.82 | 4964.539 | 2716.8219 | 14000 | 2.67 | 5243.4457 | 3057.9912 | 14000 | 2.47 | 5668.0162 | 3551.2162
|  |  | 100 | mid | 11200 | 3.97 | 2821.1587 | 1 | 11200 | 3.68 | 3043.4783 | 1 | 11200 | 3.39 | 3303.8348 | 1 | 11200 | 3.09 | 3624.5955 | 1 | 11200 | 2.88 | 3888.8889 | 1 | 11200 | 2.62 | 4274.8092 | 1
|  |  | 2439.7617 | min | 5380 | 4.68 | 1149.5726 | 0.38301 | 4920 | 3.81 | 1291.3386 | 0.4282 | 4500 | 3.18 | 1415.0943 | 0.46404 | 4000 | 2.51 | 1593.6255 | 0.50126 | 3500 | 2.04 | 1715.6863 | 0.53365 | 3000 | 1.53 | 1960.7843 | 0.56208
| 4 |  | 3.33 | max | 16620 | 3.83 | 4339.4256 | 4.8681 | 16420 | 3.5 | 4691.4286 | 3.9662 | 16160 | 3.17 | 5097.7918 | 3.4148 | 15920 | 2.82 | 5645.3901 | 2.8678 | 15220 | 2.63 | 5787.0722 | 2.5121 | 14420 | 2.41 | 5983.4025 | 2.1262
|  | 7186.3636 | 40.7753 | nom | 14000 | 4 | 3500 | 1476.2083 | 14000 | 3.67 | 3814.7139 | 1811.8955 | 14000 | 3.34 | 4191.6168 | 2104.4905 | 14000 | 2.99 | 4682.2742 | 2505.8902 | 14000 | 2.79 | 5017.9211 | 2860.693 | 14000 | 2.54 | 5511.811 | 3379.9419
|  |  | 100 | mid | 11200 | 4.29 | 2610.7226 | 1 | 11200 | 3.96 | 2828.2828 | 1 | 11200 | 3.63 | 3085.3994 | 1 | 11200 | 3.28 | 3414.6341 | 1 | 11200 | 3.01 | 3720.9302 | 1 | 11200 | 2.69 | 4163.5688 | 1
|  |  | 2158.0904 | min | 5160 | 5.16 | 1000 | 0.33549 | 4740 | 3.97 | 1193.9547 | 0.37869 | 4300 | 3.26 | 1319.0184 | 0.41831 | 3800 | 2.52 | 1507.9365 | 0.45762 | 3300 | 2.03 | 1625.6158 | 0.49194 | 2800 | 1.51 | 1854.3046 | 0.52219
| 5 |  | 3.5546 | max | 16680 | 4.12 | 4048.5437 | 5.3399 | 16480 | 3.75 | 4394.6667 | 4.1665 | 16240 | 3.38 | 4804.7337 | 3.5388 | 15980 | 2.98 | 5362.4161 | 2.9213 | 15280 | 2.72 | 5617.6471 | 2.5266 | 14480 | 2.44 | 5934.4262 | 2.1049
|  | 6763.6364 | 39.8742 | nom | 14000 | 4.3 | 3255.814 | 1266.6117 | 14000 | 3.93 | 3562.341 | 1623.3353 | 14000 | 3.56 | 3932.5843 | 1911.2608 | 14000 | 3.16 | 4430.3797 | 2315.2895 | 14000 | 2.91 | 4810.9966 | 2676.9961 | 14000 | 2.61 | 5363.9847 | 3213.3387
|  |  | 100 | mid | 11200 | 4.61 | 2429.5011 | 1 | 11200 | 4.24 | 2641.5094 | 1 | 11200 | 3.87 | 2894.0568 | 1 | 11200 | 3.47 | 3227.6657 | 1 | 11200 | 3.14 | 3566.879 | 1 | 11200 | 2.76 | 4057.971 | 1
|  |  | 1902.7716 | min | 4940 | 5.64 | 875.8865 | 0.29132 | 4560 | 4.13 | 1104.1162 | 0.33187 | 4100 | 3.34 | 1227.5449 | 0.37516 | 3600 | 2.53 | 1422.9249 | 0.41627 | 3100 | 2.02 | 1534.6535 | 0.4523 | 2600 | 1.49 | 1744.9664 | 0.48414
| 6 |  | 3.7974 | max | 16740 | 4.41 | 3795.9184 | 5.8223 | 16540 | 4 | 4135 | 4.3561 | 16320 | 3.59 | 4545.961 | 3.6507 | 16040 | 3.14 | 5108.2803 | 2.9623 | 15340 | 2.81 | 5459.0747 | 2.5324 | 14540 | 2.47 | 5886.6397 | 2.079
|  | 6340.9091 | 38.9601 | nom | 14000 | 4.6 | 3043.4783 | 1089.0667 | 14000 | 4.19 | 3341.2888 | 1455.6289 | 14000 | 3.78 | 3703.7037 | 1736.8946 | 14000 | 3.33 | 4204.2042 | 2140.547 | 14000 | 3.03 | 4620.462 | 2503.9575 | 14000 | 2.68 | 5223.8806 | 3049.9076
|  |  | 100 | mid | 11200 | 4.93 | 2271.8053 | 1 | 11200 | 4.52 | 2477.8761 | 1 | 11200 | 4.11 | 2725.0608 | 1 | 11200 | 3.66 | 3060.1093 | 1 | 11200 | 3.27 | 3425.0765 | 1 | 11200 | 2.83 | 3957.5972 | 1
|  |  | 1669.7902 | min | 4720 | 6.12 | 771.2418 | 0.25014 | 4380 | 4.29 | 1020.979 | 0.28752 | 3900 | 3.42 | 1140.3509 | 0.33437 | 3400 | 2.54 | 1338.5827 | 0.37704 | 2900 | 2.01 | 1442.7861 | 0.41457 | 2400 | 1.47 | 1632.6531 | 0.44783
| 7 |  | 4.0602 | max | 16800 | 4.7 | 3574.4681 | 6.3142 | 16600 | 4.25 | 3905.8824 | 4.5359 | 16400 | 3.8 | 4315.7895 | 3.7514 | 16100 | 3.3 | 4878.7879 | 2.9917 | 15400 | 2.9 | 5310.3448 | 2.5301 | 14600 | 2.5 | 5840 | 2.049
|  | 5918.1818 | 38.0318 | nom | 14000 | 4.9 | 2857.1429 | 937.2744 | 14000 | 4.45 | 3146.0674 | 1304.74 | 14000 | 4 | 3500 | 1577.5954 | 14000 | 3.5 | 4000 | 1978.1973 | 14000 | 3.15 | 4444.4444 | 2339.1529 | 14000 | 2.75 | 5090.9091 | 2888.2699
|  |  | 100 | mid | 11200 | 5.25 | 2133.3333 | 1 | 11200 | 4.8 | 2333.3333 | 1 | 11200 | 4.35 | 2574.7126 | 1 | 11200 | 3.85 | 2909.0909 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 2.9 | 3862.069 | 1
|  |  | 1457.6036 | min | 4500 | 6.6 | 681.8182 | 0.21167 | 4200 | 4.45 | 943.8202 | 0.24545 | 3700 | 3.5 | 1057.1429 | 0.29576 | 3200 | 2.55 | 1254.902 | 0.33977 | 2700 | 2 | 1350 | 0.37861 | 2200 | 1.45 | 1517.2414 | 0.41313
| 8 |  | 4.299 | max | 16860 | 4.81 | 3505.1975 | 6.2239 | 16640 | 4.38 | 3799.0868 | 4.5956 | 16440 | 3.93 | 4183.2061 | 3.8854 | 16160 | 3.48 | 4643.6782 | 3.1922 | 15440 | 3.06 | 5045.7516 | 2.6958 | 14640 | 2.64 | 5545.4545 | 2.1881
|  | 5495.4545 | 37.088 | nom | 14000 | 5.02 | 2788.8446 | 882.9649 | 14000 | 4.59 | 3050.1089 | 1195.8009 | 14000 | 4.16 | 3365.3846 | 1414.379 | 14000 | 3.69 | 3794.0379 | 1721.5015 | 14000 | 3.32 | 4216.8675 | 2038.528 | 14000 | 2.9 | 4827.5862 | 2511.5227
|  |  | 100 | mid | 11200 | 5.37 | 2085.6611 | 1 | 11200 | 4.95 | 2262.6263 | 1 | 11200 | 4.53 | 2472.4062 | 1 | 11200 | 4.06 | 2758.6207 | 1 | 11200 | 3.58 | 3128.4916 | 1 | 11200 | 3.06 | 3660.1307 | 1
|  |  | 1278.2978 | min | 4920 | 6.31 | 779.7147 | 0.091633 | 4600 | 4.54 | 1013.2159 | 0.13567 | 4120 | 3.73 | 1104.5576 | 0.19427 | 3640 | 2.91 | 1250.8591 | 0.24543 | 3200 | 2.34 | 1367.5214 | 0.28693 | 2760 | 1.77 | 1559.322 | 0.32411
| 9 |  | 4.4967 | max | 16920 | 4.92 | 3439.0244 | 6.02 | 16680 | 4.51 | 3698.4479 | 4.6355 | 16480 | 4.06 | 4059.1133 | 4.02 | 16220 | 3.66 | 4431.694 | 3.4094 | 15480 | 3.22 | 4807.4534 | 2.8777 | 14680 | 2.78 | 5280.5755 | 2.3413
|  | 5072.7273 | 36.1273 | nom | 14000 | 5.14 | 2723.7354 | 842.6457 | 14000 | 4.73 | 2959.8309 | 1094.3184 | 14000 | 4.32 | 3240.7407 | 1261.875 | 14000 | 3.88 | 3608.2474 | 1487.8529 | 14000 | 3.49 | 4011.4613 | 1762.7881 | 14000 | 3.05 | 4590.1639 | 2166.5888
|  |  | 100 | mid | 11200 | 5.49 | 2040.0729 | 0 | 11200 | 5.1 | 2196.0784 | 1 | 11200 | 4.71 | 2377.9193 | 1 | 11200 | 4.27 | 2622.9508 | 1 | 11200 | 3.76 | 2978.7234 | 1 | 11200 | 3.22 | 3478.2609 | 1
|  |  | 1128.0917 | min | 5340 | 6.02 | 887.0432 | 0 | 5000 | 4.63 | 1079.9136 | 0.01173 | 4540 | 3.96 | 1146.4646 | 0.079989 | 4080 | 3.27 | 1247.7064 | 0.13943 | 3700 | 2.68 | 1380.597 | 0.18303 | 3320 | 2.09 | 1588.5167 | 0.22243
| 10 |  | 4.7043 | max | 16980 | 5.03 | 3375.7455 | 5.73 | 16720 | 4.64 | 3603.4483 | 4.72 | 16520 | 4.19 | 3942.7208 | 4.19 | 16280 | 3.84 | 4239.5833 | 3.6465 | 15520 | 3.38 | 4591.716 | 3.0791 | 14720 | 2.92 | 5041.0959 | 2.512
|  | 4650 | 35.148 | nom | 14000 | 5.26 | 2661.597 | 811.5183 | 14000 | 4.87 | 2874.7433 | 985.1695 | 14000 | 4.48 | 3125 | 1109.7852 | 14000 | 4.07 | 3439.8034 | 1275.1807 | 14000 | 3.66 | 3825.1366 | 1510.1605 | 14000 | 3.2 | 4375 | 1851.0885
|  |  | 86.3193 | mid | 11200 | 5.61 | 1996.4349 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.89 | 2290.3885 | 0 | 11200 | 4.48 | 2500 | 1 | 11200 | 3.94 | 2842.6396 | 1 | 11200 | 3.38 | 3313.6095 | 1
|  |  | 988.4544 | min | 5760 | 5.73 | 1005.2356 | 0 | 5400 | 4.72 | 1144.0678 | 0 | 4960 | 4.19 | 1183.7709 | 0 | 4520 | 3.63 | 1245.1791 | 0.019461 | 4200 | 3.02 | 1390.7285 | 0.064286 | 3880 | 2.41 | 1609.9585 | 0.10519
| 11 |  | 4.8637 | max | 17040 | 5.14 | 3315.1751 | 5.44 | 16760 | 4.77 | 3513.6268 | 4.81 | 16560 | 4.32 | 3833.3333 | 4.42 | 16340 | 4.02 | 4064.6766 | 3.99 | 15560 | 3.54 | 4395.4802 | 3.36 | 14760 | 3.06 | 4823.5294 | 2.73
|  | 4227.2727 | 34.1478 | nom | 14000 | 5.38 | 2602.2305 | 777.0722 | 14000 | 5.01 | 2794.4112 | 878.8509 | 14000 | 4.64 | 3017.2414 | 956.3965 | 14000 | 4.26 | 3286.385 | 1059.4668 | 14000 | 3.83 | 3655.3525 | 1258.1169 | 14000 | 3.35 | 4179.1045 | 1548.4515
|  |  | 72.4793 | mid | 11200 | 5.73 | 1954.6248 | 0 | 11200 | 5.4 | 2074.0741 | 0 | 11200 | 5.07 | 2209.073 | 0 | 11200 | 4.69 | 2388.0597 | 0 | 11200 | 4.12 | 2718.4466 | 0 | 11200 | 3.54 | 3163.8418 | 0
|  |  | 869.1498 | min | 6180 | 5.44 | 1136.0294 | 0 | 5800 | 4.81 | 1205.8212 | 0 | 5380 | 4.42 | 1217.1946 | 0 | 4960 | 3.99 | 1243.1078 | 0 | 4700 | 3.36 | 1398.8095 | 0 | 4440 | 2.73 | 1626.3736 | 0
| 12 |  | 4.9469 | max | 17100 | 5.25 | 3257.1429 | 5.15 | 16800 | 4.9 | 3428.5714 | 4.9 | 16600 | 4.45 | 3730.3371 | 4.65 | 16400 | 4.2 | 3904.7619 | 4.35 | 15600 | 3.7 | 4216.2162 | 3.7 | 14800 | 3.2 | 4625 | 3.05
|  | 3804.5455 | 33.1243 | nom | 14000 | 5.5 | 2545.4545 | 738.7467 | 14000 | 5.15 | 2718.4466 | 776.4378 | 14000 | 4.8 | 2916.6667 | 818.1818 | 14000 | 4.45 | 3146.0674 | 874.6082 | 14000 | 4 | 3500 | 1028.2555 | 14000 | 3.5 | 4000 | 1247.392
|  |  | 60.6299 | mid | 11200 | 5.85 | 1914.5299 | 0 | 11200 | 5.55 | 2018.018 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.9 | 2285.7143 | 0 | 11200 | 4.3 | 2604.6512 | 0 | 11200 | 3.7 | 3027.027 | 0
|  |  | 769.0778 | min | 6600 | 5.15 | 1281.5534 | 0 | 6200 | 4.9 | 1265.3061 | 0 | 5800 | 4.65 | 1247.3118 | 0 | 5400 | 4.35 | 1241.3793 | 0 | 5200 | 3.7 | 1405.4054 | 0 | 5000 | 3.05 | 1639.3443 | 0
| 13 |  | 5.0203 | max | 17566.6667 | 5.2833 | 3324.9211 | 5.15 | 17266.6667 | 4.9333 | 3500 | 4.9667 | 17033.3333 | 4.55 | 3743.5897 | 4.7833 | 16833.3333 | 4.3 | 3914.7287 | 4.55 | 16033.3333 | 3.8 | 4219.2982 | 3.9167 | 15200 | 3.3 | 4606.0606 | 3.2667
|  | 3381.8182 | 32.0741 | nom | 14000 | 5.5 | 2545.4545 | 656.6637 | 14000 | 5.1833 | 2700.9646 | 680.903 | 14000 | 4.8667 | 2876.7123 | 707.0003 | 14000 | 4.55 | 3076.9231 | 743.2567 | 14000 | 4.1 | 3414.6341 | 863.4429 | 14000 | 3.6167 | 3870.9677 | 1035.2505
|  |  | 52.895 | mid | 11200 | 5.9 | 1898.3051 | 0 | 11200 | 5.5833 | 2005.9701 | 0 | 11200 | 5.3167 | 2106.5831 | 0 | 11200 | 5.0167 | 2232.5581 | 0 | 11200 | 4.4167 | 2535.8491 | 0 | 11200 | 3.8167 | 2934.4978 | 0
|  |  | 673.6276 | min | 6700 | 5.15 | 1300.9709 | 0 | 6266.6667 | 4.9667 | 1261.745 | 0 | 5833.3333 | 4.7833 | 1219.5122 | 0 | 5400 | 4.55 | 1186.8132 | 0 | 5233.3333 | 3.9167 | 1336.1702 | 0 | 5066.6667 | 3.2667 | 1551.0204 | 0
| 14 |  | 5.0801 | max | 18033.3333 | 5.3167 | 3391.8495 | 5.15 | 17733.3333 | 4.9667 | 3570.4698 | 5.0333 | 17466.6667 | 4.65 | 3756.2724 | 4.9167 | 17266.6667 | 4.4 | 3924.2424 | 4.75 | 16466.6667 | 3.9 | 4222.2222 | 4.1333 | 15600 | 3.4 | 4588.2353 | 3.4833
|  | 2959.0909 | 30.9931 | nom | 14000 | 5.5 | 2545.4545 | 574.5808 | 14000 | 5.2167 | 2683.7061 | 587.8989 | 14000 | 4.9333 | 2837.8378 | 601.849 | 14000 | 4.65 | 3010.7527 | 622.9665 | 14000 | 4.2 | 3333.3333 | 715.9091 | 14000 | 3.7333 | 3750 | 849.4998
|  |  | 45.3826 | mid | 11200 | 5.95 | 1882.3529 | 0 | 11200 | 5.6167 | 1994.0653 | 0 | 11200 | 5.3833 | 2080.4954 | 0 | 11200 | 5.1333 | 2181.8182 | 0 | 11200 | 4.5333 | 2470.5882 | 0 | 11200 | 3.9333 | 2847.4576 | 0
|  |  | 582.4889 | min | 6800 | 5.15 | 1320.3883 | 0 | 6333.3333 | 5.0333 | 1258.2781 | 0 | 5866.6667 | 4.9167 | 1193.2203 | 0 | 5400 | 4.75 | 1136.8421 | 0 | 5266.6667 | 4.1333 | 1274.1935 | 0 | 5133.3333 | 3.4833 | 1473.6842 | 0
| 15 |  | 5.1256 | max | 18500 | 5.35 | 3457.9439 | 5.15 | 18200 | 5 | 3640 | 5.1 | 17900 | 4.75 | 3768.4211 | 5.05 | 17700 | 4.5 | 3933.3333 | 4.95 | 16900 | 4 | 4225 | 4.35 | 16000 | 3.5 | 4571.4286 | 3.7
|  | 2536.3636 | 29.8757 | nom | 14000 | 5.5 | 2545.4545 | 492.4978 | 14000 | 5.25 | 2666.6667 | 497.3262 | 14000 | 5 | 2800 | 502.2502 | 14000 | 4.75 | 2947.3684 | 512.3967 | 14000 | 4.3 | 3255.814 | 583.0721 | 14000 | 3.85 | 3636.3636 | 685.5037
|  |  | 38.1052 | mid | 11200 | 6 | 1866.6667 | 0 | 11200 | 5.65 | 1982.3009 | 0 | 11200 | 5.45 | 2055.0459 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.65 | 2408.6022 | 0 | 11200 | 4.05 | 2765.4321 | 0
|  |  | 494.8402 | min | 6900 | 5.15 | 1339.8058 | 0 | 6400 | 5.1 | 1254.902 | 0 | 5900 | 5.05 | 1168.3168 | 0 | 5400 | 4.95 | 1090.9091 | 0 | 5300 | 4.35 | 1218.3908 | 0 | 5200 | 3.7 | 1405.4054 | 0
| 16 |  | 6.4594 | max | 19020 | 5.73 | 3319.3717 | 6.92 | 18720 | 5.3 | 3532.0755 | 5.68 | 18420 | 4.95 | 3721.2121 | 5.37 | 18200 | 4.59 | 3965.1416 | 5.02 | 17380 | 4.08 | 4259.8039 | 4.36 | 16460 | 3.56 | 4623.5955 | 3.65
|  | 2113.6364 | 28.7142 | nom | 14000 | 5.93 | 2360.8769 | 305.4388 | 14000 | 5.57 | 2513.465 | 372.1191 | 14000 | 5.21 | 2687.1401 | 393.6008 | 14000 | 4.85 | 2886.5979 | 421.0431 | 14000 | 4.39 | 3189.0661 | 484.779 | 14000 | 3.92 | 3571.4286 | 579.0785
|  |  | 31.1431 | mid | 11200 | 6.42 | 1744.5483 | 0 | 11200 | 5.99 | 1869.783 | 0 | 11200 | 5.68 | 1971.831 | 0 | 11200 | 5.36 | 2089.5522 | 0 | 11200 | 4.74 | 2362.8692 | 0 | 11200 | 4.12 | 2718.4466 | 0
|  |  | 327.2169 | min | 6980 | 6.92 | 1008.6705 | 0 | 6460 | 5.68 | 1137.3239 | 0 | 6000 | 5.37 | 1117.3184 | 0 | 5520 | 5.02 | 1099.6016 | 0 | 5360 | 4.36 | 1229.3578 | 0 | 5180 | 3.65 | 1419.1781 | 0
| 17 |  | 8.0831 | max | 19540 | 6.11 | 3198.036 | 8.69 | 19240 | 5.6 | 3435.7143 | 6.26 | 18940 | 5.15 | 3677.6699 | 5.69 | 18700 | 4.68 | 3995.7265 | 5.09 | 17860 | 4.16 | 4293.2692 | 4.37 | 16920 | 3.62 | 4674.0331 | 3.6
|  | 1690.9091 | 27.4975 | nom | 14000 | 6.36 | 2201.2579 | 194.581 | 14000 | 5.89 | 2376.91 | 270.1133 | 14000 | 5.42 | 2583.0258 | 297.1721 | 14000 | 4.95 | 2828.2828 | 332.2022 | 14000 | 4.48 | 3125 | 386.9357 | 14000 | 3.99 | 3508.7719 | 469.697
|  |  | 24.417 | mid | 11200 | 6.84 | 1637.4269 | 0 | 11200 | 6.33 | 1769.3523 | 0 | 11200 | 5.91 | 1895.0931 | 0 | 11200 | 5.47 | 2047.532 | 0 | 11200 | 4.83 | 2318.8406 | 0 | 11200 | 4.19 | 2673.031 | 0
|  |  | 209.1905 | min | 7060 | 8.69 | 812.4281 | 0 | 6520 | 6.26 | 1041.5335 | 0 | 6100 | 5.69 | 1072.0562 | 0 | 5640 | 5.09 | 1108.055 | 0 | 5420 | 4.37 | 1240.2746 | 0 | 5160 | 3.6 | 1433.3333 | 0
| 18 |  | 10.0228 | max | 20060 | 6.49 | 3090.9091 | 10.46 | 19760 | 5.9 | 3349.1525 | 6.84 | 19460 | 5.35 | 3637.3832 | 6.01 | 19200 | 4.77 | 4025.1572 | 5.16 | 18340 | 4.24 | 4325.4717 | 4.38 | 17380 | 3.68 | 4722.8261 | 3.55
|  | 1268.1818 | 26.2076 | nom | 14000 | 6.79 | 2061.8557 | 121.2411 | 14000 | 6.21 | 2254.4283 | 185.4067 | 14000 | 5.63 | 2486.6785 | 211.0119 | 14000 | 5.05 | 2772.2772 | 245.7717 | 14000 | 4.57 | 3063.4573 | 289.5392 | 14000 | 4.06 | 3448.2759 | 357.2343
|  |  | 17.9315 | mid | 11200 | 7.26 | 1542.6997 | 0 | 11200 | 6.67 | 1679.1604 | 0 | 11200 | 6.14 | 1824.1042 | 0 | 11200 | 5.58 | 2007.1685 | 0 | 11200 | 4.92 | 2276.4228 | 0 | 11200 | 4.26 | 2629.108 | 0
|  |  | 126.5292 | min | 7140 | 10.46 | 682.6004 | 0 | 6580 | 6.84 | 961.9883 | 0 | 6200 | 6.01 | 1031.614 | 0 | 5760 | 5.16 | 1116.2791 | 0 | 5480 | 4.38 | 1251.1416 | 0 | 5140 | 3.55 | 1447.8873 | 0
| 19 |  | 12.23 | max | 20580 | 6.87 | 2995.6332 | 12.23 | 20280 | 6.2 | 3270.9677 | 7.42 | 19980 | 5.55 | 3600 | 6.33 | 19700 | 4.86 | 4053.4979 | 5.23 | 18820 | 4.32 | 4356.4815 | 4.39 | 17840 | 3.74 | 4770.0535 | 3.5
|  | 845.4545 | 24.8123 | nom | 14000 | 7.22 | 1939.0582 | 69.1296 | 14000 | 6.53 | 2143.951 | 113.9427 | 14000 | 5.84 | 2397.2603 | 133.5631 | 14000 | 5.15 | 2718.4466 | 161.6548 | 14000 | 4.66 | 3004.2918 | 192.5865 | 14000 | 4.13 | 3389.8305 | 241.5584
|  |  | 11.7099 | mid | 11200 | 7.68 | 1458.3333 | 0 | 11200 | 7.01 | 1597.7175 | 0 | 11200 | 6.37 | 1758.2418 | 0 | 11200 | 5.69 | 1968.3656 | 0 | 11200 | 5.01 | 2235.5289 | 0 | 11200 | 4.33 | 2586.6051 | 0
|  |  | 69.1296 | min | 7220 | 12.23 | 590.3516 | 0 | 6640 | 7.42 | 894.8787 | 0 | 6300 | 6.33 | 995.2607 | 0 | 5880 | 5.23 | 1124.283 | 0 | 5540 | 4.39 | 1261.959 | 0 | 5120 | 3.5 | 1462.8571 | 0
| 20 |  | 14 | max | 21100 | 7.25 | 2910.3448 | 14 | 20800 | 6.5 | 3200 | 8 | 20500 | 5.75 | 3565.2174 | 6.65 | 20200 | 4.95 | 4080.8081 | 5.3 | 19300 | 4.4 | 4386.3636 | 4.4 | 18300 | 3.8 | 4815.7895 | 3.45
|  | 422.7273 | 23.2368 | nom | 14000 | 7.65 | 1830.0654 | 30.1948 | 14000 | 6.85 | 2043.7956 | 52.8409 | 14000 | 6.05 | 2314.0496 | 63.568 | 14000 | 5.25 | 2666.6667 | 79.7599 | 14000 | 4.75 | 2947.3684 | 96.0744 | 14000 | 4.2 | 3333.3333 | 122.5296
|  |  | 5.7908 | mid | 11200 | 8.1 | 1382.716 | 0 | 11200 | 7.35 | 1523.8095 | 0 | 11200 | 6.6 | 1696.9697 | 0 | 11200 | 5.8 | 1931.0345 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.4 | 2545.4545 | 0
|  |  | 30.1948 | min | 7300 | 14 | 521.4286 | 0 | 6700 | 8 | 837.5 | 0 | 6400 | 6.65 | 962.406 | 0 | 6000 | 5.3 | 1132.0755 | 0 | 5600 | 4.4 | 1272.7273 | 0 | 5100 | 3.45 | 1478.2609 | 0
Indoor Temp. |  | 22
LWT |  |  | 25 CAP: 25; 35 CAP: 35; 40 CAP: 40; 45 CAP: 45; 50 CAP: 50; 55 CAP: 55
Outdoor air temperature[℃] |  | Heating Demand | COP | CL | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP
|  |  | LWT |  |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI
| -15 |  | 0.17844 | max | - | - | - | - | 14000 | 1.85 | 7567.5676 | 1.6039 | 13500 | 1.7 | 7941.1765 | 1.3575 | 13100 | 1.55 | 8451.6129 | 1.1265 | 12600 | 1.45 | 8689.6552 | 0.87983 | 12200 | 1.3 | 9384.6154 | 0.43977
|  | 15640.9091 | 57.9693 | nom | - | - | - | - | 11000 | 2.3 | 4782.6087 | 9752.0193 | 11000 | 2.1 | 5238.0952 | 11522.2341 | 11000 | 1.9 | 5789.4737 | 13884.3309 | 11000 | 1.75 | 6285.7143 | 17777.2037 | 11000 | 1.6 | 6875 | 35565.8915
|  |  | 100 | mid | - | - | - | - | 8800 | 2.5 | 3520 | 3 | 8800 | 2.3 | 3826.087 | 3 | 8800 | 2.1 | 4190.4762 | 3 | 8800 | 1.9 | 4631.5789 | 3 | 8800 | 1.7 | 5176.4706 | 3
|  |  | 87653.7953 | min | - | - | - | - | 7800 | 2.35 | 3319.1489 | 1.547 | 7200 | 2 | 3600 | 1.8564 | 6500 | 1.6 | 4062.5 | 2.21 | 5700 | 1.3 | 4384.6154 | 2.9006 | 4800 | 1 | 4800 | 3.8674
| -14 |  | 1.7451 | max | 14280 | 2.08 | 6865.3846 | 0.20364 | 14080 | 1.93 | 7295.3368 | -3.9032 | 13640 | 1.78 | 7662.9213 | 3.2705 | 13280 | 1.62 | 8197.5309 | 2.3737 | 12880 | 1.53 | 8418.3007 | 2.031 | 12560 | 1.39 | 9035.9712 | 1.833
|  | 15218.1818 | 57.2192 | nom | 14000 | 2.64 | 5303.0303 | 74732.1429 | 14000 | 2.34 | 5982.906 | -3898.917 | 14000 | 2.12 | 6603.7736 | 4653.1596 | 14000 | 1.9 | 7368.4211 | 6411.0638 | 14000 | 1.77 | 7909.6045 | 7492.8064 | 14000 | 1.63 | 8588.9571 | 8302.1987
|  |  | 100 | mid | 11200 | 2.69 | 4163.5688 | 3 | 11200 | 2.54 | 4409.4488 | 3 | 11200 | 2.35 | 4765.9574 | 3 | 11200 | 2.15 | 5209.3023 | 3 | 11200 | 1.94 | 5773.1959 | 3 | 11200 | 1.73 | 6473.9884 | 3
|  |  | 8720.2809 | min | 7720 | 2.59 | 2980.695 | 4.3506 | 7420 | 2.34 | 3170.9402 | 15.2273 | 6880 | 2.01 | 3422.8856 | -3.3838 | 6260 | 1.63 | 3840.4908 | -1.6919 | 5480 | 1.33 | 4120.3008 | -1.0877 | 4640 | 1.02 | 4549.0196 | -0.84596
| -13 |  | 1.7434 | max | 14360 | 2.16 | 6648.1481 | 1.531 | 14160 | 2.01 | 7044.7761 | 0.54051 | 13780 | 1.86 | 7408.6022 | 3.1524 | 13460 | 1.69 | 7964.497 | 2.2093 | 13160 | 1.61 | 8173.913 | 1.9605 | 12920 | 1.48 | 8729.7297 | 1.7926
|  | 14795.4545 | 56.4642 | nom | 14000 | 2.68 | 5223.8806 | 9663.8517 | 14000 | 2.38 | 5882.3529 | 27373.0684 | 14000 | 2.14 | 6542.0561 | 4693.3987 | 14000 | 1.9 | 7368.4211 | 6696.7653 | 14000 | 1.79 | 7821.2291 | 7546.9511 | 14000 | 1.66 | 8433.7349 | 8253.7402
|  |  | 100 | mid | 11200 | 2.73 | 4102.5641 | 3 | 11200 | 2.58 | 4341.0853 | 3 | 11200 | 2.4 | 4666.6667 | 3 | 11200 | 2.2 | 5090.9091 | 3 | 11200 | 1.98 | 5656.5657 | 3 | 11200 | 1.76 | 6363.6364 | 3
|  |  | 8486.4772 | min | 7340 | 2.58 | 2844.9612 | 2.2096 | 7040 | 2.33 | 3021.4592 | 4.9716 | 6560 | 2.02 | 3247.5248 | -3.6157 | 6020 | 1.66 | 3626.506 | -1.4731 | 5260 | 1.36 | 3867.6471 | -0.94697 | 4480 | 1.04 | 4307.6923 | -0.73653
| -12 |  | 1.7327 | max | 14440 | 2.24 | 6446.4286 | 2.3134 | 14240 | 2.09 | 6813.3971 | 1.9075 | 13920 | 1.94 | 7175.2577 | 3.185 | 13640 | 1.76 | 7750 | 2.0449 | 13440 | 1.69 | 7952.6627 | 1.8899 | 13280 | 1.57 | 8458.5987 | 1.7521
|  | 14372.7273 | 55.7042 | nom | 14000 | 2.72 | 5147.0588 | 6212.8465 | 14000 | 2.42 | 5785.124 | 7534.8505 | 14000 | 2.16 | 6481.4815 | 4512.6302 | 14000 | 1.9 | 7368.4211 | 7028.4021 | 14000 | 1.81 | 7734.8066 | 7605.1402 | 14000 | 1.69 | 8284.0237 | 8203.0439
|  |  | 100 | mid | 11200 | 2.77 | 4043.3213 | 3 | 11200 | 2.62 | 4274.8092 | 3 | 11200 | 2.45 | 4571.4286 | 3 | 11200 | 2.25 | 4977.7778 | 3 | 11200 | 2.02 | 5544.5545 | 3 | 11200 | 1.79 | 6256.9832 | 3
|  |  | 8294.8878 | min | 6960 | 2.57 | 2708.1712 | 0.84711 | 6660 | 2.32 | 2870.6897 | 1.553 | 6240 | 2.03 | 3073.8916 | -4.6591 | 5780 | 1.69 | 3420.1183 | -1.0354 | 5040 | 1.39 | 3625.8993 | -0.66558 | 4320 | 1.06 | 4075.4717 | -0.51768
| -11 |  | 1.7232 | max | 14520 | 2.32 | 6258.6207 | 2.7609 | 14320 | 2.17 | 6599.0783 | 2.4636 | 14060 | 2.02 | 6960.396 | 2.1857 | 13820 | 1.83 | 7551.9126 | 1.9071 | 13720 | 1.77 | 7751.4124 | 1.8341 | 13640 | 1.66 | 8216.8675 | 1.7218
|  | 13950 | 54.939 | nom | 14000 | 2.76 | 5072.4638 | 5052.7133 | 14000 | 2.46 | 5691.0569 | 5662.5109 | 14000 | 2.18 | 6422.0183 | 6382.3529 | 14000 | 1.9 | 7368.4211 | 7314.6067 | 14000 | 1.83 | 7650.2732 | 7605.8806 | 14000 | 1.72 | 8139.5349 | 8102.0535
|  |  | 100 | mid | 11200 | 2.81 | 3985.7651 | 2 | 11200 | 2.66 | 4210.5263 | 2 | 11200 | 2.5 | 4480 | 2 | 11200 | 2.3 | 4869.5652 | 2 | 11200 | 2.06 | 5436.8932 | 2 | 11200 | 1.82 | 6153.8462 | 2
|  |  | 8095.6131 | min | 6580 | 2.56 | 2570.3125 | 0.98214 | 6280 | 2.31 | 2718.6147 | 0.98214 | 5920 | 2.04 | 2901.9608 | 0.98214 | 5540 | 1.72 | 3220.9302 | 0.98214 | 4820 | 1.42 | 3394.3662 | 0.98214 | 4160 | 1.08 | 3851.8519 | 0.98214
| -10 |  | 1.7877 | max | 14600 | 2.4 | 6083.3333 | 2.8084 | 14400 | 2.25 | 6400 | 2.5338 | 14200 | 2.1 | 6761.9048 | 2.2591 | 14000 | 1.9 | 7368.4211 | 1.976 | 14000 | 1.85 | 7567.5676 | 1.8922 | 14000 | 1.75 | 8000 | 1.7669
|  | 13527.2727 | 54.1685 | nom | 14000 | 2.8 | 5000 | 4816.6474 | 14000 | 2.5 | 5600 | 5338.8006 | 14000 | 2.2 | 6363.6364 | 5987.9276 | 14000 | 1.9 | 7368.4211 | 6845.8758 | 14000 | 1.85 | 7567.5676 | 7148.9362 | 14000 | 1.75 | 8000 | 7656.0088
|  |  | 100 | mid | 11200 | 2.85 | 3929.8246 | 2 | 11200 | 2.7 | 4148.1481 | 2 | 11200 | 2.55 | 4392.1569 | 2 | 11200 | 2.35 | 4765.9574 | 2 | 11200 | 2.1 | 5333.3333 | 2 | 11200 | 1.85 | 6054.0541 | 2
|  |  | 7566.7539 | min | 6200 | 2.55 | 2431.3725 | 0.83117 | 5900 | 2.3 | 2565.2174 | 0.83117 | 5600 | 2.05 | 2731.7073 | 0.83117 | 5300 | 1.75 | 3028.5714 | 0.83117 | 4600 | 1.45 | 3172.4138 | 0.83117 | 4000 | 1.1 | 3636.3636 | 0.83117
| -9 |  | 1.9071 | max | 15100 | 2.5 | 6040 | 2.9153 | 14900 | 2.3333 | 6385.7143 | 2.664 | 14700 | 2.1667 | 6784.6154 | 2.4126 | 14500 | 1.9667 | 7372.8814 | 2.1506 | 14233.3333 | 1.9167 | 7426.087 | 2.0193 | 14000 | 1.8167 | 7706.422 | 1.854
|  | 13104.5455 | 53.3924 | nom | 14000 | 2.8833 | 4855.4913 | 4495.0719 | 14000 | 2.6 | 5384.6154 | 4919.1956 | 14000 | 2.3167 | 6043.1655 | 5431.6923 | 14000 | 2.0333 | 6885.2459 | 6093.4504 | 14000 | 1.95 | 7179.4872 | 6489.6761 | 14000 | 1.8167 | 7706.422 | 7068.342
|  |  | 100 | mid | 11200 | 2.9833 | 3754.1899 | 2 | 11200 | 2.8 | 4000 | 2 | 11200 | 2.6167 | 4280.2548 | 2 | 11200 | 2.4 | 4666.6667 | 2 | 11200 | 2.1667 | 5169.2308 | 2 | 11200 | 1.9333 | 5793.1034 | 2
|  |  | 6871.3462 | min | 5833.3333 | 2.9167 | 2000 | 0.68019 | 5266.6667 | 2.2833 | 2306.5693 | 0.68019 | 5066.6667 | 2.05 | 2471.5447 | 0.68019 | 4866.6667 | 1.7833 | 2728.972 | 0.68019 | 4266.6667 | 1.4667 | 2909.0909 | 0.68019 | 3700 | 1.1167 | 3313.4328 | 0.68019
| -8 |  | 2.037 | max | 15600 | 2.6 | 6000 | 3.0373 | 15400 | 2.4167 | 6372.4138 | 2.7942 | 15200 | 2.2333 | 6805.9701 | 2.551 | 15000 | 2.0333 | 7377.0492 | 2.3001 | 14466.6667 | 1.9833 | 7294.1176 | 2.1363 | 14000 | 1.8833 | 7433.6283 | 1.9461
|  | 12681.8182 | 52.6105 | nom | 14000 | 2.9667 | 4719.1011 | 4175.3817 | 14000 | 2.7 | 5185.1852 | 4538.6939 | 14000 | 2.4333 | 5753.4247 | 4971.2577 | 14000 | 2.1667 | 6461.5385 | 5513.7043 | 14000 | 2.05 | 6829.2683 | 5936.3206 | 14000 | 1.8833 | 7433.6283 | 6516.5165
|  |  | 100 | mid | 11200 | 3.1167 | 3593.5829 | 2 | 11200 | 2.9 | 3862.069 | 2 | 11200 | 2.6833 | 4173.913 | 2 | 11200 | 2.45 | 4571.4286 | 2 | 11200 | 2.2333 | 5014.9254 | 2 | 11200 | 2.0167 | 5553.719 | 2
|  |  | 6225.7217 | min | 5466.6667 | 3.2833 | 1664.9746 | 0.52922 | 4633.3333 | 2.2667 | 2044.1176 | 0.52922 | 4533.3333 | 2.05 | 2211.3821 | 0.52922 | 4433.3333 | 1.8167 | 2440.367 | 0.52922 | 3933.3333 | 1.4833 | 2651.6854 | 0.52922 | 3400 | 1.1333 | 3000 | 0.52922
| -7 |  | 2.1704 | max | 16100 | 2.7 | 5962.963 | 3.1744 | 15900 | 2.5 | 6360 | 2.9244 | 15700 | 2.3 | 6826.087 | 2.6744 | 15500 | 2.1 | 7380.9524 | 2.4244 | 14700 | 2.05 | 7170.7317 | 2.2433 | 14000 | 1.95 | 7179.4872 | 2.0433
|  | 12259.0909 | 51.8225 | nom | 14000 | 3.05 | 4590.1639 | 3861.9208 | 14000 | 2.8 | 5000 | 4192.0728 | 14000 | 2.55 | 5490.1961 | 4583.9505 | 14000 | 2.3 | 6086.9565 | 5056.6493 | 14000 | 2.15 | 6511.6279 | 5464.8478 | 14000 | 1.95 | 7179.4872 | 5999.7616
|  |  | 100 | mid | 11200 | 3.25 | 3446.1538 | 2 | 11200 | 3 | 3733.3333 | 2 | 11200 | 2.75 | 4072.7273 | 2 | 11200 | 2.5 | 4480 | 2 | 11200 | 2.3 | 4869.5652 | 2 | 11200 | 2.1 | 5333.3333 | 2
|  |  | 5648.41 | min | 5100 | 3.65 | 1397.2603 | 0.37825 | 4000 | 2.25 | 1777.7778 | 0.37825 | 4000 | 2.05 | 1951.2195 | 0.37825 | 4000 | 1.85 | 2162.1622 | 0.37825 | 3600 | 1.5 | 2400 | 0.37825 | 3100 | 1.15 | 2695.6522 | 0.37825
| -6 |  | 2.2738 | max | 16144.4444 | 2.7611 | 5847.0825 | 3.2477 | 15944.4444 | 2.5556 | 6239.1304 | 2.9977 | 15733.3333 | 2.35 | 6695.0355 | 2.7477 | 15533.3333 | 2.1444 | 7243.5233 | 2.4977 | 14744.4444 | 2.0944 | 7039.7878 | 2.3146 | 14033.3333 | 1.9944 | 7036.2117 | 2.1159
|  | 11836.3636 | 51.0283 | nom | 14000 | 3.0889 | 4532.3741 | 3644.5066 | 14000 | 2.8389 | 4931.5068 | 3948.4458 | 14000 | 2.5889 | 5407.7253 | 4307.6923 | 14000 | 2.3389 | 5985.7482 | 4738.8535 | 14000 | 2.1944 | 6379.7468 | 5113.681 | 14000 | 2 | 7000 | 5593.985
|  |  | 100 | mid | 11200 | 3.2944 | 3399.6627 | 2 | 11200 | 3.0444 | 3678.8321 | 2 | 11200 | 2.7944 | 4007.9523 | 2 | 11200 | 2.5444 | 4401.7467 | 2 | 11200 | 2.35 | 4765.9574 | 2 | 11200 | 2.15 | 5209.3023 | 2
|  |  | 5205.6021 | min | 5155.5556 | 3.7111 | 1389.2216 | 0.22727 | 4122.2222 | 2.4056 | 1713.6259 | 0.22727 | 4077.7778 | 2.1667 | 1882.0513 | 0.22727 | 4022.2222 | 1.9222 | 2092.4855 | 0.22727 | 3611.1111 | 1.5611 | 2313.1673 | 0.22727 | 3111.1111 | 1.1944 | 2604.6512 | 0.22727
| -5 |  | 2.3786 | max | 16188.8889 | 2.8222 | 5736.2205 | 3.3228 | 15988.8889 | 2.6111 | 6123.4043 | 3.0728 | 15766.6667 | 2.4 | 6569.4444 | 2.8228 | 15566.6667 | 2.1889 | 7111.6751 | 2.5728 | 14788.8889 | 2.1389 | 6914.2857 | 2.3877 | 14066.6667 | 2.0389 | 6899.1826 | 2.1886
|  | 11413.6364 | 50.2275 | nom | 14000 | 3.1278 | 4476.0213 | 3434.9646 | 14000 | 2.8778 | 4864.8649 | 3714.4316 | 14000 | 2.6278 | 5327.6956 | 4043.4007 | 14000 | 2.3778 | 5887.8505 | 4436.3025 | 14000 | 2.2389 | 6253.1017 | 4780.1654 | 14000 | 2.05 | 6829.2683 | 5215.1467
|  |  | 100 | mid | 11200 | 3.3389 | 3354.4093 | 2 | 11200 | 3.0889 | 3625.8993 | 2 | 11200 | 2.8389 | 3945.2055 | 2 | 11200 | 2.5889 | 4326.1803 | 2 | 11200 | 2.4 | 4666.6667 | 2 | 11200 | 2.2 | 5090.9091 | 2
|  |  | 4798.374 | min | 5211.1111 | 3.7722 | 1381.4433 | 0.076299 | 4244.4444 | 2.5611 | 1657.2668 | 0.076299 | 4155.5556 | 2.2833 | 1819.9513 | 0.076299 | 4044.4444 | 1.9944 | 2027.8552 | 0.076299 | 3622.2222 | 1.6222 | 2232.8767 | 0.076299 | 3122.2222 | 1.2389 | 2520.1794 | 0.076299
| -4 |  | 2.4506 | max | 16233.3333 | 2.8833 | 5630.0578 | 3.3992 | 16033.3333 | 2.6667 | 6012.5 | 3.1206 | 15800 | 2.45 | 6448.9796 | 2.8688 | 15600 | 2.2333 | 6985.0746 | 2.6167 | 14833.3333 | 2.1833 | 6793.8931 | 2.4288 | 14100 | 2.0833 | 6768 | 2.2249
|  | 10990.9091 | 49.4198 | nom | 14000 | 3.1667 | 4421.0526 | 3233.3893 | 14000 | 2.9167 | 4800 | 3522.0681 | 14000 | 2.6667 | 5250 | 3831.1508 | 14000 | 2.4167 | 5793.1034 | 4200.2565 | 14000 | 2.2833 | 6131.3869 | 4525.2154 | 14000 | 2.1 | 6666.6667 | 4939.8595
|  |  | 100 | mid | 11200 | 3.3833 | 3310.3448 | 1 | 11200 | 3.1333 | 3574.4681 | 1 | 11200 | 2.8833 | 3884.3931 | 1 | 11200 | 2.6333 | 4253.1646 | 1 | 11200 | 2.45 | 4571.4286 | 1 | 11200 | 2.25 | 4977.7778 | 1
|  |  | 4484.9507 | min | 5266.6667 | 3.8333 | 1373.913 | 0.96476 | 4366.6667 | 2.7167 | 1607.362 | 0.9694 | 4233.3333 | 2.4 | 1763.8889 | 0.96999 | 4066.6667 | 2.0667 | 1967.7419 | 0.97069 | 3633.3333 | 1.6833 | 2158.4158 | 0.97237 | 3133.3333 | 1.2833 | 2441.5584 | 0.97408
| -3 |  | 2.4907 | max | 16277.7778 | 2.9444 | 5528.3019 | 3.4779 | 16077.7778 | 2.7222 | 5906.1224 | 3.149 | 15833.3333 | 2.5 | 6333.3333 | 2.8901 | 15633.3333 | 2.2778 | 6863.4146 | 2.6299 | 14877.7778 | 2.2278 | 6678.3042 | 2.4368 | 14133.3333 | 2.1278 | 6642.2977 | 2.2237
|  | 10568.1818 | 48.6049 | nom | 14000 | 3.2056 | 4367.4177 | 3038.6317 | 14000 | 2.9556 | 4736.8421 | 3356.0318 | 14000 | 2.7056 | 5174.538 | 3656.7186 | 14000 | 2.4556 | 5701.3575 | 4018.4762 | 14000 | 2.3278 | 6014.3198 | 4336.8774 | 14000 | 2.15 | 6511.6279 | 4752.4229
|  |  | 100 | mid | 11200 | 3.4278 | 3267.423 | 1 | 11200 | 3.1778 | 3524.4755 | 1 | 11200 | 2.9278 | 3825.4269 | 1 | 11200 | 2.6778 | 4182.5726 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1
|  |  | 4243.0715 | min | 5322.2222 | 3.8944 | 1366.6191 | 0.89251 | 4488.8889 | 2.8722 | 1562.8627 | 0.90585 | 4311.1111 | 2.5167 | 1713.0243 | 0.90828 | 4088.8889 | 2.1389 | 1911.6883 | 0.91115 | 3644.4444 | 1.7444 | 2089.172 | 0.91638 | 3144.4444 | 1.3278 | 2368.2008 | 0.92157
| -2 |  | 2.5348 | max | 16322.2222 | 3.0056 | 5430.6839 | 3.5598 | 16122.2222 | 2.7778 | 5804 | 3.1911 | 15866.6667 | 2.55 | 6222.2222 | 2.9198 | 15666.6667 | 2.3222 | 6746.4115 | 2.6462 | 14922.2222 | 2.2722 | 6567.2372 | 2.4459 | 14166.6667 | 2.1722 | 6521.7391 | 2.2218
|  | 10145.4545 | 47.7824 | nom | 14000 | 3.2444 | 4315.0685 | 2850.0344 | 14000 | 2.9944 | 4675.3247 | 3179.2954 | 14000 | 2.7444 | 5101.2146 | 3474.7647 | 14000 | 2.4944 | 5612.4722 | 3833.9869 | 14000 | 2.3722 | 5901.6393 | 4147.87 | 14000 | 2.2 | 6363.6364 | 4566.2745
|  |  | 100 | mid | 11200 | 3.4722 | 3225.6 | 1 | 11200 | 3.2222 | 3475.8621 | 1 | 11200 | 2.9722 | 3768.2243 | 1 | 11200 | 2.7222 | 4114.2857 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1
|  |  | 4002.5391 | min | 5377.7778 | 3.9556 | 1359.5506 | 0.81888 | 4611.1111 | 3.0278 | 1522.9358 | 0.83995 | 4388.8889 | 2.6333 | 1666.6667 | 0.84517 | 4111.1111 | 2.2111 | 1859.2965 | 0.85124 | 3655.5556 | 1.8056 | 2024.6154 | 0.86022 | 3155.5556 | 1.3722 | 2299.5951 | 0.86891
| -1 |  | 2.5839 | max | 16366.6667 | 3.0667 | 5336.9565 | 3.6448 | 16166.6667 | 2.8333 | 5705.8824 | 3.2476 | 15900 | 2.6 | 6115.3846 | 2.9582 | 15700 | 2.3667 | 6633.8028 | 2.6656 | 14966.6667 | 2.3167 | 6460.4317 | 2.4562 | 14200 | 2.2167 | 6406.015 | 2.2192
|  | 9722.7273 | 46.952 | nom | 14000 | 3.2833 | 4263.9594 | 2667.595 | 14000 | 3.0333 | 4615.3846 | 2993.7919 | 14000 | 2.7833 | 5029.9401 | 3286.7474 | 14000 | 2.5333 | 5526.3158 | 3647.4451 | 14000 | 2.4167 | 5793.1034 | 3958.4514 | 14000 | 2.25 | 6222.2222 | 4381.2409
|  |  | 100 | mid | 11200 | 3.5167 | 3184.8341 | 1 | 11200 | 3.2667 | 3428.5714 | 1 | 11200 | 3.0167 | 3712.7072 | 1 | 11200 | 2.7667 | 4048.1928 | 1 | 11200 | 2.6 | 4307.6923 | 1 | 11200 | 2.4 | 4666.6667 | 1
|  |  | 3762.8651 | min | 5433.3333 | 4.0167 | 1352.6971 | 0.74383 | 4733.3333 | 3.1833 | 1486.911 | 0.77156 | 4466.6667 | 2.75 | 1624.2424 | 0.7806 | 4133.3333 | 2.2833 | 1810.219 | 0.79095 | 3666.6667 | 1.8667 | 1964.2857 | 0.8039 | 3166.6667 | 1.4167 | 2235.2941 | 0.81611
| 0 |  | 2.6391 | max | 16411.1111 | 3.1278 | 5246.8917 | 3.733 | 16211.1111 | 2.8889 | 5611.5385 | 3.3194 | 15933.3333 | 2.65 | 6012.5786 | 3.0056 | 15733.3333 | 2.4111 | 6525.3456 | 2.6882 | 15011.1111 | 2.3611 | 6357.6471 | 2.4676 | 14233.3333 | 2.2611 | 6294.8403 | 2.2158
|  | 9300 | 46.1133 | nom | 14000 | 3.3222 | 4214.0468 | 2491.295 | 14000 | 3.0722 | 4556.962 | 2801.686 | 14000 | 2.8222 | 4960.6299 | 3094.2221 | 14000 | 2.5722 | 5442.7646 | 3459.512 | 14000 | 2.4611 | 5688.4876 | 3768.8785 | 14000 | 2.3 | 6086.9565 | 4197.1496
|  |  | 100 | mid | 11200 | 3.5611 | 3145.0858 | 1 | 11200 | 3.3111 | 3382.5503 | 1 | 11200 | 3.0611 | 3658.8022 | 1 | 11200 | 2.8111 | 3984.1897 | 1 | 11200 | 2.65 | 4226.4151 | 1 | 11200 | 2.45 | 4571.4286 | 1
|  |  | 3523.9161 | min | 5488.8889 | 4.0778 | 1346.049 | 0.66732 | 4855.5556 | 3.3389 | 1454.2429 | 0.70053 | 4544.4444 | 2.8667 | 1585.2713 | 0.71452 | 4155.5556 | 2.3556 | 1764.1509 | 0.73028 | 3677.7778 | 1.9278 | 1907.781 | 0.74742 | 3177.7778 | 1.4611 | 2174.9049 | 0.76316
| 1 |  | 2.7016 | max | 16455.5556 | 3.1889 | 5160.2787 | 3.8246 | 16255.5556 | 2.9444 | 5520.7547 | 3.4074 | 15966.6667 | 2.7 | 5913.5802 | 3.0624 | 15766.6667 | 2.4556 | 6420.8145 | 2.7141 | 15055.5556 | 2.4056 | 6258.6605 | 2.4801 | 14266.6667 | 2.3056 | 6187.9518 | 2.2117
|  | 8877.2727 | 45.2656 | nom | 14000 | 3.3611 | 4165.2893 | 2321.1016 | 14000 | 3.1111 | 4500 | 2605.2906 | 14000 | 2.8611 | 4893.2039 | 2898.799 | 14000 | 2.6111 | 5361.7021 | 3270.8458 | 14000 | 2.5056 | 5587.5831 | 3579.4057 | 14000 | 2.35 | 5957.4468 | 4013.8278
|  |  | 100 | mid | 11200 | 3.6056 | 3106.3174 | 1 | 11200 | 3.3556 | 3337.7483 | 1 | 11200 | 3.1056 | 3606.4401 | 1 | 11200 | 2.8556 | 3922.179 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.5 | 4480 | 1
|  |  | 3285.8943 | min | 5544.4444 | 4.1389 | 1339.5973 | 0.5893 | 4977.7778 | 3.4944 | 1424.4833 | 0.6267 | 4622.2222 | 2.9833 | 1549.3482 | 0.64688 | 4177.7778 | 2.4278 | 1720.8238 | 0.66923 | 3688.8889 | 1.9889 | 1854.7486 | 0.69076 | 3188.8889 | 1.5056 | 2118.0812 | 0.71006
14kW-Maximum heating CAP | 2 |  | 2.7887 | max | 16500 | 3.25 | 5076.9231 | 3.9196 | 16300 | 3 | 5433.3333 | 3.5125 | 16000 | 2.75 | 5818.1818 | 3.1289 | 15800 | 2.5 | 6320 | 2.7431 | 15100 | 2.45 | 6163.2653 | 2.4938 | 14300 | 2.35 | 6085.1064 | 2.2068
|  | 8454.5455 | 44.4086 | nom | 14000 | 3.4 | 4117.6471 | 2156.9683 | 14000 | 3.15 | 4444.4444 | 2406.9753 | 14000 | 2.9 | 4827.5862 | 2702.0987 | 14000 | 2.65 | 5283.0189 | 3082.0945 | 14000 | 2.55 | 5490.1961 | 3390.2836 | 14000 | 2.4 | 5833.3333 | 3831.102
|  |  | 100 | mid | 11200 | 3.65 | 3068.4932 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 3.15 | 3555.5556 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.55 | 4392.1569 | 1
|  |  | 3031.6696 | min | 5600 | 4.2 | 1333.3333 | 0.50974 | 5100 | 3.65 | 1397.2603 | 0.54993 | 4700 | 3.1 | 1516.129 | 0.57762 | 4200 | 2.5 | 1680 | 0.60779 | 3700 | 2.05 | 1804.878 | 0.63394 | 3200 | 1.55 | 2064.5161 | 0.65682
| 3 |  | 2.9678 | max | 16560 | 3.54 | 4677.9661 | 4.3565 | 16360 | 3.25 | 5033.8462 | 3.7456 | 16080 | 2.96 | 5432.4324 | 3.2907 | 15860 | 2.66 | 5962.406 | 2.8348 | 15160 | 2.54 | 5968.5039 | 2.5344 | 14360 | 2.38 | 6033.6134 | 2.1989
|  | 8031.8182 | 43.5417 | nom | 14000 | 3.7 | 3783.7838 | 1843.6416 | 14000 | 3.41 | 4105.5718 | 2144.3437 | 14000 | 3.12 | 4487.1795 | 2440.7637 | 14000 | 2.82 | 4964.539 | 2833.3074 | 14000 | 2.67 | 5243.4457 | 3169.145 | 14000 | 2.47 | 5668.0162 | 3652.7132
|  |  | 100 | mid | 11200 | 3.97 | 2821.1587 | 1 | 11200 | 3.68 | 3043.4783 | 1 | 11200 | 3.39 | 3303.8348 | 1 | 11200 | 3.09 | 3624.5955 | 1 | 11200 | 2.88 | 3888.8889 | 1 | 11200 | 2.62 | 4274.8092 | 1
|  |  | 2706.3587 | min | 5380 | 4.68 | 1149.5726 | 0.45564 | 4920 | 3.81 | 1291.3386 | 0.49551 | 4500 | 3.18 | 1415.0943 | 0.52714 | 4000 | 2.51 | 1593.6255 | 0.55997 | 3500 | 2.04 | 1715.6863 | 0.58855 | 3000 | 1.53 | 1960.7843 | 0.61364
| 4 |  | 3.157 | max | 16620 | 3.83 | 4339.4256 | 4.8072 | 16420 | 3.5 | 4691.4286 | 3.9656 | 16160 | 3.17 | 5097.7918 | 3.4374 | 15920 | 2.82 | 5645.3901 | 2.9112 | 15220 | 2.63 | 5787.0722 | 2.5645 | 14420 | 2.41 | 5983.4025 | 2.1856
|  | 7609.0909 | 42.6641 | nom | 14000 | 4 | 3500 | 1582.8419 | 14000 | 3.67 | 3814.7139 | 1918.7942 | 14000 | 3.34 | 4191.6168 | 2213.5898 | 14000 | 2.99 | 4682.2742 | 2613.7265 | 14000 | 2.79 | 5017.9211 | 2967.033 | 14000 | 2.54 | 5511.811 | 3481.5248
|  |  | 100 | mid | 11200 | 4.29 | 2610.7226 | 1 | 11200 | 3.96 | 2828.2828 | 1 | 11200 | 3.63 | 3085.3994 | 1 | 11200 | 3.28 | 3414.6341 | 1 | 11200 | 3.01 | 3720.9302 | 1 | 11200 | 2.69 | 4163.5688 | 1
|  |  | 2410.1913 | min | 5160 | 5.16 | 1000 | 0.40548 | 4740 | 3.97 | 1193.9547 | 0.44413 | 4300 | 3.26 | 1319.0184 | 0.47958 | 3800 | 2.52 | 1507.9365 | 0.51474 | 3300 | 2.03 | 1625.6158 | 0.54545 | 2800 | 1.51 | 1854.3046 | 0.57251
| 5 |  | 3.3585 | max | 16680 | 4.12 | 4048.5437 | 5.2704 | 16480 | 3.75 | 4394.6667 | 4.1735 | 16240 | 3.38 | 4804.7337 | 3.5704 | 15980 | 2.98 | 5362.4161 | 2.9736 | 15280 | 2.72 | 5617.6471 | 2.585 | 14480 | 2.44 | 5934.4262 | 2.1673
|  | 7186.3636 | 41.7753 | nom | 14000 | 4.3 | 3255.814 | 1363.5353 | 14000 | 3.93 | 3562.341 | 1721.8996 | 14000 | 3.56 | 3932.5843 | 2012.7668 | 14000 | 3.16 | 4430.3797 | 2416.7408 | 14000 | 2.91 | 4810.9966 | 2779.9944 | 14000 | 2.61 | 5363.9847 | 3315.8314
|  |  | 100 | mid | 11200 | 4.61 | 2429.5011 | 1 | 11200 | 4.24 | 2641.5094 | 1 | 11200 | 3.87 | 2894.0568 | 1 | 11200 | 3.47 | 3227.6657 | 1 | 11200 | 3.14 | 3566.879 | 1 | 11200 | 2.76 | 4057.971 | 1
|  |  | 2139.7602 | min | 4940 | 5.64 | 875.8865 | 0.35884 | 4560 | 4.13 | 1104.1162 | 0.39554 | 4100 | 3.34 | 1227.5449 | 0.4347 | 3600 | 2.53 | 1422.9249 | 0.47189 | 3100 | 2.02 | 1534.6535 | 0.50449 | 2600 | 1.49 | 1744.9664 | 0.5333
| 6 |  | 3.5739 | max | 16740 | 4.41 | 3795.9184 | 5.7447 | 16540 | 4 | 4135 | 4.3704 | 16320 | 3.59 | 4545.961 | 3.6907 | 16040 | 3.14 | 5108.2803 | 3.023 | 15340 | 2.81 | 5459.0747 | 2.5965 | 14540 | 2.47 | 5886.6397 | 2.1444
|  | 6763.6364 | 40.8742 | nom | 14000 | 4.6 | 3043.4783 | 1177.3693 | 14000 | 4.19 | 3341.2888 | 1547.606 | 14000 | 3.78 | 3703.7037 | 1832.6298 | 14000 | 3.33 | 4204.2042 | 2237.4042 | 14000 | 3.03 | 4620.462 | 2604.8772 | 14000 | 2.68 | 5223.8806 | 3154.1219
|  |  | 100 | mid | 11200 | 4.93 | 2271.8053 | 1 | 11200 | 4.52 | 2477.8761 | 1 | 11200 | 4.11 | 2725.0608 | 1 | 11200 | 3.66 | 3060.1093 | 1 | 11200 | 3.27 | 3425.0765 | 1 | 11200 | 2.83 | 3957.5972 | 1
|  |  | 1892.4928 | min | 4720 | 6.12 | 771.2418 | 0.31538 | 4380 | 4.29 | 1020.979 | 0.34951 | 3900 | 3.42 | 1140.3509 | 0.39228 | 3400 | 2.54 | 1338.5827 | 0.43124 | 2900 | 2.01 | 1442.7861 | 0.4655 | 2400 | 1.47 | 1632.6531 | 0.49587
| 7 |  | 3.8054 | max | 16800 | 4.7 | 3574.4681 | 6.2291 | 16600 | 4.25 | 3905.8824 | 4.557 | 16400 | 3.8 | 4315.7895 | 3.7993 | 16100 | 3.3 | 4878.7879 | 3.0604 | 15400 | 2.9 | 5310.3448 | 2.5997 | 14600 | 2.5 | 5840 | 2.1171
|  | 6340.9091 | 39.9601 | nom | 14000 | 4.9 | 2857.1429 | 1017.9543 | 14000 | 4.45 | 3146.0674 | 1391.4518 | 14000 | 4 | 3500 | 1668.9664 | 14000 | 3.5 | 4000 | 2071.9232 | 14000 | 3.15 | 4444.4444 | 2439.1122 | 14000 | 2.75 | 5090.9091 | 2995.0262
|  |  | 100 | mid | 11200 | 5.25 | 2133.3333 | 1 | 11200 | 4.8 | 2333.3333 | 1 | 11200 | 4.35 | 2574.7126 | 1 | 11200 | 3.85 | 2909.0909 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 2.9 | 3862.069 | 1
|  |  | 1666.3142 | min | 4500 | 6.6 | 681.8182 | 0.27476 | 4200 | 4.45 | 943.8202 | 0.30584 | 3700 | 3.5 | 1057.1429 | 0.35212 | 3200 | 2.55 | 1254.902 | 0.39261 | 2700 | 2 | 1350 | 0.42834 | 2200 | 1.45 | 1517.2414 | 0.4601
| 8 |  | 4.0665 | max | 16860 | 4.81 | 3505.1975 | 6.1606 | 16640 | 4.38 | 3799.0868 | 4.6219 | 16440 | 3.93 | 4183.2061 | 3.9332 | 16160 | 3.48 | 4643.6782 | 3.2565 | 15440 | 3.06 | 5045.7516 | 2.7613 | 14640 | 2.64 | 5545.4545 | 2.2527
|  | 5918.1818 | 39.0318 | nom | 14000 | 5.02 | 2788.8446 | 960.6517 | 14000 | 4.59 | 3050.1089 | 1280.4687 | 14000 | 4.16 | 3365.3846 | 1504.6795 | 14000 | 3.69 | 3794.0379 | 1817.3171 | 14000 | 3.32 | 4216.8675 | 2143.2452 | 14000 | 2.9 | 4827.5862 | 2627.1413
|  |  | 100 | mid | 11200 | 5.37 | 2085.6611 | 1 | 11200 | 4.95 | 2262.6263 | 1 | 11200 | 4.53 | 2472.4062 | 1 | 11200 | 4.06 | 2758.6207 | 1 | 11200 | 3.58 | 3128.4916 | 1 | 11200 | 3.06 | 3660.1307 | 1
|  |  | 1455.3333 | min | 4920 | 6.31 | 779.7147 | 0.15895 | 4600 | 4.54 | 1013.2159 | 0.19972 | 4120 | 3.73 | 1104.5576 | 0.25398 | 3640 | 2.91 | 1250.8591 | 0.30135 | 3200 | 2.34 | 1367.5214 | 0.33977 | 2760 | 1.77 | 1559.322 | 0.37419
| 9 |  | 4.297 | max | 16920 | 4.92 | 3439.0244 | 6.0059 | 16680 | 4.51 | 3698.4479 | 4.6676 | 16480 | 4.06 | 4059.1133 | 4.0676 | 16220 | 3.66 | 4431.694 | 3.4688 | 15480 | 3.22 | 4807.4534 | 2.9385 | 14680 | 2.78 | 5280.5755 | 2.402
|  | 5495.4545 | 38.088 | nom | 14000 | 5.14 | 2723.7354 | 915.0032 | 14000 | 4.73 | 2959.8309 | 1177.3724 | 14000 | 4.32 | 3240.7407 | 1351.0325 | 14000 | 3.88 | 3608.2474 | 1584.2524 | 14000 | 3.49 | 4011.4613 | 1870.1275 | 14000 | 3.05 | 4590.1639 | 2287.902
|  |  | 100 | mid | 11200 | 5.49 | 2040.0729 | 1 | 11200 | 5.1 | 2196.0784 | 1 | 11200 | 4.71 | 2377.9193 | 1 | 11200 | 4.27 | 2622.9508 | 1 | 11200 | 3.76 | 2978.7234 | 1 | 11200 | 3.22 | 3478.2609 | 1
|  |  | 1278.8992 | min | 5340 | 6.02 | 887.0432 | 0.026528 | 5000 | 4.63 | 1079.9136 | 0.079912 | 4540 | 3.96 | 1146.4646 | 0.14346 | 4080 | 3.27 | 1247.7064 | 0.1988 | 3700 | 2.68 | 1380.597 | 0.23939 | 3320 | 2.09 | 1588.5167 | 0.27607
| 10 |  | 4.4999 | max | 16980 | 5.03 | 3375.7455 | 5.73 | 16720 | 4.64 | 3603.4483 | 4.72 | 16520 | 4.19 | 3942.7208 | 4.2026 | 16280 | 3.84 | 4239.5833 | 3.7003 | 15520 | 3.38 | 4591.716 | 3.1347 | 14720 | 2.92 | 5041.0959 | 2.5681
|  | 5072.7273 | 37.1273 | nom | 14000 | 5.26 | 2661.597 | 885.2927 | 14000 | 4.87 | 2874.7433 | 1074.7304 | 14000 | 4.48 | 3125 | 1207.0319 | 14000 | 4.07 | 3439.8034 | 1370.8843 | 14000 | 3.66 | 3825.1366 | 1618.249 | 14000 | 3.2 | 4375 | 1975.3206
|  |  | 100 | mid | 11200 | 5.61 | 1996.4349 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.89 | 2290.3885 | 1 | 11200 | 4.48 | 2500 | 1 | 11200 | 3.94 | 2842.6396 | 1 | 11200 | 3.38 | 3313.6095 | 1
|  |  | 1127.3022 | min | 5760 | 5.73 | 1005.2356 | 0 | 5400 | 4.72 | 1144.0678 | 0 | 4960 | 4.19 | 1183.7709 | 0.018065 | 4520 | 3.63 | 1245.1791 | 0.082744 | 4200 | 3.02 | 1390.7285 | 0.12468 | 3880 | 2.41 | 1609.9585 | 0.16294
| 11 |  | 4.7205 | max | 17040 | 5.14 | 3315.1751 | 5.44 | 16760 | 4.77 | 3513.6268 | 4.81 | 16560 | 4.32 | 3833.3333 | 4.42 | 16340 | 4.02 | 4064.6766 | 3.99 | 15560 | 3.54 | 4395.4802 | 3.36 | 14760 | 3.06 | 4823.5294 | 2.7552
|  | 4650 | 36.148 | nom | 14000 | 5.38 | 2602.2305 | 854.7794 | 14000 | 5.01 | 2794.4112 | 966.736 | 14000 | 4.64 | 3017.2414 | 1052.0362 | 14000 | 4.26 | 3286.385 | 1165.4135 | 14000 | 3.83 | 3655.3525 | 1383.9286 | 14000 | 3.35 | 4179.1045 | 1687.7406
|  |  | 81.5279 | mid | 11200 | 5.73 | 1954.6248 | 0 | 11200 | 5.4 | 2074.0741 | 0 | 11200 | 5.07 | 2209.073 | 0 | 11200 | 4.69 | 2388.0597 | 0 | 11200 | 4.12 | 2718.4466 | 0 | 11200 | 3.54 | 3163.8418 | 1
|  |  | 985.074 | min | 6180 | 5.44 | 1136.0294 | 0 | 5800 | 4.81 | 1205.8212 | 0 | 5380 | 4.42 | 1217.1946 | 0 | 4960 | 3.99 | 1243.1078 | 0 | 4700 | 3.36 | 1398.8095 | 0 | 4440 | 2.73 | 1626.3736 | 0.031065
| 12 |  | 4.8926 | max | 17100 | 5.25 | 3257.1429 | 5.15 | 16800 | 4.9 | 3428.5714 | 4.9 | 16600 | 4.45 | 3730.3371 | 4.65 | 16400 | 4.2 | 3904.7619 | 4.35 | 15600 | 3.7 | 4216.2162 | 3.7 | 14800 | 3.2 | 4625 | 3.05
|  | 4227.2727 | 35.1478 | nom | 14000 | 5.5 | 2545.4545 | 820.8297 | 14000 | 5.15 | 2718.4466 | 862.7087 | 14000 | 4.8 | 2916.6667 | 909.0909 | 14000 | 4.45 | 3146.0674 | 971.7868 | 14000 | 4 | 3500 | 1142.5061 | 14000 | 3.5 | 4000 | 1385.9911
|  |  | 68.3121 | mid | 11200 | 5.85 | 1914.5299 | 0 | 11200 | 5.55 | 2018.018 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.9 | 2285.7143 | 0 | 11200 | 4.3 | 2604.6512 | 0 | 11200 | 3.7 | 3027.027 | 0
|  |  | 864.012 | min | 6600 | 5.15 | 1281.5534 | 0 | 6200 | 4.9 | 1265.3061 | 0 | 5800 | 4.65 | 1247.3118 | 0 | 5400 | 4.35 | 1241.3793 | 0 | 5200 | 3.7 | 1405.4054 | 0 | 5000 | 3.05 | 1639.3443 | 0
| 13 |  | 4.9827 | max | 17566.6667 | 5.2833 | 3324.9211 | 5.15 | 17266.6667 | 4.9333 | 3500 | 4.9667 | 17033.3333 | 4.55 | 3743.5897 | 4.7833 | 16833.3333 | 4.3 | 3914.7287 | 4.55 | 16033.3333 | 3.8 | 4219.2982 | 3.9167 | 15200 | 3.3 | 4606.0606 | 3.2667
|  | 3804.5455 | 34.1243 | nom | 14000 | 5.5 | 2545.4545 | 738.7467 | 14000 | 5.1833 | 2700.9646 | 766.0159 | 14000 | 4.8667 | 2876.7123 | 795.3754 | 14000 | 4.55 | 3076.9231 | 836.1638 | 14000 | 4.1 | 3414.6341 | 971.3733 | 14000 | 3.6167 | 3870.9677 | 1164.6568
|  |  | 60.3454 | mid | 11200 | 5.9 | 1898.3051 | 0 | 11200 | 5.5833 | 2005.9701 | 0 | 11200 | 5.3167 | 2106.5831 | 0 | 11200 | 5.0167 | 2232.5581 | 0 | 11200 | 4.4167 | 2535.8491 | 0 | 11200 | 3.8167 | 2934.4978 | 0
|  |  | 763.5477 | min | 6700 | 5.15 | 1300.9709 | 0 | 6266.6667 | 4.9667 | 1261.745 | 0 | 5833.3333 | 4.7833 | 1219.5122 | 0 | 5400 | 4.55 | 1186.8132 | 0 | 5233.3333 | 3.9167 | 1336.1702 | 0 | 5066.6667 | 3.2667 | 1551.0204 | 0
| 14 |  | 5.0558 | max | 18033.3333 | 5.3167 | 3391.8495 | 5.15 | 17733.3333 | 4.9667 | 3570.4698 | 5.0333 | 17466.6667 | 4.65 | 3756.2724 | 4.9167 | 17266.6667 | 4.4 | 3924.2424 | 4.75 | 16466.6667 | 3.9 | 4222.2222 | 4.1333 | 15600 | 3.4 | 4588.2353 | 3.4833
|  | 3381.8182 | 33.0741 | nom | 14000 | 5.5 | 2545.4545 | 656.6637 | 14000 | 5.2167 | 2683.7061 | 671.8844 | 14000 | 4.9333 | 2837.8378 | 687.8274 | 14000 | 4.65 | 3010.7527 | 711.9617 | 14000 | 4.2 | 3333.3333 | 818.1818 | 14000 | 3.7333 | 3750 | 970.8569
|  |  | 52.65 | mid | 11200 | 5.95 | 1882.3529 | 0 | 11200 | 5.6167 | 1994.0653 | 0 | 11200 | 5.3833 | 2080.4954 | 0 | 11200 | 5.1333 | 2181.8182 | 0 | 11200 | 4.5333 | 2470.5882 | 0 | 11200 | 3.9333 | 2847.4576 | 0
|  |  | 668.8984 | min | 6800 | 5.15 | 1320.3883 | 0 | 6333.3333 | 5.0333 | 1258.2781 | 0 | 5866.6667 | 4.9167 | 1193.2203 | 0 | 5400 | 4.75 | 1136.8421 | 0 | 5266.6667 | 4.1333 | 1274.1935 | 0 | 5133.3333 | 3.4833 | 1473.6842 | 0
| 15 |  | 5.115 | max | 18500 | 5.35 | 3457.9439 | 5.15 | 18200 | 5 | 3640 | 5.1 | 17900 | 4.75 | 3768.4211 | 5.05 | 17700 | 4.5 | 3933.3333 | 4.95 | 16900 | 4 | 4225 | 4.35 | 16000 | 3.5 | 4571.4286 | 3.7
|  | 2959.0909 | 31.9931 | nom | 14000 | 5.5 | 2545.4545 | 574.5808 | 14000 | 5.25 | 2666.6667 | 580.2139 | 14000 | 5 | 2800 | 585.9586 | 14000 | 4.75 | 2947.3684 | 597.7961 | 14000 | 4.3 | 3255.814 | 680.2508 | 14000 | 3.85 | 3636.3636 | 799.7543
|  |  | 45.1746 | mid | 11200 | 6 | 1866.6667 | 0 | 11200 | 5.65 | 1982.3009 | 0 | 11200 | 5.45 | 2055.0459 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.65 | 2408.6022 | 0 | 11200 | 4.05 | 2765.4321 | 0
|  |  | 578.5085 | min | 6900 | 5.15 | 1339.8058 | 0 | 6400 | 5.1 | 1254.902 | 0 | 5900 | 5.05 | 1168.3168 | 0 | 5400 | 4.95 | 1090.9091 | 0 | 5300 | 4.35 | 1218.3908 | 0 | 5200 | 3.7 | 1405.4054 | 0
| 16 |  | 6.1914 | max | 19020 | 5.73 | 3319.3717 | 6.92 | 18720 | 5.3 | 3532.0755 | 5.68 | 18420 | 4.95 | 3721.2121 | 5.37 | 18200 | 4.59 | 3965.1416 | 5.02 | 17380 | 4.08 | 4259.8039 | 4.36 | 16460 | 3.56 | 4623.5955 | 3.65
|  | 2536.3636 | 30.8757 | nom | 14000 | 5.93 | 2360.8769 | 366.5265 | 14000 | 5.57 | 2513.465 | 446.5429 | 14000 | 5.21 | 2687.1401 | 472.321 | 14000 | 4.85 | 2886.5979 | 505.2517 | 14000 | 4.39 | 3189.0661 | 581.7348 | 14000 | 3.92 | 3571.4286 | 694.8941
|  |  | 38.001 | mid | 11200 | 6.42 | 1744.5483 | 0 | 11200 | 5.99 | 1869.783 | 0 | 11200 | 5.68 | 1971.831 | 0 | 11200 | 5.36 | 2089.5522 | 0 | 11200 | 4.74 | 2362.8692 | 0 | 11200 | 4.12 | 2718.4466 | 0
|  |  | 409.658 | min | 6980 | 6.92 | 1008.6705 | 0 | 6460 | 5.68 | 1137.3239 | 0 | 6000 | 5.37 | 1117.3184 | 0 | 5520 | 5.02 | 1099.6016 | 0 | 5360 | 4.36 | 1229.3578 | 0 | 5180 | 3.65 | 1419.1781 | 0
| 17 |  | 7.5444 | max | 19540 | 6.11 | 3198.036 | 8.69 | 19240 | 5.6 | 3435.7143 | 6.26 | 18940 | 5.15 | 3677.6699 | 5.69 | 18700 | 4.68 | 3995.7265 | 5.09 | 17860 | 4.16 | 4293.2692 | 4.37 | 16920 | 3.62 | 4674.0331 | 3.6
|  | 2113.6364 | 29.7142 | nom | 14000 | 6.36 | 2201.2579 | 243.2263 | 14000 | 5.89 | 2376.91 | 337.6416 | 14000 | 5.42 | 2583.0258 | 371.4651 | 14000 | 4.95 | 2828.2828 | 415.2527 | 14000 | 4.48 | 3125 | 483.6696 | 14000 | 3.99 | 3508.7719 | 587.1212
|  |  | 31.0581 | mid | 11200 | 6.84 | 1637.4269 | 0 | 11200 | 6.33 | 1769.3523 | 0 | 11200 | 5.91 | 1895.0931 | 0 | 11200 | 5.47 | 2047.532 | 0 | 11200 | 4.83 | 2318.8406 | 0 | 11200 | 4.19 | 2673.031 | 0
|  |  | 280.158 | min | 7060 | 8.69 | 812.4281 | 0 | 6520 | 6.26 | 1041.5335 | 0 | 6100 | 5.69 | 1072.0562 | 0 | 5640 | 5.09 | 1108.055 | 0 | 5420 | 4.37 | 1240.2746 | 0 | 5160 | 3.6 | 1433.3333 | 0
| 18 |  | 9.1939 | max | 20060 | 6.49 | 3090.9091 | 10.46 | 19760 | 5.9 | 3349.1525 | 6.84 | 19460 | 5.35 | 3637.3832 | 6.01 | 19200 | 4.77 | 4025.1572 | 5.16 | 18340 | 4.24 | 4325.4717 | 4.38 | 17380 | 3.68 | 4722.8261 | 3.55
|  | 1690.9091 | 28.4975 | nom | 14000 | 6.79 | 2061.8557 | 161.6548 | 14000 | 6.21 | 2254.4283 | 247.2089 | 14000 | 5.63 | 2486.6785 | 281.3493 | 14000 | 5.05 | 2772.2772 | 327.6956 | 14000 | 4.57 | 3063.4573 | 386.0523 | 14000 | 4.06 | 3448.2759 | 476.3124
|  |  | 24.3502 | mid | 11200 | 7.26 | 1542.6997 | 0 | 11200 | 6.67 | 1679.1604 | 0 | 11200 | 6.14 | 1824.1042 | 0 | 11200 | 5.58 | 2007.1685 | 0 | 11200 | 4.92 | 2276.4228 | 0 | 11200 | 4.26 | 2629.108 | 0
|  |  | 183.9163 | min | 7140 | 10.46 | 682.6004 | 0 | 6580 | 6.84 | 961.9883 | 0 | 6200 | 6.01 | 1031.614 | 0 | 5760 | 5.16 | 1116.2791 | 0 | 5480 | 4.38 | 1251.1416 | 0 | 5140 | 3.55 | 1447.8873 | 0
| 19 |  | 11.1681 | max | 20580 | 6.87 | 2995.6332 | 12.23 | 20280 | 6.2 | 3270.9677 | 7.42 | 19980 | 5.55 | 3600 | 6.33 | 19700 | 4.86 | 4053.4979 | 5.23 | 18820 | 4.32 | 4356.4815 | 4.39 | 17840 | 3.74 | 4770.0535 | 3.5
|  | 1268.1818 | 27.2076 | nom | 14000 | 7.22 | 1939.0582 | 103.6943 | 14000 | 6.53 | 2143.951 | 170.914 | 14000 | 5.84 | 2397.2603 | 200.3447 | 14000 | 5.15 | 2718.4466 | 242.4822 | 14000 | 4.66 | 3004.2918 | 288.8797 | 14000 | 4.13 | 3389.8305 | 362.3377
|  |  | 17.882 | mid | 11200 | 7.68 | 1458.3333 | 0 | 11200 | 7.01 | 1597.7175 | 0 | 11200 | 6.37 | 1758.2418 | 0 | 11200 | 5.69 | 1968.3656 | 0 | 11200 | 5.01 | 2235.5289 | 0 | 11200 | 4.33 | 2586.6051 | 0
|  |  | 113.5536 | min | 7220 | 12.23 | 590.3516 | 0 | 6640 | 7.42 | 894.8787 | 0 | 6300 | 6.33 | 995.2607 | 0 | 5880 | 5.23 | 1124.283 | 0 | 5540 | 4.39 | 1261.959 | 0 | 5120 | 3.5 | 1462.8571 | 0
| 20 |  | 13.5126 | max | 21100 | 7.25 | 2910.3448 | 14 | 20800 | 6.5 | 3200 | 8 | 20500 | 5.75 | 3565.2174 | 6.65 | 20200 | 4.95 | 4080.8081 | 5.3 | 19300 | 4.4 | 4386.3636 | 4.4 | 18300 | 3.8 | 4815.7895 | 3.45
|  | 845.4545 | 25.8123 | nom | 14000 | 7.65 | 1830.0654 | 60.3896 | 14000 | 6.85 | 2043.7956 | 105.6818 | 14000 | 6.05 | 2314.0496 | 127.136 | 14000 | 5.25 | 2666.6667 | 159.5197 | 14000 | 4.75 | 2947.3684 | 192.1488 | 14000 | 4.2 | 3333.3333 | 245.0593
|  |  | 11.6594 | mid | 11200 | 8.1 | 1382.716 | 0 | 11200 | 7.35 | 1523.8095 | 0 | 11200 | 6.6 | 1696.9697 | 0 | 11200 | 5.8 | 1931.0345 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.4 | 2545.4545 | 0
|  |  | 62.5677 | min | 7300 | 14 | 521.4286 | 0 | 6700 | 8 | 837.5 | 0 | 6400 | 6.65 | 962.406 | 0 | 6000 | 5.3 | 1132.0755 | 0 | 5600 | 4.4 | 1272.7273 | 0 | 5100 | 3.45 | 1478.2609 | 0
Indoor Temp. |  | 23
LWT |  |  | 25 CAP: 25; 35 CAP: 35; 40 CAP: 40; 45 CAP: 45; 50 CAP: 50; 55 CAP: 55
Outdoor air temperature[℃] |  | Heating Demand | COP | CL | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP
|  |  | LWT |  |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI
| -15 |  | -0.10578 | max | - | - | - | - | 14000 | 1.85 | 7567.5676 | 1.5405 | 13500 | 1.7 | 7941.1765 | 1.2898 | 13100 | 1.55 | 8451.6129 | 1.0561 | 12600 | 1.45 | 8689.6552 | 0.80057 | 12200 | 1.3 | 9384.6154 | 0.33409
|  | 16063.6364 | 59.7148 | nom | - | - | - | - | 11000 | 2.3 | 4782.6087 | 10427.8548 | 11000 | 2.1 | 5238.0952 | 12454.1866 | 11000 | 1.9 | 5789.4737 | 15210.9039 | 11000 | 1.75 | 6285.7143 | 20065.2945 | 11000 | 1.6 | 6875 | 48081.6327
|  |  | 100 | mid | - | - | - | - | 8800 | 2.5 | 3520 | 3 | 8800 | 2.3 | 3826.087 | 3 | 8800 | 2.1 | 4190.4762 | 3 | 8800 | 1.9 | 4631.5789 | 3 | 8800 | 1.7 | 5176.4706 | 3
|  |  | -151860.1008 | min | - | - | - | - | 7800 | 2.35 | 3319.1489 | 1.6879 | 7200 | 2 | 3600 | 2.0255 | 6500 | 1.6 | 4062.5 | 2.4113 | 5700 | 1.3 | 4384.6154 | 3.1648 | 4800 | 1 | 4800 | 4.2197
| -14 |  | 1.7303 | max | 14280 | 2.08 | 6865.3846 | -0.64182 | 14080 | 1.93 | 7295.3368 | -6.0697 | 13640 | 1.78 | 7662.9213 | 3.6697 | 13280 | 1.62 | 8197.5309 | 2.5381 | 12880 | 1.53 | 8418.3007 | 2.1216 | 12560 | 1.39 | 9035.9712 | 1.9035
|  | 15640.9091 | 58.9693 | nom | 14000 | 2.64 | 5303.0303 | -24369.6884 | 14000 | 2.34 | 5982.906 | -2576.9008 | 14000 | 2.12 | 6603.7736 | 4262.1214 | 14000 | 1.9 | 7368.4211 | 6162.3719 | 14000 | 1.77 | 7909.6045 | 7372.1421 | 14000 | 1.63 | 8588.9571 | 8216.9864
|  |  | 100 | mid | 11200 | 2.69 | 4163.5688 | 3 | 11200 | 2.54 | 4409.4488 | 3 | 11200 | 2.35 | 4765.9574 | 3 | 11200 | 2.15 | 5209.3023 | 3 | 11200 | 1.94 | 5773.1959 | 3 | 11200 | 1.73 | 6473.9884 | 3
|  |  | 9039.3529 | min | 7720 | 2.59 | 2980.695 | 5.8604 | 7420 | 2.34 | 3170.9402 | 20.5114 | 6880 | 2.01 | 3422.8856 | -4.5581 | 6260 | 1.63 | 3840.4908 | -2.279 | 5480 | 1.33 | 4120.3008 | -1.4651 | 4640 | 1.02 | 4549.0196 | -1.1395
| -13 |  | 1.742 | max | 14360 | 2.16 | 6648.1481 | 0.9204 | 14160 | 2.01 | 7044.7761 | -0.43705 | 13780 | 1.86 | 7408.6022 | 3.6904 | 13460 | 1.69 | 7964.497 | 2.3737 | 13160 | 1.61 | 8173.913 | 2.051 | 12920 | 1.48 | 8729.7297 | 1.863
|  | 15218.1818 | 58.2192 | nom | 14000 | 2.68 | 5223.8806 | 16534.2406 | 14000 | 2.38 | 5882.3529 | -34820.5928 | 14000 | 2.14 | 6542.0561 | 4123.7067 | 14000 | 1.9 | 7368.4211 | 6411.0638 | 14000 | 1.79 | 7821.2291 | 7419.7429 | 14000 | 1.66 | 8433.7349 | 8168.5101
|  |  | 100 | mid | 11200 | 2.73 | 4102.5641 | 3 | 11200 | 2.58 | 4341.0853 | 3 | 11200 | 2.4 | 4666.6667 | 3 | 11200 | 2.2 | 5090.9091 | 3 | 11200 | 1.98 | 5656.5657 | 3 | 11200 | 1.76 | 6363.6364 | 3
|  |  | 8736.1169 | min | 7340 | 2.58 | 2844.9612 | 3.3838 | 7040 | 2.33 | 3021.4592 | 7.6136 | 6560 | 2.02 | 3247.5248 | -5.5372 | 6020 | 1.66 | 3626.506 | -2.2559 | 5260 | 1.36 | 3867.6471 | -1.4502 | 4480 | 1.04 | 4307.6923 | -1.1279
| -12 |  | 1.7448 | max | 14440 | 2.24 | 6446.4286 | 1.8522 | 14240 | 2.09 | 6813.3971 | 1.3263 | 13920 | 1.94 | 7175.2577 | 4.3475 | 13640 | 1.76 | 7750 | 2.2093 | 13440 | 1.69 | 7952.6627 | 1.9805 | 13280 | 1.57 | 8458.5987 | 1.8226
|  | 14795.4545 | 57.4642 | nom | 14000 | 2.72 | 5147.0588 | 7987.9083 | 14000 | 2.42 | 5785.124 | 11155.8564 | 14000 | 2.16 | 6481.4815 | 3403.2098 | 14000 | 1.9 | 7368.4211 | 6696.7653 | 14000 | 1.81 | 7734.8066 | 7470.7367 | 14000 | 1.69 | 8284.0237 | 8117.8818
|  |  | 100 | mid | 11200 | 2.77 | 4043.3213 | 3 | 11200 | 2.62 | 4274.8092 | 3 | 11200 | 2.45 | 4571.4286 | 3 | 11200 | 2.25 | 4977.7778 | 3 | 11200 | 2.02 | 5544.5545 | 3 | 11200 | 1.79 | 6256.9832 | 3
|  |  | 8479.8984 | min | 6960 | 2.57 | 2708.1712 | 1.8079 | 6660 | 2.32 | 2870.6897 | 3.3144 | 6240 | 2.03 | 3073.8916 | -9.9432 | 5780 | 1.69 | 3420.1183 | -2.2096 | 5040 | 1.39 | 3625.8993 | -1.4205 | 4320 | 1.06 | 4075.4717 | -1.1048
| -11 |  | 1.7386 | max | 14520 | 2.32 | 6258.6207 | 2.4446 | 14320 | 2.17 | 6599.0783 | 2.1222 | 14060 | 2.02 | 6960.396 | 1.1861 | 13820 | 1.83 | 7551.9126 | 2.0449 | 13720 | 1.77 | 7751.4124 | 1.9099 | 13640 | 1.66 | 8216.8675 | 1.7821
|  | 14372.7273 | 56.7042 | nom | 14000 | 2.76 | 5072.4638 | 5879.3409 | 14000 | 2.46 | 5691.0569 | 6772.5094 | 14000 | 2.18 | 6422.0183 | 12118.0378 | 14000 | 1.9 | 7368.4211 | 7028.4021 | 14000 | 1.83 | 7650.2732 | 7525.4998 | 14000 | 1.72 | 8139.5349 | 8064.9549
|  |  | 100 | mid | 11200 | 2.81 | 3985.7651 | 3 | 11200 | 2.66 | 4210.5263 | 3 | 11200 | 2.5 | 4480 | 3 | 11200 | 2.3 | 4869.5652 | 3 | 11200 | 2.06 | 5436.8932 | 3 | 11200 | 1.82 | 6153.8462 | 3
|  |  | 8266.9361 | min | 6580 | 2.56 | 2570.3125 | 0.71678 | 6280 | 2.31 | 2718.6147 | 1.1648 | 5920 | 2.04 | 2901.9608 | 6.2121 | 5540 | 1.72 | 3220.9302 | -2.0707 | 4820 | 1.42 | 3394.3662 | -1.3312 | 4160 | 1.08 | 3851.8519 | -1.0354
| -10 |  | 1.7325 | max | 14600 | 2.4 | 6083.3333 | 2.8009 | 14400 | 2.25 | 6400 | 2.5036 | 14200 | 2.1 | 6761.9048 | 2.2063 | 14000 | 1.9 | 7368.4211 | 1.908 | 14000 | 1.85 | 7567.5676 | 1.8545 | 14000 | 1.75 | 8000 | 1.7518
|  | 13950 | 55.939 | nom | 14000 | 2.8 | 5000 | 4980.5547 | 14000 | 2.5 | 5600 | 5572.0399 | 14000 | 2.2 | 6363.6364 | 6322.9462 | 14000 | 1.9 | 7368.4211 | 7311.1839 | 14000 | 1.85 | 7567.5676 | 7522.3881 | 14000 | 1.75 | 8000 | 7963.3028
|  |  | 100 | mid | 11200 | 2.85 | 3929.8246 | 2 | 11200 | 2.7 | 4148.1481 | 2 | 11200 | 2.55 | 4392.1569 | 2 | 11200 | 2.35 | 4765.9574 | 2 | 11200 | 2.1 | 5333.3333 | 2 | 11200 | 1.85 | 6054.0541 | 2
|  |  | 8051.938 | min | 6200 | 2.55 | 2431.3725 | 0.98214 | 5900 | 2.3 | 2565.2174 | 0.98214 | 5600 | 2.05 | 2731.7073 | 0.98214 | 5300 | 1.75 | 3028.5714 | 0.98214 | 4600 | 1.45 | 3172.4138 | 0.98214 | 4000 | 1.1 | 3636.3636 | 0.98214
| -9 |  | 1.8313 | max | 15100 | 2.5 | 6040 | 2.9002 | 14900 | 2.3333 | 6385.7143 | 2.6338 | 14700 | 2.1667 | 6784.6154 | 2.3673 | 14500 | 1.9667 | 7372.8814 | 2.0952 | 14233.3333 | 1.9167 | 7426.087 | 1.9866 | 14000 | 1.8167 | 7706.422 | 1.8364
|  | 13527.2727 | 55.1685 | nom | 14000 | 2.8833 | 4855.4913 | 4664.2287 | 14000 | 2.6 | 5384.6154 | 5136.0947 | 14000 | 2.3167 | 6043.1655 | 5714.1812 | 14000 | 2.0333 | 6885.2459 | 6456.1983 | 14000 | 1.95 | 7179.4872 | 6809.3267 | 14000 | 1.8167 | 7706.422 | 7366.3366
|  |  | 100 | mid | 11200 | 2.9833 | 3754.1899 | 2 | 11200 | 2.8 | 4000 | 2 | 11200 | 2.6167 | 4280.2548 | 2 | 11200 | 2.4 | 4666.6667 | 2 | 11200 | 2.1667 | 5169.2308 | 2 | 11200 | 1.9333 | 5793.1034 | 2
|  |  | 7386.6992 | min | 5833.3333 | 2.9167 | 2000 | 0.83117 | 5266.6667 | 2.2833 | 2306.5693 | 0.83117 | 5066.6667 | 2.05 | 2471.5447 | 0.83117 | 4866.6667 | 1.7833 | 2728.972 | 0.83117 | 4266.6667 | 1.4667 | 2909.0909 | 0.83117 | 3700 | 1.1167 | 3313.4328 | 0.83117
| -8 |  | 1.9482 | max | 15600 | 2.6 | 6000 | 3.0146 | 15400 | 2.4167 | 6372.4138 | 2.764 | 15200 | 2.2333 | 6805.9701 | 2.5133 | 15000 | 2.0333 | 7377.0492 | 2.2573 | 14466.6667 | 1.9833 | 7294.1176 | 2.1086 | 14000 | 1.8833 | 7433.6283 | 1.926
|  | 13104.5455 | 54.3924 | nom | 14000 | 2.9667 | 4719.1011 | 4346.9723 | 14000 | 2.7 | 5185.1852 | 4741.2193 | 14000 | 2.4333 | 5753.4247 | 5214.1112 | 14000 | 2.1667 | 6461.5385 | 5805.4633 | 14000 | 2.05 | 6829.2683 | 6214.7174 | 14000 | 1.8833 | 7433.6283 | 6804.1133
|  |  | 100 | mid | 11200 | 3.1167 | 3593.5829 | 2 | 11200 | 2.9 | 3862.069 | 2 | 11200 | 2.6833 | 4173.913 | 2 | 11200 | 2.45 | 4571.4286 | 2 | 11200 | 2.2333 | 5014.9254 | 2 | 11200 | 2.0167 | 5553.719 | 2
|  |  | 6726.5896 | min | 5466.6667 | 3.2833 | 1664.9746 | 0.68019 | 4633.3333 | 2.2667 | 2044.1176 | 0.68019 | 4533.3333 | 2.05 | 2211.3821 | 0.68019 | 4433.3333 | 1.8167 | 2440.367 | 0.68019 | 3933.3333 | 1.4833 | 2651.6854 | 0.68019 | 3400 | 1.1333 | 3000 | 0.68019
| -7 |  | 2.0762 | max | 16100 | 2.7 | 5962.963 | 3.1442 | 15900 | 2.5 | 6360 | 2.8942 | 15700 | 2.3 | 6826.087 | 2.6442 | 15500 | 2.1 | 7380.9524 | 2.3942 | 14700 | 2.05 | 7170.7317 | 2.2206 | 14000 | 1.95 | 7179.4872 | 2.0206
|  | 12681.8182 | 53.6105 | nom | 14000 | 3.05 | 4590.1639 | 4033.4572 | 14000 | 2.8 | 5000 | 4381.8712 | 14000 | 2.55 | 5490.1961 | 4796.169 | 14000 | 2.3 | 6086.9565 | 5296.9894 | 14000 | 2.15 | 6511.6279 | 5710.9438 | 14000 | 1.95 | 7179.4872 | 6276.2111
|  |  | 100 | mid | 11200 | 3.25 | 3446.1538 | 2 | 11200 | 3 | 3733.3333 | 2 | 11200 | 2.75 | 4072.7273 | 2 | 11200 | 2.5 | 4480 | 2 | 11200 | 2.3 | 4869.5652 | 2 | 11200 | 2.1 | 5333.3333 | 2
|  |  | 6108.1946 | min | 5100 | 3.65 | 1397.2603 | 0.52922 | 4000 | 2.25 | 1777.7778 | 0.52922 | 4000 | 2.05 | 1951.2195 | 0.52922 | 4000 | 1.85 | 2162.1622 | 0.52922 | 3600 | 1.5 | 2400 | 0.52922 | 3100 | 1.15 | 2695.6522 | 0.52922
| -6 |  | 2.1794 | max | 16144.4444 | 2.7611 | 5847.0825 | 3.2167 | 15944.4444 | 2.5556 | 6239.1304 | 2.9667 | 15733.3333 | 2.35 | 6695.0355 | 2.7167 | 15533.3333 | 2.1444 | 7243.5233 | 2.4667 | 14744.4444 | 2.0944 | 7039.7878 | 2.2912 | 14033.3333 | 1.9944 | 7036.2117 | 2.0933
|  | 12259.0909 | 52.8225 | nom | 14000 | 3.0889 | 4532.3741 | 3811.0843 | 14000 | 2.8389 | 4931.5068 | 4132.2401 | 14000 | 2.5889 | 5407.7253 | 4512.5039 | 14000 | 2.3389 | 5985.7482 | 4969.8472 | 14000 | 2.1944 | 6379.7468 | 5350.6007 | 14000 | 2 | 7000 | 5856.4504
|  |  | 100 | mid | 11200 | 3.2944 | 3399.6627 | 2 | 11200 | 3.0444 | 3678.8321 | 2 | 11200 | 2.7944 | 4007.9523 | 2 | 11200 | 2.5444 | 4401.7467 | 2 | 11200 | 2.35 | 4765.9574 | 2 | 11200 | 2.15 | 5209.3023 | 2
|  |  | 5624.865 | min | 5155.5556 | 3.7111 | 1389.2216 | 0.37825 | 4122.2222 | 2.4056 | 1713.6259 | 0.37825 | 4077.7778 | 2.1667 | 1882.0513 | 0.37825 | 4022.2222 | 1.9222 | 2092.4855 | 0.37825 | 3611.1111 | 1.5611 | 2313.1673 | 0.37825 | 3111.1111 | 1.1944 | 2604.6512 | 0.37825
| -5 |  | 2.2833 | max | 16188.8889 | 2.8222 | 5736.2205 | 3.2909 | 15988.8889 | 2.6111 | 6123.4043 | 3.0409 | 15766.6667 | 2.4 | 6569.4444 | 2.7909 | 15566.6667 | 2.1889 | 7111.6751 | 2.5409 | 14788.8889 | 2.1389 | 6914.2857 | 2.3634 | 14066.6667 | 2.0389 | 6899.1826 | 2.1659
|  | 11836.3636 | 52.0283 | nom | 14000 | 3.1278 | 4476.0213 | 3596.6851 | 14000 | 2.8778 | 4864.8649 | 3892.3767 | 14000 | 2.6278 | 5327.6956 | 4241.0423 | 14000 | 2.3778 | 5887.8505 | 4658.3184 | 14000 | 2.2389 | 6253.1017 | 5008.2274 | 14000 | 2.05 | 6829.2683 | 5464.8478
|  |  | 100 | mid | 11200 | 3.3389 | 3354.4093 | 2 | 11200 | 3.0889 | 3625.8993 | 2 | 11200 | 2.8389 | 3945.2055 | 2 | 11200 | 2.5889 | 4326.1803 | 2 | 11200 | 2.4 | 4666.6667 | 2 | 11200 | 2.2 | 5090.9091 | 2
|  |  | 5183.9384 | min | 5211.1111 | 3.7722 | 1381.4433 | 0.22727 | 4244.4444 | 2.5611 | 1657.2668 | 0.22727 | 4155.5556 | 2.2833 | 1819.9513 | 0.22727 | 4044.4444 | 1.9944 | 2027.8552 | 0.22727 | 3622.2222 | 1.6222 | 2232.8767 | 0.22727 | 3122.2222 | 1.2389 | 2520.1794 | 0.22727
| -4 |  | 2.3885 | max | 16233.3333 | 2.8833 | 5630.0578 | 3.3668 | 16033.3333 | 2.6667 | 6012.5 | 3.1168 | 15800 | 2.45 | 6448.9796 | 2.8668 | 15600 | 2.2333 | 6985.0746 | 2.6168 | 14833.3333 | 2.1833 | 6793.8931 | 2.4373 | 14100 | 2.0833 | 6768 | 2.2386
|  | 11413.6364 | 51.2275 | nom | 14000 | 3.1667 | 4421.0526 | 3390.0528 | 14000 | 2.9167 | 4800 | 3661.9704 | 14000 | 2.6667 | 5250 | 3981.3132 | 14000 | 2.4167 | 5793.1034 | 4361.6737 | 14000 | 2.2833 | 6131.3869 | 4682.9333 | 14000 | 2.1 | 6666.6667 | 5098.662
|  |  | 100 | mid | 11200 | 3.3833 | 3310.3448 | 2 | 11200 | 3.1333 | 3574.4681 | 2 | 11200 | 2.8833 | 3884.3931 | 2 | 11200 | 2.6333 | 4253.1646 | 2 | 11200 | 2.45 | 4571.4286 | 2 | 11200 | 2.25 | 4977.7778 | 2
|  |  | 4778.5863 | min | 5266.6667 | 3.8333 | 1373.913 | 0.076299 | 4366.6667 | 2.7167 | 1607.362 | 0.076299 | 4233.3333 | 2.4 | 1763.8889 | 0.076299 | 4066.6667 | 2.0667 | 1967.7419 | 0.076299 | 3633.3333 | 1.6833 | 2158.4158 | 0.076299 | 3133.3333 | 1.2833 | 2441.5584 | 0.076299
| -3 |  | 2.4619 | max | 16277.7778 | 2.9444 | 5528.3019 | 3.4444 | 16077.7778 | 2.7222 | 5906.1224 | 3.1683 | 15833.3333 | 2.5 | 6333.3333 | 2.9153 | 15633.3333 | 2.2778 | 6863.4146 | 2.6619 | 14877.7778 | 2.2278 | 6678.3042 | 2.4791 | 14133.3333 | 2.1278 | 6642.2977 | 2.2748
|  | 10990.9091 | 50.4198 | nom | 14000 | 3.2056 | 4367.4177 | 3190.9701 | 14000 | 2.9556 | 4736.8421 | 3469.0702 | 14000 | 2.7056 | 5174.538 | 3770.0785 | 14000 | 2.4556 | 5701.3575 | 4128.9209 | 14000 | 2.3278 | 6014.3198 | 4433.4433 | 14000 | 2.15 | 6511.6279 | 4831.6682
|  |  | 100 | mid | 11200 | 3.4278 | 3267.423 | 1 | 11200 | 3.1778 | 3524.4755 | 1 | 11200 | 2.9278 | 3825.4269 | 1 | 11200 | 2.6778 | 4182.5726 | 1 | 11200 | 2.5 | 4480 | 1 | 11200 | 2.3 | 4869.5652 | 1
|  |  | 4464.3357 | min | 5322.2222 | 3.8944 | 1366.6191 | 0.96443 | 4488.8889 | 2.8722 | 1562.8627 | 0.96884 | 4311.1111 | 2.5167 | 1713.0243 | 0.96965 | 4088.8889 | 2.1389 | 1911.6883 | 0.9706 | 3644.4444 | 1.7444 | 2089.172 | 0.97233 | 3144.4444 | 1.3278 | 2368.2008 | 0.97404
| -2 |  | 2.5026 | max | 16322.2222 | 3.0056 | 5430.6839 | 3.5247 | 16122.2222 | 2.7778 | 5804 | 3.2036 | 15866.6667 | 2.55 | 6222.2222 | 2.9408 | 15666.6667 | 2.3222 | 6746.4115 | 2.6767 | 14922.2222 | 2.2722 | 6567.2372 | 2.4877 | 14166.6667 | 2.1722 | 6521.7391 | 2.2732
|  | 10568.1818 | 49.6049 | nom | 14000 | 3.2444 | 4315.0685 | 2998.3441 | 14000 | 2.9944 | 4675.3247 | 3298.8697 | 14000 | 2.7444 | 5101.2146 | 3593.659 | 14000 | 2.4944 | 5612.4722 | 3948.2603 | 14000 | 2.3722 | 5901.6393 | 4248.2495 | 14000 | 2.2 | 6363.6364 | 4649.024
|  |  | 100 | mid | 11200 | 3.4722 | 3225.6 | 1 | 11200 | 3.2222 | 3475.8621 | 1 | 11200 | 2.9722 | 3768.2243 | 1 | 11200 | 2.7222 | 4114.2857 | 1 | 11200 | 2.55 | 4392.1569 | 1 | 11200 | 2.35 | 4765.9574 | 1
|  |  | 4222.8952 | min | 5377.7778 | 3.9556 | 1359.5506 | 0.89148 | 4611.1111 | 3.0278 | 1522.9358 | 0.90411 | 4388.8889 | 2.6333 | 1666.6667 | 0.90724 | 4111.1111 | 2.2111 | 1859.2965 | 0.91087 | 3655.5556 | 1.8056 | 2024.6154 | 0.91625 | 3155.5556 | 1.3722 | 2299.5951 | 0.92146
| -1 |  | 2.5454 | max | 16366.6667 | 3.0667 | 5336.9565 | 3.6081 | 16166.6667 | 2.8333 | 5705.8824 | 3.2531 | 15900 | 2.6 | 6115.3846 | 2.9749 | 15700 | 2.3667 | 6633.8028 | 2.6945 | 14966.6667 | 2.3167 | 6460.4317 | 2.4973 | 14200 | 2.2167 | 6406.015 | 2.2709
|  | 10145.4545 | 48.7824 | nom | 14000 | 3.2833 | 4263.9594 | 2811.8542 | 14000 | 3.0333 | 4615.3846 | 3118.7255 | 14000 | 2.7833 | 5029.9401 | 3410.3486 | 14000 | 2.5333 | 5526.3158 | 3765.1902 | 14000 | 2.4167 | 5793.1034 | 4062.496 | 14000 | 2.25 | 6222.2222 | 4467.5592
|  |  | 100 | mid | 11200 | 3.5167 | 3184.8341 | 1 | 11200 | 3.2667 | 3428.5714 | 1 | 11200 | 3.0167 | 3712.7072 | 1 | 11200 | 2.7667 | 4048.1928 | 1 | 11200 | 2.6 | 4307.6923 | 1 | 11200 | 2.4 | 4666.6667 | 1
|  |  | 3985.8556 | min | 5433.3333 | 4.0167 | 1352.6971 | 0.81713 | 4733.3333 | 3.1833 | 1486.911 | 0.83693 | 4466.6667 | 2.75 | 1624.2424 | 0.84338 | 4133.3333 | 2.2833 | 1810.219 | 0.85077 | 3666.6667 | 1.8667 | 1964.2857 | 0.86002 | 3166.6667 | 1.4167 | 2235.2941 | 0.86873
| 0 |  | 2.5931 | max | 16411.1111 | 3.1278 | 5246.8917 | 3.6948 | 16211.1111 | 2.8889 | 5611.5385 | 3.3176 | 15933.3333 | 2.65 | 6012.5786 | 3.018 | 15733.3333 | 2.4111 | 6525.3456 | 2.7156 | 15011.1111 | 2.3611 | 6357.6471 | 2.5082 | 14233.3333 | 2.2611 | 6294.8403 | 2.2679
|  | 9722.7273 | 47.952 | nom | 14000 | 3.3222 | 4214.0468 | 2631.4941 | 14000 | 3.0722 | 4556.962 | 2930.6694 | 14000 | 2.8222 | 4960.6299 | 3221.6308 | 14000 | 2.5722 | 5442.7646 | 3580.3532 | 14000 | 2.4611 | 5688.4876 | 3876.4315 | 14000 | 2.3 | 6086.9565 | 4287.1086
|  |  | 100 | mid | 11200 | 3.5611 | 3145.0858 | 1 | 11200 | 3.3111 | 3382.5503 | 1 | 11200 | 3.0611 | 3658.8022 | 1 | 11200 | 2.8111 | 3984.1897 | 1 | 11200 | 2.65 | 4226.4151 | 1 | 11200 | 2.45 | 4571.4286 | 1
|  |  | 3749.4332 | min | 5488.8889 | 4.0778 | 1346.049 | 0.74133 | 4855.5556 | 3.3389 | 1454.2429 | 0.76715 | 4544.4444 | 2.8667 | 1585.2713 | 0.77804 | 4155.5556 | 2.3556 | 1764.1509 | 0.79029 | 3677.7778 | 1.9278 | 1907.781 | 0.80361 | 3177.7778 | 1.4611 | 2174.9049 | 0.81585
| 1 |  | 2.647 | max | 16455.5556 | 3.1889 | 5160.2787 | 3.7847 | 16255.5556 | 2.9444 | 5520.7547 | 3.398 | 15966.6667 | 2.7 | 5913.5802 | 3.0703 | 15766.6667 | 2.4556 | 6420.8145 | 2.7398 | 15055.5556 | 2.4056 | 6258.6605 | 2.5201 | 14266.6667 | 2.3056 | 6187.9518 | 2.2641
|  | 9300 | 47.1133 | nom | 14000 | 3.3611 | 4165.2893 | 2457.2424 | 14000 | 3.1111 | 4500 | 2736.9312 | 14000 | 2.8611 | 4893.2039 | 3029.0678 | 14000 | 2.6111 | 5361.7021 | 3394.3936 | 14000 | 2.5056 | 5587.5831 | 3690.3029 | 14000 | 2.35 | 5957.4468 | 4107.5071
|  |  | 100 | mid | 11200 | 3.6056 | 3106.3174 | 1 | 11200 | 3.3556 | 3337.7483 | 1 | 11200 | 3.1056 | 3606.4401 | 1 | 11200 | 2.8556 | 3922.179 | 1 | 11200 | 2.7 | 4148.1481 | 1 | 11200 | 2.5 | 4480 | 1
|  |  | 3513.4672 | min | 5544.4444 | 4.1389 | 1339.5973 | 0.66405 | 4977.7778 | 3.4944 | 1424.4833 | 0.69464 | 4622.2222 | 2.9833 | 1549.3482 | 0.71115 | 4177.7778 | 2.4278 | 1720.8238 | 0.72943 | 3688.8889 | 1.9889 | 1854.7486 | 0.74704 | 3188.8889 | 1.5056 | 2118.0812 | 0.76283
14kW-Maximum heating CAP | 2 |  | 2.708 | max | 16500 | 3.25 | 5076.9231 | 3.8781 | 16300 | 3 | 5433.3333 | 3.4952 | 16000 | 2.75 | 5818.1818 | 3.1321 | 15800 | 2.5 | 6320 | 2.7673 | 15100 | 2.45 | 6163.2653 | 2.5332 | 14300 | 2.35 | 6085.1064 | 2.2597
|  | 8877.2727 | 46.2656 | nom | 14000 | 3.4 | 4117.6471 | 2289.0631 | 14000 | 3.15 | 4444.4444 | 2539.8514 | 14000 | 2.9 | 4827.5862 | 2834.258 | 14000 | 2.65 | 5283.0189 | 3207.9501 | 14000 | 2.55 | 5490.1961 | 3504.3543 | 14000 | 2.4 | 5833.3333 | 3928.5894
|  |  | 100 | mid | 11200 | 3.65 | 3068.4932 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 3.15 | 3555.5556 | 1 | 11200 | 2.9 | 3862.069 | 1 | 11200 | 2.75 | 4072.7273 | 1 | 11200 | 2.55 | 4392.1569 | 1
|  |  | 3278.1345 | min | 5600 | 4.2 | 1333.3333 | 0.58523 | 5100 | 3.65 | 1397.2603 | 0.61923 | 4700 | 3.1 | 1516.129 | 0.64266 | 4200 | 2.5 | 1680 | 0.66818 | 3700 | 2.05 | 1804.878 | 0.6903 | 3200 | 1.55 | 2064.5161 | 0.70966
| 3 |  | 2.8453 | max | 16560 | 3.54 | 4677.9661 | 4.3049 | 16360 | 3.25 | 5033.8462 | 3.7368 | 16080 | 2.96 | 5432.4324 | 3.3039 | 15860 | 2.66 | 5962.406 | 2.8688 | 15160 | 2.54 | 5968.5039 | 2.5805 | 14360 | 2.38 | 6033.6134 | 2.2551
|  | 8454.5455 | 45.4086 | nom | 14000 | 3.7 | 3783.7838 | 1963.9233 | 14000 | 3.41 | 4105.5718 | 2262.4897 | 14000 | 3.12 | 4487.1795 | 2558.9217 | 14000 | 2.82 | 4964.539 | 2947.0274 | 14000 | 2.67 | 5243.4457 | 3276.3259 | 14000 | 2.47 | 5668.0162 | 3749.1519
|  |  | 100 | mid | 11200 | 3.97 | 2821.1587 | 1 | 11200 | 3.68 | 3043.4783 | 1 | 11200 | 3.39 | 3303.8348 | 1 | 11200 | 3.09 | 3624.5955 | 1 | 11200 | 2.88 | 3888.8889 | 1 | 11200 | 2.62 | 4274.8092 | 1
|  |  | 2971.4356 | min | 5380 | 4.68 | 1149.5726 | 0.52827 | 4920 | 3.81 | 1291.3386 | 0.56283 | 4500 | 3.18 | 1415.0943 | 0.59023 | 4000 | 2.51 | 1593.6255 | 0.61869 | 3500 | 2.04 | 1715.6863 | 0.64345 | 3000 | 1.53 | 1960.7843 | 0.66519
| 4 |  | 3.001 | max | 16620 | 3.83 | 4339.4256 | 4.7463 | 16420 | 3.5 | 4691.4286 | 3.9649 | 16160 | 3.17 | 5097.7918 | 3.4601 | 15920 | 2.82 | 5645.3901 | 2.9546 | 15220 | 2.63 | 5787.0722 | 2.617 | 14420 | 2.41 | 5983.4025 | 2.2449
|  | 8031.8182 | 44.5417 | nom | 14000 | 4 | 3500 | 1692.2115 | 14000 | 3.67 | 3814.7139 | 2025.7281 | 14000 | 3.34 | 4191.6168 | 2321.2596 | 14000 | 2.99 | 4682.2742 | 2718.3937 | 14000 | 2.79 | 5017.9211 | 3069.1112 | 14000 | 2.54 | 5511.811 | 3577.7335
|  |  | 100 | mid | 11200 | 4.29 | 2610.7226 | 1 | 11200 | 3.96 | 2828.2828 | 1 | 11200 | 3.63 | 3085.3994 | 1 | 11200 | 3.28 | 3414.6341 | 1 | 11200 | 3.01 | 3720.9302 | 1 | 11200 | 2.69 | 4163.5688 | 1
|  |  | 2676.4217 | min | 5160 | 5.16 | 1000 | 0.47547 | 4740 | 3.97 | 1193.9547 | 0.50957 | 4300 | 3.26 | 1319.0184 | 0.54084 | 3800 | 2.52 | 1507.9365 | 0.57187 | 3300 | 2.03 | 1625.6158 | 0.59896 | 2800 | 1.51 | 1854.3046 | 0.62284
| 5 |  | 3.1798 | max | 16680 | 4.12 | 4048.5437 | 5.2008 | 16480 | 3.75 | 4394.6667 | 4.1805 | 16240 | 3.38 | 4804.7337 | 3.6019 | 15980 | 2.98 | 5362.4161 | 3.0259 | 15280 | 2.72 | 5617.6471 | 2.6435 | 14480 | 2.44 | 5934.4262 | 2.2297
|  | 7609.0909 | 43.6641 | nom | 14000 | 4.3 | 3255.814 | 1463.0514 | 14000 | 3.93 | 3562.341 | 1820.1337 | 14000 | 3.56 | 3932.5843 | 2112.4943 | 14000 | 3.16 | 4430.3797 | 2514.686 | 14000 | 2.91 | 4810.9966 | 2878.4379 | 14000 | 2.61 | 5363.9847 | 3412.5852
|  |  | 100 | mid | 11200 | 4.61 | 2429.5011 | 1 | 11200 | 4.24 | 2641.5094 | 1 | 11200 | 3.87 | 2894.0568 | 1 | 11200 | 3.47 | 3227.6657 | 1 | 11200 | 3.14 | 3566.879 | 1 | 11200 | 2.76 | 4057.971 | 1
|  |  | 2392.9652 | min | 4940 | 5.64 | 875.8865 | 0.42637 | 4560 | 4.13 | 1104.1162 | 0.4592 | 4100 | 3.34 | 1227.5449 | 0.49424 | 3600 | 2.53 | 1422.9249 | 0.52751 | 3100 | 2.02 | 1534.6535 | 0.55668 | 2600 | 1.49 | 1744.9664 | 0.58245
| 6 |  | 3.3715 | max | 16740 | 4.41 | 3795.9184 | 5.6671 | 16540 | 4 | 4135 | 4.3846 | 16320 | 3.59 | 4545.961 | 3.7306 | 16040 | 3.14 | 5108.2803 | 3.0837 | 15340 | 2.81 | 5459.0747 | 2.6607 | 14540 | 2.47 | 5886.6397 | 2.2097
|  | 7186.3636 | 42.7753 | nom | 14000 | 4.6 | 3043.4783 | 1268.0911 | 14000 | 4.19 | 3341.2888 | 1638.985 | 14000 | 3.78 | 3703.7037 | 1926.3143 | 14000 | 3.33 | 4204.2042 | 2330.4483 | 14000 | 3.03 | 4620.462 | 2700.9287 | 14000 | 2.68 | 5223.8806 | 3252.1739
|  |  | 100 | mid | 11200 | 4.93 | 2271.8053 | 1 | 11200 | 4.52 | 2477.8761 | 1 | 11200 | 4.11 | 2725.0608 | 1 | 11200 | 3.66 | 3060.1093 | 1 | 11200 | 3.27 | 3425.0765 | 1 | 11200 | 2.83 | 3957.5972 | 1
|  |  | 2131.4782 | min | 4720 | 6.12 | 771.2418 | 0.38061 | 4380 | 4.29 | 1020.979 | 0.41149 | 3900 | 3.42 | 1140.3509 | 0.45019 | 3400 | 2.54 | 1338.5827 | 0.48543 | 2900 | 2.01 | 1442.7861 | 0.51643 | 2400 | 1.47 | 1632.6531 | 0.5439
| 7 |  | 3.578 | max | 16800 | 4.7 | 3574.4681 | 6.1439 | 16600 | 4.25 | 3905.8824 | 4.5782 | 16400 | 3.8 | 4315.7895 | 3.8472 | 16100 | 3.3 | 4878.7879 | 3.1291 | 15400 | 2.9 | 5310.3448 | 2.6693 | 14600 | 2.5 | 5840 | 2.1853
|  | 6763.6364 | 41.8742 | nom | 14000 | 4.9 | 2857.1429 | 1100.8712 | 14000 | 4.45 | 3146.0674 | 1477.363 | 14000 | 4 | 3500 | 1758.0617 | 14000 | 3.5 | 4000 | 2161.534 | 14000 | 3.15 | 4444.4444 | 2533.8569 | 14000 | 2.75 | 5090.9091 | 3095.128
|  |  | 100 | mid | 11200 | 5.25 | 2133.3333 | 1 | 11200 | 4.8 | 2333.3333 | 1 | 11200 | 4.35 | 2574.7126 | 1 | 11200 | 3.85 | 2909.0909 | 1 | 11200 | 3.4 | 3294.1176 | 1 | 11200 | 2.9 | 3862.069 | 1
|  |  | 1890.3256 | min | 4500 | 6.6 | 681.8182 | 0.33786 | 4200 | 4.45 | 943.8202 | 0.36623 | 3700 | 3.5 | 1057.1429 | 0.40848 | 3200 | 2.55 | 1254.902 | 0.44545 | 2700 | 2 | 1350 | 0.47807 | 2200 | 1.45 | 1517.2414 | 0.50707
| 8 |  | 3.8542 | max | 16860 | 4.81 | 3505.1975 | 6.0973 | 16640 | 4.38 | 3799.0868 | 4.6481 | 16440 | 3.93 | 4183.2061 | 3.981 | 16160 | 3.48 | 4643.6782 | 3.3209 | 15440 | 3.06 | 5045.7516 | 2.8268 | 14640 | 2.64 | 5545.4545 | 2.3173
|  | 6340.9091 | 40.9601 | nom | 14000 | 5.02 | 2788.8446 | 1039.9508 | 14000 | 4.59 | 3050.1089 | 1364.1799 | 14000 | 4.16 | 3365.3846 | 1592.813 | 14000 | 3.69 | 3794.0379 | 1909.422 | 14000 | 3.32 | 4216.8675 | 2243.1079 | 14000 | 2.9 | 4827.5862 | 2736.3125
|  |  | 100 | mid | 11200 | 5.37 | 2085.6611 | 1 | 11200 | 4.95 | 2262.6263 | 1 | 11200 | 4.53 | 2472.4062 | 1 | 11200 | 4.06 | 2758.6207 | 1 | 11200 | 3.58 | 3128.4916 | 1 | 11200 | 3.06 | 3660.1307 | 1
|  |  | 1645.1952 | min | 4920 | 6.31 | 779.7147 | 0.22626 | 4600 | 4.54 | 1013.2159 | 0.26377 | 4120 | 3.73 | 1104.5576 | 0.31369 | 3640 | 2.91 | 1250.8591 | 0.35726 | 3200 | 2.34 | 1367.5214 | 0.39261 | 2760 | 1.77 | 1559.322 | 0.42428
| 9 |  | 4.1115 | max | 16920 | 4.92 | 3439.0244 | 5.9677 | 16680 | 4.51 | 3698.4479 | 4.6996 | 16480 | 4.06 | 4059.1133 | 4.1152 | 16220 | 3.66 | 4431.694 | 3.5282 | 15480 | 3.22 | 4807.4534 | 2.9994 | 14680 | 2.78 | 5280.5755 | 2.4626
|  | 5918.1818 | 40.0318 | nom | 14000 | 5.14 | 2723.7354 | 991.7011 | 14000 | 4.73 | 2959.8309 | 1259.2937 | 14000 | 4.32 | 3240.7407 | 1438.1272 | 14000 | 3.88 | 3608.2474 | 1677.4076 | 14000 | 3.49 | 4011.4613 | 1973.1099 | 14000 | 3.05 | 4590.1639 | 2403.2426
|  |  | 100 | mid | 11200 | 5.49 | 2040.0729 | 1 | 11200 | 5.1 | 2196.0784 | 1 | 11200 | 4.71 | 2377.9193 | 1 | 11200 | 4.27 | 2622.9508 | 1 | 11200 | 3.76 | 2978.7234 | 1 | 11200 | 3.22 | 3478.2609 | 1
|  |  | 1439.4323 | min | 5340 | 6.02 | 887.0432 | 0.098666 | 5000 | 4.63 | 1079.9136 | 0.14809 | 4540 | 3.96 | 1146.4646 | 0.20693 | 4080 | 3.27 | 1247.7064 | 0.25817 | 3700 | 2.68 | 1380.597 | 0.29576 | 3320 | 2.09 | 1588.5167 | 0.32972
| 10 |  | 4.3374 | max | 16980 | 5.03 | 3375.7455 | 5.73 | 16720 | 4.64 | 3603.4483 | 4.7287 | 16520 | 4.19 | 3942.7208 | 4.2501 | 16280 | 3.84 | 4239.5833 | 3.7541 | 15520 | 3.38 | 4591.716 | 3.1903 | 14720 | 2.92 | 5041.0959 | 2.6241
|  | 5495.4545 | 39.088 | nom | 14000 | 5.26 | 2661.597 | 959.0671 | 14000 | 4.87 | 2874.7433 | 1162.1436 | 14000 | 4.48 | 3125 | 1293.0277 | 14000 | 4.07 | 3439.8034 | 1463.8454 | 14000 | 3.66 | 3825.1366 | 1722.5728 | 14000 | 3.2 | 4375 | 2094.2486
|  |  | 100 | mid | 11200 | 5.61 | 1996.4349 | 0 | 11200 | 5.25 | 2133.3333 | 1 | 11200 | 4.89 | 2290.3885 | 1 | 11200 | 4.48 | 2500 | 1 | 11200 | 3.94 | 2842.6396 | 1 | 11200 | 3.38 | 3313.6095 | 1
|  |  | 1267.001 | min | 5760 | 5.73 | 1005.2356 | 0 | 5400 | 4.72 | 1144.0678 | 0.016458 | 4960 | 4.19 | 1183.7709 | 0.08581 | 4520 | 3.63 | 1245.1791 | 0.14603 | 4200 | 3.02 | 1390.7285 | 0.18506 | 3880 | 2.41 | 1609.9585 | 0.22069
| 11 |  | 4.5661 | max | 17040 | 5.14 | 3315.1751 | 5.44 | 16760 | 4.77 | 3513.6268 | 4.81 | 16560 | 4.32 | 3833.3333 | 4.42 | 16340 | 4.02 | 4064.6766 | 4.0026 | 15560 | 3.54 | 4395.4802 | 3.4036 | 14760 | 3.06 | 4823.5294 | 2.8058
|  | 5072.7273 | 38.1273 | nom | 14000 | 5.38 | 2602.2305 | 932.4866 | 14000 | 5.01 | 2794.4112 | 1054.6211 | 14000 | 4.64 | 3017.2414 | 1147.6759 | 14000 | 4.26 | 3286.385 | 1267.3436 | 14000 | 3.83 | 3655.3525 | 1490.4091 | 14000 | 3.35 | 4179.1045 | 1807.9337
|  |  | 91.6101 | mid | 11200 | 5.73 | 1954.6248 | 0 | 11200 | 5.4 | 2074.0741 | 0 | 11200 | 5.07 | 2209.073 | 0 | 11200 | 4.69 | 2388.0597 | 1 | 11200 | 4.12 | 2718.4466 | 1 | 11200 | 3.54 | 3163.8418 | 1
|  |  | 1110.9619 | min | 6180 | 5.44 | 1136.0294 | 0 | 5800 | 4.81 | 1205.8212 | 0 | 5380 | 4.42 | 1217.1946 | 0 | 4960 | 3.99 | 1243.1078 | 0.018065 | 4700 | 3.36 | 1398.8095 | 0.057343 | 4440 | 2.73 | 1626.3736 | 0.093599
| 12 |  | 4.7926 | max | 17100 | 5.25 | 3257.1429 | 5.15 | 16800 | 4.9 | 3428.5714 | 4.9 | 16600 | 4.45 | 3730.3371 | 4.65 | 16400 | 4.2 | 3904.7619 | 4.35 | 15600 | 3.7 | 4216.2162 | 3.7 | 14800 | 3.2 | 4625 | 3.05
|  | 4650 | 37.148 | nom | 14000 | 5.5 | 2545.4545 | 902.9126 | 14000 | 5.15 | 2718.4466 | 948.9796 | 14000 | 4.8 | 2916.6667 | 1000 | 14000 | 4.45 | 3146.0674 | 1068.9655 | 14000 | 4 | 3500 | 1256.7568 | 14000 | 3.5 | 4000 | 1524.5902
|  |  | 77.1379 | mid | 11200 | 5.85 | 1914.5299 | 0 | 11200 | 5.55 | 2018.018 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.9 | 2285.7143 | 0 | 11200 | 4.3 | 2604.6512 | 0 | 11200 | 3.7 | 3027.027 | 0
|  |  | 970.2456 | min | 6600 | 5.15 | 1281.5534 | 0 | 6200 | 4.9 | 1265.3061 | 0 | 5800 | 4.65 | 1247.3118 | 0 | 5400 | 4.35 | 1241.3793 | 0 | 5200 | 3.7 | 1405.4054 | 0 | 5000 | 3.05 | 1639.3443 | 0
| 13 |  | 4.9246 | max | 17566.6667 | 5.2833 | 3324.9211 | 5.15 | 17266.6667 | 4.9333 | 3500 | 4.9667 | 17033.3333 | 4.55 | 3743.5897 | 4.7833 | 16833.3333 | 4.3 | 3914.7287 | 4.55 | 16033.3333 | 3.8 | 4219.2982 | 3.9167 | 15200 | 3.3 | 4606.0606 | 3.2667
|  | 4227.2727 | 36.1478 | nom | 14000 | 5.5 | 2545.4545 | 820.8297 | 14000 | 5.1833 | 2700.9646 | 851.1287 | 14000 | 4.8667 | 2876.7123 | 883.7504 | 14000 | 4.55 | 3076.9231 | 929.0709 | 14000 | 4.1 | 3414.6341 | 1079.3037 | 14000 | 3.6167 | 3870.9677 | 1294.0631
|  |  | 68.5446 | mid | 11200 | 5.9 | 1898.3051 | 0 | 11200 | 5.5833 | 2005.9701 | 0 | 11200 | 5.3167 | 2106.5831 | 0 | 11200 | 5.0167 | 2232.5581 | 0 | 11200 | 4.4167 | 2535.8491 | 0 | 11200 | 3.8167 | 2934.4978 | 0
|  |  | 858.4027 | min | 6700 | 5.15 | 1300.9709 | 0 | 6266.6667 | 4.9667 | 1261.745 | 0 | 5833.3333 | 4.7833 | 1219.5122 | 0 | 5400 | 4.55 | 1186.8132 | 0 | 5233.3333 | 3.9167 | 1336.1702 | 0 | 5066.6667 | 3.2667 | 1551.0204 | 0
| 14 |  | 5.0304 | max | 18033.3333 | 5.3167 | 3391.8495 | 5.15 | 17733.3333 | 4.9667 | 3570.4698 | 5.0333 | 17466.6667 | 4.65 | 3756.2724 | 4.9167 | 17266.6667 | 4.4 | 3924.2424 | 4.75 | 16466.6667 | 3.9 | 4222.2222 | 4.1333 | 15600 | 3.4 | 4588.2353 | 3.4833
|  | 3804.5455 | 35.1243 | nom | 14000 | 5.5 | 2545.4545 | 738.7467 | 14000 | 5.2167 | 2683.7061 | 755.87 | 14000 | 4.9333 | 2837.8378 | 773.8059 | 14000 | 4.65 | 3010.7527 | 800.9569 | 14000 | 4.2 | 3333.3333 | 920.4545 | 14000 | 3.7333 | 3750 | 1092.214
|  |  | 60.182 | mid | 11200 | 5.95 | 1882.3529 | 0 | 11200 | 5.6167 | 1994.0653 | 0 | 11200 | 5.3833 | 2080.4954 | 0 | 11200 | 5.1333 | 2181.8182 | 0 | 11200 | 4.5333 | 2470.5882 | 0 | 11200 | 3.9333 | 2847.4576 | 0
|  |  | 756.3057 | min | 6800 | 5.15 | 1320.3883 | 0 | 6333.3333 | 5.0333 | 1258.2781 | 0 | 5866.6667 | 4.9167 | 1193.2203 | 0 | 5400 | 4.75 | 1136.8421 | 0 | 5266.6667 | 4.1333 | 1274.1935 | 0 | 5133.3333 | 3.4833 | 1473.6842 | 0
| 15 |  | 5.1046 | max | 18500 | 5.35 | 3457.9439 | 5.15 | 18200 | 5 | 3640 | 5.1 | 17900 | 4.75 | 3768.4211 | 5.05 | 17700 | 4.5 | 3933.3333 | 4.95 | 16900 | 4 | 4225 | 4.35 | 16000 | 3.5 | 4571.4286 | 3.7
|  | 3381.8182 | 34.0741 | nom | 14000 | 5.5 | 2545.4545 | 656.6637 | 14000 | 5.25 | 2666.6667 | 663.1016 | 14000 | 5 | 2800 | 669.667 | 14000 | 4.75 | 2947.3684 | 683.1956 | 14000 | 4.3 | 3255.814 | 777.4295 | 14000 | 3.85 | 3636.3636 | 914.0049
|  |  | 52.4614 | mid | 11200 | 6 | 1866.6667 | 0 | 11200 | 5.65 | 1982.3009 | 0 | 11200 | 5.45 | 2055.0459 | 0 | 11200 | 5.25 | 2133.3333 | 0 | 11200 | 4.65 | 2408.6022 | 0 | 11200 | 4.05 | 2765.4321 | 0
|  |  | 662.5002 | min | 6900 | 5.15 | 1339.8058 | 0 | 6400 | 5.1 | 1254.902 | 0 | 5900 | 5.05 | 1168.3168 | 0 | 5400 | 4.95 | 1090.9091 | 0 | 5300 | 4.35 | 1218.3908 | 0 | 5200 | 3.7 | 1405.4054 | 0
| 16 |  | 5.9289 | max | 19020 | 5.73 | 3319.3717 | 6.92 | 18720 | 5.3 | 3532.0755 | 5.68 | 18420 | 4.95 | 3721.2121 | 5.37 | 18200 | 4.59 | 3965.1416 | 5.02 | 17380 | 4.08 | 4259.8039 | 4.36 | 16460 | 3.56 | 4623.5955 | 3.65
|  | 2959.0909 | 32.9931 | nom | 14000 | 5.93 | 2360.8769 | 427.6143 | 14000 | 5.57 | 2513.465 | 520.9667 | 14000 | 5.21 | 2687.1401 | 551.0411 | 14000 | 4.85 | 2886.5979 | 589.4603 | 14000 | 4.39 | 3189.0661 | 678.6906 | 14000 | 3.92 | 3571.4286 | 810.7098
|  |  | 45.0781 | mid | 11200 | 6.42 | 1744.5483 | 0 | 11200 | 5.99 | 1869.783 | 0 | 11200 | 5.68 | 1971.831 | 0 | 11200 | 5.36 | 2089.5522 | 0 | 11200 | 4.74 | 2362.8692 | 0 | 11200 | 4.12 | 2718.4466 | 0
|  |  | 499.0994 | min | 6980 | 6.92 | 1008.6705 | 0 | 6460 | 5.68 | 1137.3239 | 0 | 6000 | 5.37 | 1117.3184 | 0 | 5520 | 5.02 | 1099.6016 | 0 | 5360 | 4.36 | 1229.3578 | 0 | 5180 | 3.65 | 1419.1781 | 0
| 17 |  | 7.0192 | max | 19540 | 6.11 | 3198.036 | 8.69 | 19240 | 5.6 | 3435.7143 | 6.26 | 18940 | 5.15 | 3677.6699 | 5.69 | 18700 | 4.68 | 3995.7265 | 5.09 | 17860 | 4.16 | 4293.2692 | 4.37 | 16920 | 3.62 | 4674.0331 | 3.6
|  | 2536.3636 | 31.8757 | nom | 14000 | 6.36 | 2201.2579 | 291.8715 | 14000 | 5.89 | 2376.91 | 405.1699 | 14000 | 5.42 | 2583.0258 | 445.7581 | 14000 | 4.95 | 2828.2828 | 498.3033 | 14000 | 4.48 | 3125 | 580.4036 | 14000 | 3.99 | 3508.7719 | 704.5455
|  |  | 37.92 | mid | 11200 | 6.84 | 1637.4269 | 0 | 11200 | 6.33 | 1769.3523 | 0 | 11200 | 5.91 | 1895.0931 | 0 | 11200 | 5.47 | 2047.532 | 0 | 11200 | 4.83 | 2318.8406 | 0 | 11200 | 4.19 | 2673.031 | 0
|  |  | 361.3459 | min | 7060 | 8.69 | 812.4281 | 0 | 6520 | 6.26 | 1041.5335 | 0 | 6100 | 5.69 | 1072.0562 | 0 | 5640 | 5.09 | 1108.055 | 0 | 5420 | 4.37 | 1240.2746 | 0 | 5160 | 3.6 | 1433.3333 | 0
| 18 |  | 8.3915 | max | 20060 | 6.49 | 3090.9091 | 10.46 | 19760 | 5.9 | 3349.1525 | 6.84 | 19460 | 5.35 | 3637.3832 | 6.01 | 19200 | 4.77 | 4025.1572 | 5.16 | 18340 | 4.24 | 4325.4717 | 4.38 | 17380 | 3.68 | 4722.8261 | 3.55
|  | 2113.6364 | 30.7142 | nom | 14000 | 6.79 | 2061.8557 | 202.0685 | 14000 | 6.21 | 2254.4283 | 309.0112 | 14000 | 5.63 | 2486.6785 | 351.6866 | 14000 | 5.05 | 2772.2772 | 409.6195 | 14000 | 4.57 | 3063.4573 | 482.5654 | 14000 | 4.06 | 3448.2759 | 595.3905
|  |  | 30.9917 | mid | 11200 | 7.26 | 1542.6997 | 0 | 11200 | 6.67 | 1679.1604 | 0 | 11200 | 6.14 | 1824.1042 | 0 | 11200 | 5.58 | 2007.1685 | 0 | 11200 | 4.92 | 2276.4228 | 0 | 11200 | 4.26 | 2629.108 | 0
|  |  | 251.8797 | min | 7140 | 10.46 | 682.6004 | 0 | 6580 | 6.84 | 961.9883 | 0 | 6200 | 6.01 | 1031.614 | 0 | 5760 | 5.16 | 1116.2791 | 0 | 5480 | 4.38 | 1251.1416 | 0 | 5140 | 3.55 | 1447.8873 | 0
| 19 |  | 10.0667 | max | 20580 | 6.87 | 2995.6332 | 12.23 | 20280 | 6.2 | 3270.9677 | 7.42 | 19980 | 5.55 | 3600 | 6.33 | 19700 | 4.86 | 4053.4979 | 5.23 | 18820 | 4.32 | 4356.4815 | 4.39 | 17840 | 3.74 | 4770.0535 | 3.5
|  | 1690.9091 | 29.4975 | nom | 14000 | 7.22 | 1939.0582 | 138.2591 | 14000 | 6.53 | 2143.951 | 227.8853 | 14000 | 5.84 | 2397.2603 | 267.1262 | 14000 | 5.15 | 2718.4466 | 323.3096 | 14000 | 4.66 | 3004.2918 | 385.1729 | 14000 | 4.13 | 3389.8305 | 483.1169
|  |  | 24.2977 | mid | 11200 | 7.68 | 1458.3333 | 0 | 11200 | 7.01 | 1597.7175 | 0 | 11200 | 6.37 | 1758.2418 | 0 | 11200 | 5.69 | 1968.3656 | 0 | 11200 | 5.01 | 2235.5289 | 0 | 11200 | 4.33 | 2586.6051 | 0
|  |  | 167.9705 | min | 7220 | 12.23 | 590.3516 | 0 | 6640 | 7.42 | 894.8787 | 0 | 6300 | 6.33 | 995.2607 | 0 | 5880 | 5.23 | 1124.283 | 0 | 5540 | 4.39 | 1261.959 | 0 | 5120 | 3.5 | 1462.8571 | 0
| 20 |  | 12.0754 | max | 21100 | 7.25 | 2910.3448 | 14 | 20800 | 6.5 | 3200 | 8 | 20500 | 5.75 | 3565.2174 | 6.65 | 20200 | 4.95 | 4080.8081 | 5.3 | 19300 | 4.4 | 4386.3636 | 4.4 | 18300 | 3.8 | 4815.7895 | 3.45
|  | 1268.1818 | 28.2076 | nom | 14000 | 7.65 | 1830.0654 | 90.5844 | 14000 | 6.85 | 2043.7956 | 158.5227 | 14000 | 6.05 | 2314.0496 | 190.704 | 14000 | 5.25 | 2666.6667 | 239.2796 | 14000 | 4.75 | 2947.3684 | 288.2231 | 14000 | 4.2 | 3333.3333 | 367.5889
|  |  | 17.8428 | mid | 11200 | 8.1 | 1382.716 | 0 | 11200 | 7.35 | 1523.8095 | 0 | 11200 | 6.6 | 1696.9697 | 0 | 11200 | 5.8 | 1931.0345 | 0 | 11200 | 5.1 | 2196.0784 | 0 | 11200 | 4.4 | 2545.4545 | 0
|  |  | 105.0217 | min | 7300 | 14 | 521.4286 | 0 | 6700 | 8 | 837.5 | 0 | 6400 | 6.65 | 962.406 | 0 | 6000 | 5.3 | 1132.0755 | 0 | 5600 | 4.4 | 1272.7273 | 0 | 5100 | 3.45 | 1478.2609 | 0