## Sheet1
Heating Demand (W) |  | 12400 | at | -2 | Indoor Temp. |  | 19 |  | Total Heating Elements Output (W) | [5 empty] | 23000 | at Delta T of 50C
LWT |  |  |  |  | 30 |  |  |  | 35 |  |  |  | 40 |  |  |  | 45 |  |  |  | 50 |  |  |  | 55 |  |  |  | 60 |  |  |  | 65
Outdoor air temperature[℃] |  | Heating Demand | COP | CL | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP | CAP | COP | PI | COP
|  |  | LWT |  |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI |  |  |  | PI
14kW-Maximum heating CAP | -15 |  | 1.1707 | max | 9566 | 2.62 | 3646 | 2.0092 | 9567 | 2.43 | 3944 | 1.9566 | 8569 | 2.17 | 3952 | 1.6898 | 7632 | 1.85 | 4123 | 1.6164 | 7010 | 1.62 | 4319 | 1.3074 | 6463 | 1.41 | 4578 | 1.2876 | 6012 | 1.19 | 5052 | 1.19 | / | / | / | /
|  | 18330.4348 | 60.9912 | norm | 7939 | 2.85 | 2787 | 9123.4112 | 7864 | 2.6 | 3030 | 9368.3486 | 7163 | 2.29 | 3123 | 10847.7062 | 6235 | 1.91 | 3264 | 11340.2156 | 5755 | 1.68 | 3420 | 14020.2602 | 5410 | 1.42 | 3809 | 14236.2113 | 5086 | 1.18 | 4313 | 15403.7267 | / | / | / | /
|  |  | 15658.298 | min | 5405 | 2.91 | 1854 | 3.1063 | 5309 | 2.66 | 1999 | 3.0581 | 4910 | 2.35 | 2091 | 3.6678 | 4884 | 1.91 | 2557 | 4.8932 | 4837 | 1.68 | 2874 | 6.2096 | 4524 | 1.43 | 3170 | 7.1204 | 4329 | 1.19 | 3652 | 8.3193 | / | / | / | /
| -10 |  | 1.3868 | max | 11420 | 2.73 | 4181 | 2.5371 | 10949 | 2.47 | 4441 | 2.3261 | 10601 | 2.26 | 4697 | 2.1298 | 9638 | 2.04 | 4730 | 1.9233 | 9067 | 1.81 | 5009 | 1.6584 | 8717 | 1.67 | 5213 | 1.482 | 6732 | 1.27 | 5301 | 1.0697 | / | / | / | /
|  | 15634.7826 | 56.1552 | norm | 9364 | 2.91 | 3216 | 6162.3421 | 8890 | 2.59 | 3434 | 6721.5199 | 8756 | 2.34 | 3738 | 7340.9852 | 8067 | 2.09 | 3855 | 8129.0126 | 7625 | 1.87 | 4082 | 9427.6482 | 7340 | 1.72 | 4257 | 10549.6664 | 5729 | 1.29 | 4440 | 14616.4903 | / | / | / | /
|  |  | 11274.4052 | min | 5082 | 3.02 | 1682 | 1.665 | 4763 | 2.66 | 1789 | 1.7575 | 4802 | 2.41 | 1992 | 1.868 | 5012 | 2.13 | 2349 | 2.2963 | 5168 | 1.9 | 2714 | 2.6845 | 5405 | 1.76 | 3075 | 3.0887 | 4510 | 1.32 | 3428 | 5.0067 | / | / | / | /
| -7 |  | 1.9467 | max | 12914 | 3.02 | 4282 | 2.9752 | 12698 | 2.79 | 4553 | 2.7397 | 12317 | 2.49 | 4939 | 2.4183 | 11943 | 2.31 | 5170 | 2.234 | 11035 | 2.07 | 5331 | 1.9936 | 10968 | 2.01 | 5457 | 1.9195 | 8024 | 1.51 | 5314 | 1.3179 | / | / | / | /
|  | 14017.3913 | 53.1616 | norm | 10486 | 3.19 | 3286 | 4711.4619 | 10044 | 2.96 | 3394 | 5116.4477 | 9866 | 2.69 | 3670 | 5796.3534 | 9459 | 2.44 | 3870 | 6274.5288 | 8563 | 2.15 | 3974 | 7031.1291 | 8577 | 2.09 | 4099 | 7302.7206 | 6507 | 1.55 | 4188 | 10636.1237 | / | / | / | /
|  |  | 7200.4593 | min | 4546 | 3.36 | 1354 | 1.1319 | 4571 | 3.1 | 1475 | 1.1623 | 4964 | 2.8 | 1772 | 1.2313 | 6210 | 2.52 | 2460 | 1.3618 | 5959 | 2.2 | 2713 | 1.5875 | 6252 | 2.15 | 2904 | 1.6466 | 5216 | 1.6 | 3262 | 3.1344 | / | / | / | /
| -5 |  | 2.0673 | max | 13191 | 3.41 | 3870 | 3.422 | 12464 | 2.99 | 4165 | 2.9688 | 12560 | 2.73 | 4609 | 2.7125 | 12071 | 2.42 | 4993 | 2.3848 | 11173 | 2.13 | 5243 | 2.0773 | 11144 | 2.09 | 5324 | 2.0325 | 8248 | 1.63 | 5059 | 1.4627 | / | / | / | /
|  | 12939.1304 | 51.1217 | norm | 10843 | 3.66 | 2965 | 3781.1923 | 9984 | 3.21 | 3115 | 4358.3394 | 10186 | 2.95 | 3452 | 4770.157 | 9681 | 2.57 | 3767 | 5425.659 | 8782 | 2.22 | 3959 | 6228.7879 | 8826 | 2.18 | 4051 | 6366.1908 | 6772 | 1.68 | 4037 | 8846.0672 | / | / | / | /
|  |  | 6259.0946 | min | 4775 | 3.81 | 1253 | 0.97007 | 4612 | 3.34 | 1381 | 1.0605 | 5187 | 3.07 | 1688 | 1.0514 | 6398 | 2.65 | 2410 | 1.153 | 6145 | 2.28 | 2692 | 1.3513 | 6463 | 2.24 | 2883 | 1.3835 | 5444 | 1.73 | 3153 | 2.673 | / | / | / | /
| 0 |  | 2.6726 | max | 13681 | 3.87 | 3535 | 4.0718 | 12432 | 3.26 | 3717 | 3.3745 | 13006 | 3.01 | 4319 | 3.1623 | 12694 | 2.62 | 4845 | 2.7388 | 11691 | 2.29 | 5099 | 2.3441 | 11599 | 2.27 | 5099 | 2.3248 | 9139 | 1.7 | 5366 | 1.6554 | / | / | / | /
|  | 10243.4783 | 45.8383 | norm | 10767 | 4.17 | 2584 | 2515.6855 | 9523 | 3.5 | 2721 | 3035.5612 | 10093 | 3.27 | 3085 | 3239.2942 | 9736 | 2.79 | 3484 | 3740.1438 | 8780 | 2.39 | 3666 | 4369.9434 | 8780 | 2.38 | 3695 | 4406.1363 | 7183 | 1.76 | 4085 | 6188.0122 | / | / | / | /
|  |  | 3832.751 | min | 5336 | 4.36 | 1224 | 0.58807 | 4786 | 3.66 | 1307 | 0.71377 | 5567 | 3.42 | 1627 | 0.62864 | 6918 | 2.9 | 2386 | 0.57574 | 6605 | 2.48 | 2669 | 0.71539 | 6901 | 2.46 | 2810 | 0.71147 | 6169 | 1.82 | 3393 | 1.3719 | / | / | / | /
| 5 |  | 4.0426 | max | 14908 | 4.51 | 3302 | 5.0323 | 14316 | 3.94 | 3632 | 4.3663 | 14275 | 3.61 | 3952 | 4.0671 | 14290 | 3.11 | 4592 | 3.5084 | 13798 | 2.77 | 4982 | 3.0439 | 13779 | 2.66 | 5179 | 2.9656 | 11696 | 2.17 | 5380 | 2.3695 | 9762 | 1.83 | 5334 | 1.9607
|  | 7547.8261 | 40.2195 | norm | 11882 | 4.9 | 2422 | 1499.8797 | 11109 | 4.27 | 2599 | 1728.6723 | 11220 | 3.96 | 2833 | 1855.815 | 11103 | 3.35 | 3314 | 2151.3665 | 10500 | 2.92 | 3595 | 2479.6569 | 10568 | 2.81 | 3767 | 2545.1523 | 9310 | 2.27 | 4108 | 3185.4293 | 8063 | 1.93 | 4186 | 3849.5612
|  |  | 1867.0739 | min | 5889 | 5.15 | 1143 | 0.18393 | 5583 | 4.49 | 1243 | 0.22499 | 6181 | 4.16 | 1486 | 0.16887 | 7859 | 3.49 | 2252 | -0.048387 | 7865 | 3.03 | 2595 | -0.053459 | 8681 | 2.91 | 2981 | -0.22228 | 7953 | 2.35 | 3380 | -0.10825 | 6882 | 2 | 3442 | 0.23119
| 7 |  | 4.9243 | max | 15551 | 4.94 | 3149 | 5.6461 | 15457 | 4.59 | 3368 | 5.2308 | 15596 | 4.04 | 3863 | 4.6925 | 15649 | 3.6 | 4347 | 4.2032 | 14971 | 3.11 | 4812 | 3.5258 | 14526 | 2.95 | 4925 | 3.3914 | 13202 | 2.54 | 5200 | 2.8987 | 10385 | 2.1 | 4945 | 2.3622
|  | 6469.5652 | 37.8468 | norm | 12285 | 5.39 | 2279 | 1145.8402 | 11886 | 5 | 2377 | 1236.8177 | 12149 | 4.45 | 2732 | 1378.7119 | 12050 | 3.89 | 3095 | 1539.1873 | 11288 | 3.28 | 3441 | 1834.8977 | 11040 | 3.11 | 3549 | 1907.6566 | 10416 | 2.65 | 3936 | 2231.8936 | 8505 | 2.21 | 3848 | 2738.7947
|  |  | 1313.8025 | min | 6034 | 5.68 | 1063 | 0.045767 | 5920 | 5.27 | 1124 | 0.057625 | 6644 | 4.68 | 1419 | -0.019486 | 8497 | 4.07 | 2090 | -0.28348 | 8429 | 3.43 | 2457 | -0.29952 | 9050 | 3.25 | 2783 | -0.47123 | 8885 | 2.77 | 3209 | -0.55952 | 7249 | 2.31 | 3126 | -0.24854
| 10 |  | 6.8528 | max | 15519 | 5.36 | 2894 | 6.2735 | 14863 | 4.79 | 3100 | 6.979 | 15266 | 4.24 | 3599 | 5.0625 | 14974 | 3.67 | 4076 | 4.3959 | 15308 | 3.31 | 4623 | 3.8539 | 14150 | 3.08 | 4601 | 3.5813 | 13200 | 2.69 | 4905 | 3.1289 | 11235 | 2.26 | 4982 | 2.6491
|  | 4852.1739 | 34.1053 | norm | 12136 | 5.85 | 2074 | 773.4457 | 11310 | 5.22 | 2165 | 695.2534 | 11770 | 4.67 | 2419 | 958.4612 | 11410 | 3.97 | 2872 | 1103.7943 | 11420 | 3.46 | 3302 | 1259.027 | 10641 | 3.21 | 3312 | 1354.8536 | 10309 | 2.78 | 3711 | 1550.7409 | 9111 | 2.35 | 3876 | 1831.6462
|  |  | 708.0618 | min | 6177 | 6.16 | 1002 | -0.14181 | 11616 | 5.5 | 1062 | -2.0831 | 6656 | 4.92 | 1353 | -0.2095 | 8281 | 4.15 | 1996 | -0.5123 | 8772 | 3.65 | 2403 | -0.59973 | 8957 | 3.36 | 2666 | -0.79045 | 9016 | 2.91 | 3101 | -0.99518 | 7954 | 2.46 | 3235 | -0.94539
| 15 |  | 7.048 | max | 15180 | 5.79 | 2624 | 7.048 | 14642 | 5.16 | 2941 | 6.2649 | 15833 | 4.45 | 3561 | 5.6243 | 15503 | 3.89 | 3981 | 4.9131 | 15342 | 3.51 | 4370 | 4.3627 | 12994 | 3.24 | 4016 | 3.9787 | 12737 | 2.84 | 4480 | 3.5561 | 11862 | 2.41 | 4965 | 3.1511
|  | 2156.5217 | 27.0951 | norm | 11947 | 6.37 | 1875 | 305.9779 | 11091 | 5.67 | 2049 | 344.2223 | 12286 | 4.94 | 2486 | 383.4299 | 11891 | 4.25 | 2797 | 438.934 | 11522 | 3.7 | 3112 | 494.3087 | 9836 | 3.41 | 2883 | 542.0164 | 10011 | 2.96 | 3378 | 606.436 | 9679 | 2.56 | 3780 | 684.3685
|  |  | 305.9779 | min | 5966 | 6.68 | 893 | -0.41344 | 5828 | 5.94 | 998 | -0.41655 | 7331 | 5.18 | 1416 | -0.60862 | 8589 | 4.42 | 1944 | -0.93036 | 9466 | 3.89 | 2435 | -1.244 | 8446 | 3.55 | 2378 | -1.3829 | 9043 | 3.09 | 2930 | -1.8642 | 8719 | 2.65 | 3287 | -2.088
Abbreviations:
LWT: Leaving water temperature (°C )
CL: Capacity level
CAP: Total heating capacity (W)
PI: Power input (W)

## Sheet2
Standard Conditions.
Heating Demand at 21C Indoor Temp. and -3.3C Outdoor Temp. = 8000W
Total output from Heating Elements at 50C Delta T = 20000W (10 radiators of nominal 2000W output).
To allow meaningful comparisons to be made a cold Winter's day is deemed to be as specified below.
Outside Temp | -7 | -6 | -5 | -4 | -3 | -2 | -1 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Hours | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2
Initial Conditions
Heating Demand = 8000W
Heating Elements = 20000W
Required Indoor Temp. = 21C
Indoor Temp. | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
Outside Temp | -7 | -6 | -5 | -4 | -3 | -2 | -1 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Hours | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2
COP | 2.2 | 2.26 | 2.42 | 2.49 | 2.55 | 2.9 | 2.98 | 3.07 | 3.16 | 3.25 | 4.11 | 4.21 | 4.28 | 5.01 | 5.13
LWT | 48.6 | 47.8 | 47 | 46.3 | 45.5 | 44.7 | 43.9 | 43.1 | 42.3 | 41.4 | 40.6 | 39.8 | 38.9 | 38 | 37.2 | 14kW
PI (W/h) | 4188 | 3940 | 3539 | 3311 | 3093 | 2615 | 2428 | 2251 | 2083 | 1924 | 1443 | 1328 | 1229 | 985 | 898 | Total | 12kW | % Diff.
Total Power at Temp | 8376 | 5910 | 5308.5 | 4966.5 | 4639.5 | 3922.5 | 3642 | 3376.5 | 3124.5 | 2886 | 2164.5 | 1992 | 1843.5 | 1970 | 1796 | 55918 | 54585.5 | 2.4411
Scenario 1.
To reduce the Indoor Temp, from 21C to 20C.
Indoor Temp. | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Outside Temp | -7 | -6 | -5 | -4 | -3 | -2 | -1 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Hours | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2
COP | 2.32 | 2.37 | 2.56 | 2.63 | 2.7 | 3.07 | 3.16 | 3.25 | 3.34 | 3.42 | 4.27 | 4.34 | 4.41 | 5.24 | 5.36
LWT | 46.8 | 46 | 45.3 | 44.5 | 43.7 | 42.9 | 42.1 | 41.3 | 40.4 | 39.6 | 38.8 | 37.9 | 37 | 36.2 | 35.3 | 14kW
PI (W/h) | 3839 | 3608 | 3218 | 3008 | 2808 | 2358 | 2188 | 2026 | 1872 | 1735 | 1310 | 1213 | 1119 | 880 | 799 | Total | 12kW | % Diff.
Total Power at Temp | 7678 | 5412 | 4827 | 4512 | 4212 | 3537 | 3282 | 3039 | 2808 | 2602.5 | 1965 | 1819.5 | 1678.5 | 1760 | 1598 | 50730.5 | 50566 | 0.32532
-9.277
Reducing the Indoor Temp, to 20C would lower the energy consumption by 9.28%.
Scenario 2.
To reduce the Indoor Temp. to 20C for 8 hours overnight, then increase it to 21C for 9 hours and 22 for 7 hours.
Indoor Temp. | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 22
Outside Temp | -7 | -6 | -5 | -4 | -3 | -2 | -1 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Hours | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2
COP | 2.32 | 2.37 | 2.56 | 2.63 | 2.7 | 2.9 | 2.98 | 3.07 | 3.16 | 3.25 | 4.11 | 399 | 4.11 | 4.79 | 4.9
LWT | 46.8 | 46 | 45.3 | 44.5 | 43.7 | 44.7 | 43.9 | 43.1 | 42.3 | 41.4 | 40.6 | 41.6 | 40.8 | 39.9 | 39 | 14kW
PI (W/h) | 3839 | 3608 | 3218 | 3008 | 2808 | 2615 | 2428 | 2251 | 2083 | 1924 | 1443 | 1484 | 1361 | 1100 | 1007 | Total | 12kW | % Diff.
Total Power at Temp | 7678 | 5412 | 4827 | 4512 | 4212 | 3922.5 | 3642 | 3376.5 | 3124.5 | 2886 | 2164.5 | 2226 | 2041.5 | 2200 | 2014 | 54238.5 | 53673 | 1.0536
-3.0035
Whilst the calculated overall reduction in energy consumption only shows a value of 3%, the true figure will be higher,
since the loading on the ASHP will reduce during the transition from 22C to 21C and 21C to 20C.
Scenario 3.
To reduce the Heating Demand by 10% with improved insulation.
Indoor Temp. | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
Outside Temp | -7 | -6 | -5 | -4 | -3 | -2 | -1 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Hours | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2
COP | 2.36 | 2.41 | 2.6 | 2.66 | 2.72 | 3.1 | 3.18 | 3.26 | 3.34 | 3.42 | 4.27 | 4.33 | 4.4 | 5.19 | 5.3
LWT | 46.4 | 45.7 | 45 | 44.3 | 43.6 | 42.8 | 42.1 | 41.4 | 40.6 | 39.9 | 39.1 | 38.3 | 37.5 | 36.7 | 35.9 | 14kW
PI (W/h) | 3518 | 3318 | 2967 | 2785 | 2610 | 2200 | 2051 | 1908 | 1772 | 1645 | 1249 | 1162 | 1078 | 856 | 783 | Total | 12kW | % Diff.
Total Power at Temp | 7036 | 4977 | 4450.5 | 4177.5 | 3915 | 3300 | 3076.5 | 2862 | 2658 | 2467.5 | 1873.5 | 1743 | 1617 | 1712 | 1566 | 47431.5 | 47347.5 | 0.17741
-15.1767
A 10% reduction in Heating Demand reduces energy consumption by 15.18%.
Scenario 4.
To reduce the Heating Demand by 20% with improved insulation.
Indoor Temp. | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
Outside Temp | -7 | -6 | -5 | -4 | -3 | -2 | -1 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Hours | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2
COP | 2.51 | 2.55 | 2.78 | 2.84 | 2.9 | 3.31 | 3.38 | 3.44 | 3.48 | 3.52 | 4.4 | 4.46 | 4.51 | 5.37 | 5.46
LWT | 44.2 | 43.6 | 42.9 | 42.3 | 41.6 | 41 | 40.3 | 39.6 | 38.9 | 38.2 | 37.5 | 36.8 | 36.1 | 35.4 | 34.6 | 14kW
PI (W/h) | 2935 | 2788 | 2461 | 2318 | 2180 | 1832 | 1713 | 1609 | 1514 | 1421 | 1078 | 1005 | 933 | 735 | 675 | Total | 12kW | % Diff.
Total Power at Temp | 5870 | 4182 | 3691.5 | 3477 | 3270 | 2748 | 2569.5 | 2413.5 | 2271 | 2131.5 | 1617 | 1507.5 | 1399.5 | 1470 | 1350 | 39968 | 40353 | -0.95408
-28.5239
A 20% reduction in Heating Demand reduces energy consumption by 28.52%.
Scenario 5.
To replace the Heating Elements with type K3, giving 31000W in total.
Indoor Temp. | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
Outside Temp | -7 | -6 | -5 | -4 | -3 | -2 | -1 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Hours | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2
COP | 2.59 | 2.63 | 2.94 | 2.98 | 3.02 | 3.4 | 3.44 | 3.48 | 3.52 | 3.56 | 4.47 | 4.57 | 4.68 | 5.5 | 5.57
LWT | 40.7 | 40.1 | 39.6 | 39 | 38.5 | 37.9 | 37.3 | 36.8 | 36.2 | 35.6 | 35 | 34.4 | 33.8 | 33.2 | 32.5 | 14kW
PI (W/h) | 3556 | 3381 | 2916 | 2764 | 2616 | 2230 | 2108 | 1988 | 1872 | 1757 | 1326 | 1224 | 1127 | 899 | 827 | Total | 12kW | % Diff.
Total Power at Temp | 7112 | 5071.5 | 4374 | 4146 | 3924 | 3345 | 3162 | 2982 | 2808 | 2635.5 | 1989 | 1836 | 1690.5 | 1798 | 1654 | 48527.5 | 49089 | -1.1438
-13.2167
A 55% increase in Heating Element output produces a 13.22% reduction in energy consumption.
Scenario 6.
To use stored heat energy to keep the air drawn into the ASHP at, or above, 7C.
Indoor Temp. | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
Outside Temp | -7 | -6 | -5 | -4 | -3 | -2 | -1 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Hours | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2
COP | 3.7 | 3.82 | 3.94 | 4.05 | 4.16 | 4.27 | 4.36 | 4.44 | 4.53 | 4.64 | 4.72 | 4.81 | 4.93 | 5.03 | 5.13
LWT | 48.6 | 47.8 | 47 | 46.3 | 45.5 | 44.7 | 43.9 | 43.1 | 42.3 | 41.4 | 40.6 | 39.8 | 38.9 | 38 | 37.2 | 14kW
PI (W/h) | 2490.1622 | 2330.9948 | 2173.7005 | 2035.6519 | 1895.9495 | 1775.9953 | 1659.5046 | 1556.4347 | 1453.0419 | 1347.6293 | 1256.5106 | 1162.3451 | 1066.9615 | 981.0835 | 898 | Total | 12kW | % Diff.
Total Power at Temp | 4980.3243 | 3496.4921 | 3260.5508 | 3053.4778 | 2843.9243 | 2663.993 | 2489.2569 | 2334.652 | 2179.5629 | 2021.444 | 1884.7659 | 1743.5177 | 1600.4422 | 1962.167 | 1796 | 38310.5708 | 38055.5 | 0.67026
-31.4879
If it is possible to keep the air flowing into the ASHP at 7C or above, then energy consumption could probably be reduced by 31.49%.
Scenario 7.
Running ASHP on fixed LWT at 45C.
Indoor Temp. | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
Outside Temp | -7 | -6 | -5 | -4 | -3 | -2 | -1 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Hours | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2
COP | 2.41 | 2.42 | 2.56 | 2.58 | 2.59 | 2.87 | 2.88 | 2.9 | 2.92 | 2.93 | 3.6 | 3.62 | 3.64 | 4.3 | 4.33
LWT | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 14kW
PI (W/h) | 3825 | 3670 | 3341 | 3195 | 3052 | 2640 | 2511 | 2384 | 2258 | 2133 | 1644 | 1544 | 1446 | 1147 | 1066 | Total | 12kW | % Diff.
Total Power at Temp | 7650 | 5505 | 5011.5 | 4792.5 | 4578 | 3960 | 3766.5 | 3576 | 3387 | 3199.5 | 2466 | 2316 | 2169 | 2294 | 2132 | 56803 | 56089 | 1.273
1.5827
Running an ASHP on a fixed LWT of 45C appears to increase the energy consumption by approximately 1.58%.
The actual increase may be greater, since the ASHP may be stopping and starting more frequently.

## Sheet3
Time | Required | Actual
0 | 55 | 25
5 | 52 | 28
10 | 49.6 | 30.4
15 | 47.68 | 32.32
20 | 46.144 | 33.856
25 | 44.9152 | 35.0848
30 | 43.9322 | 36.0678
35 | 43.1457 | 36.8543
40 | 42.5166 | 37.4834
45 | 42.0133 | 37.9867
50 | 41.6106 | 38.3894
55 | 41.2885 | 38.7115
60 | 41.0308 | 38.9692
65 | 40.8246 | 39.1754
70 | 40.6597 | 39.3403
75 | 40.5278 | 39.4722
80 | 40.4222 | 39.5778
85 | 40.3378 | 39.6622
90 | 40.2702 | 39.7298
95 | 40.2162 | 39.7838
100 | 40.1729 | 39.8271
105 | 40.1384 | 39.8616
110 | 40.1107 | 39.8893
115 | 40.0885 | 39.9115
120 | 40.0708 | 39.9292
125 | 40.0567 | 39.9433
130 | 40.0453 | 39.9547
135 | 40.0363 | 39.9637
140 | 40.029 | 39.971
145 | 40.0232 | 39.9768
150 | 40.0186 | 39.9814