## Sheet1
|  |  |  | Heating only. |  |  |  | Heating + DHW
| 24 Hours Ending | Amb Avg | kWh Meter (kWh) | VxI Calc. (kWh) | Corr. Factor | Diff. (kWh) | Auxilary PI Avg. each hour (kWh) | VxI Calc. (kWh) | Corr. Factor | Diff. (kWh) | Auxilary PI Avg. each hour (kWh)
| 2023-12-14T21:01:00 | 6.19 | 42 | 36.746 | 1.143 | 5.254 | 0.21892 | 38.375 | 1.0945 | 3.625 | 0.15104
| 2023-12-15T21:01:01 | 6.88 | 40 | 35.152 | 1.1379 | 4.848 | 0.202 | 35.152 | 1.1379 | 4.848 | 0.202
| 2023-12-13T21:01:01 | 8.07 | 36 | 29.935 | 1.2026 | 6.065 | 0.25271 | 29.935 | 1.2026 | 6.065 | 0.25271
| 2023-12-16T21:01:00 | 9.5 | 33 | 26.342 | 1.2528 | 6.658 | 0.27742 | 27.553 | 1.1977 | 5.447 | 0.22696
| 2023-12-17T21:01:00 | 10.44 | 23 | 17.34 | 1.3264 | 5.66 | 0.23583 | 18.318 | 1.2556 | 4.682 | 0.19508
| 2023-12-18T21:01:00 | 11.48 | 22 | 16.012 | 1.374 | 5.988 | 0.2495 | 17.252 | 1.2752 | 4.748 | 0.19783
[5 empty] | Average | 5.7455 | 0.2394 |  | Average | 4.9025 | 0.20427
Notes:
1) | The 24 hour time periods commence at 21:00 on the previous day and end at 21:00 on the date shown.
2) | The ambient temperature values in column C are averaged over the 24 hour period using the hourly average data which itself has been obtained by averaging the minute data.
3) | The kWh Meter values are only available as integers, so will produce a degree of inaccuracy in any calculations in which they are used. They also appear to include energy used for DHW heating.
4) | The VxI Calc values are the summed values from the 'minite data' and exclude energy used for DHW heating in column E, and include DHW heating in Column I.
5) | The calculated Corr. Factors are produced by dividing the kWh Meter reading by the appropriate VxI Calc.
6) | The Diff. vakues are a simple subtraction of the appropriate VxI value from the kWh Meter value.
7) | The Auxiliary PI Avg. is obtained by dividing the Diff. value by 24.