## Base
[9 empty] | water specific heat | 4.2 | kJ/kg/C
| Average rad surface temp | 52.95 | [6 empty] | average power | 8.4187 | kJ/s (kW)
| Average | 49.1 | 56.8 | -4 | 25 |  |  | 8.4187 | Average rad temp | 52.95 | C
[9 empty] | Average room temp | 25 | C
|  | C | C | C | C | m3/hr | l/s | Q | DT rad – room | 27.95 | C
datetime |  | RWT | LWT | ambient | room_temp | flowrate |  | kJ/s (kW)
2025-01-11T06:00:33 | 0 | 50 | 56 | -4 | 25 | 1.03 | 0.28611 | 7.21 | Q=U.A.DT
2025-01-11T06:01:33 | 1 | 49 | 58 | -4 | 25 | 0.93 | 0.25833 | 9.765 | U.A = Q / DT
2025-01-11T06:02:33 | 2 | 49 | 58 | -4 | 25 | 0.93 | 0.25833 | 9.765
2025-01-11T06:03:33 | 3 | 49 | 56 | -4 | 25 | 0.95 | 0.26389 | 7.7583 | U.A = | 0.3012 | kW/C | This number is the heat transfer coefficient of your heat emitters multiplied by the total surface area
2025-01-11T06:04:33 | 4 | 49 | 56 | -4 | 25 | 0.93 | 0.25833 | 7.595
2025-01-11T06:05:33 | 5 | 49 | 57 | -4 | 25 | 0.89 | 0.24722 | 8.3067
2025-01-11T06:06:33 | 6 | 49 | 57 | -4 | 25 | 0.92 | 0.25556 | 8.5867
2025-01-11T06:07:33 | 7 | 49 | 56 | -4 | 25 | 0.95 | 0.26389 | 7.7583
2025-01-11T06:08:33 | 8 | 49 | 56 | -4 | 25 | 0.94 | 0.26111 | 7.6767
2025-01-11T06:09:33 | 9 | 49 | 58 | -4 | 25 | 0.93 | 0.25833 | 9.765

## Calcs
[13 empty] | Incremental |  |  |  |  | The energy flow in 1min
[9 empty] | ASHP | [13 empty] | Ice heat of fusion (melting) | 333 | kg/kg
[9 empty] | kW |  | energy out of rads
[6 empty] | m3/hr |  | C |  | l/min | kW | kJ |  |  |  |  | flow | Delta Q
datetime | time | RWT | LWT | ambient | room | flowrate | fan | DT |  | Flow | Q out |  | time | time | t_start | t_end | l | kJ |  |  |  |  | t0 to t9 is the system in equilibrium, energy out from ASHP is released into building, RWT and LWT are stable.
2025-01-11T06:00:33 | 0 | 50 | 56 | -4 | 25 | 1.03 | 610 | 6 | 7.21 | 17.1667 | 8.4337 | 506.0236 | 0 | 1 | 56 | 58 | 17.1667 | 144.2 | - the system is at equilibrium |  |  |  | Base load is 8.4kW with U.A = 0.3kW/C
2025-01-11T06:01:33 | 1 | 49 | 58 | -4 | 25 | 0.93 | 610 | 9 | 9.765 | 15.5 | 8.5843 | 515.0597 | 1 | 2 | 58 | 58 | 15.5 | 0 |  |  |  |  | Fan stops between t9 and t10, start of defrost.
2025-01-11T06:02:33 | 2 | 49 | 58 | -4 | 25 | 0.93 | 610 | 9 | 9.765 | 15.5 | 8.5843 | 515.0597 | 2 | 3 | 58 | 56 | 15.5 | -130.2 |  |  |  |  | Refrigerant circuit runs backwards, LWT goes down because energy is flowing into refrigerant.
2025-01-11T06:03:33 | 3 | 49 | 56 | -4 | 25 | 0.95 | 610 | 7 | 7.7583 | 15.8333 | 8.2831 | 496.9875 | 3 | 4 | 56 | 56 | 15.8333 | 0 |  |  |  |  | Switch to incremental analysis
2025-01-11T06:04:33 | 4 | 49 | 56 | -4 | 25 | 0.93 | 610 | 7 | 7.595 | 15.5 | 8.2831 | 496.9875 | 4 | 5 | 56 | 57 | 15.5 | 65.1 | [5 empty] | every minute, water flows through ASHP and cools down.
2025-01-11T06:05:33 | 5 | 49 | 57 | -4 | 25 | 0.89 | 610 | 8 | 8.3067 | 14.8333 | 8.4337 | 506.0236 | 5 | 6 | 57 | 57 | 14.8333 | 0 | [5 empty] | every minute, LWT drops but is still higher than room temperature, rads are still releasing energy.
2025-01-11T06:06:33 | 6 | 49 | 57 | -4 | 25 | 0.92 | 610 | 8 | 8.5867 | 15.3333 | 8.4337 | 506.0236 | 6 | 7 | 57 | 56 | 15.3333 | -64.4 | [5 empty] | Every minute, RWT drops because LWT drops and rads are releasing enery.
2025-01-11T06:07:33 | 7 | 49 | 56 | -4 | 25 | 0.95 | 610 | 7 | 7.7583 | 15.8333 | 8.2831 | 496.9875 | 7 | 8 | 56 | 56 | 15.8333 | 0 | [5 empty] | Rad energy release based on U.A.DT – refer to “base” tab
2025-01-11T06:08:33 | 8 | 49 | 56 | -4 | 25 | 0.94 | 610 | 7 | 7.6767 | 15.6667 | 8.2831 | 496.9875 | 8 | 9 | 56 | 58 | 15.6667 | 131.6 | /- energy leaving system (defrost + rads) |  |  |  |  | add in rad energy to get energy needed for melting ice
2025-01-11T06:09:33 | 9 | 49 | 58 | -4 | 25 | 0.93 | 610 | 9 | 9.765 | 15.5 | 8.5843 | 515.0597 | 9 | 10 | 58 | 50 | 15.5 | -520.8 | -5.7403 | -1018.3485 | -3.0581 | kg |  | about 3kg of ice on ASHP
2025-01-11T06:10:33 | 10 | 49 | 50 | -4 | 25 | 1.06 | 30 | 1 | 1.2367 | 17.6667 | 7.3795 | 442.7707 | 10 | 11 | 50 | 41 | 17.6667 | -667.8 | -225.0293
2025-01-11T06:11:33 | 11 | 47 | 41 | -3 | 25 | 1.41 | 0 | -6 | -9.87 | 23.5 | 5.7229 | 343.3732 | 11 | 12 | 41 | 35 | 23.5 | -592.2 | -248.8268
2025-01-11T06:12:33 | 12 | 44 | 35 | -2 | 25 | 1.43 | 0 | -9 | -15.015 | 23.8333 | 4.3675 | 262.0479 | 12 | 13 | 35 | 27 | 23.8333 | -800.8 | -538.7521
2025-01-11T06:13:33 | 13 | 38 | 27 | 0 | 25 | 1.44 | 0 | -11 | -18.48 | 24 | 2.259 | 135.542 | 13 | 14 | 27 | 38 | 24 | 1108.8 |  | \- | Need to add in the energy out the rads
2025-01-11T06:14:33 | 14 | 35 | 38 | 1 | 25 | 1.45 | 590 | 3 | 5.075 | 24.1667 | 3.4639 | 207.8311 | 14 | 15 | 38 | 39 | 24.1667 | 101.5
2025-01-11T06:15:33 | 15 | 35 | 39 | 0 | 25 | 1.41 | 610 | 4 | 6.58 | 23.5 | 3.6145 | 216.8673 | 15 | 16 | 39 | 40 | 23.5 | 98.7
2025-01-11T06:16:33 | 16 | 36 | 40 | -1 | 25 | 1.41 | 620 | 4 | 6.58 | 23.5 | 3.9157 | 234.9395 | 16 | 17 | 40 | 42 | 23.5 | 197.4
2025-01-11T06:17:33 | 17 | 37 | 42 | -2 | 25 | 1.41 | 630 | 5 | 8.225 | 23.5 | 4.3675 | 262.0479 | 17 | 18 | 42 | 45 | 23.5 | 296.1
2025-01-11T06:18:33 | 18 | 39 | 45 | -2 | 25 | 1.4 | 630 | 6 | 9.8 | 23.3333 | 5.1205 | 307.2286 | 18 | 19 | 45 | 48 | 23.3333 | 294
2025-01-11T06:19:33 | 19 | 40 | 48 | -2 | 25 | 1.39 | 630 | 8 | 12.9733 | 23.1667 | 5.7229 | 343.3732 | 19 | 20 | 48 | 49 | 23.1667 | 97.3
2025-01-11T06:20:33 | 20 | 42 | 49 | -3 | 25 | 1.37 | 630 | 7 | 11.1883 | 22.8333 | 6.1747 | 370.4816 | 20 | 21 | 49 | 50 | 22.8333 | 95.9
2025-01-11T06:21:33 | 21 | 43 | 50 | -3 | 25 | 1.32 | 620 | 7 | 10.78 | 22 | 6.4759 | 388.5538 | 21 | 22 | 50 | 51 | 22 | 92.4
2025-01-11T06:22:33 | 22 | 44 | 51 | -3 | 25 | 1.31 | 610 | 7 | 10.6983 | 21.8333 | 6.7771 | 406.6261 | 22 | 23 | 51 | 52 | 21.8333 | 91.7
2025-01-11T06:23:33 | 23 | 45 | 52 | -3 | 25 | 1.3 | 610 | 7 | 10.6167 | 21.6667 | 7.0783 | 424.6984 | 23 | 24 | 52 | 53 | 21.6667 | 91
2025-01-11T06:24:33 | 24 | 46 | 53 | -3 | 25 | 1.38 | 610 | 7 | 11.27 | 23 | 7.3795 | 442.7707 | 24 | 25 | 53 | 53 | 23 | 0
2025-01-11T06:25:33 | 25 | 46 | 53 | -3 | 25 | 1.39 | 610 | 7 | 11.3517 | 23.1667 | 7.3795 | 442.7707 | 25 | 26 | 53 | 54 | 23.1667 | 97.3
2025-01-11T06:26:33 | 26 | 47 | 54 | -3 | 25 | 1.37 | 610 | 7 | 11.1883 | 22.8333 | 7.6807 | 460.8429 | 26 | 27 | 54 | 54 | 22.8333 | 0
2025-01-11T06:27:33 | 27 | 48 | 54 | -4 | 25 | 1.38 | 610 | 6 | 9.66 | 23 | 7.8313 | 469.8791 | 27 | 28 | 54 | 55 | 23 | 96.6
2025-01-11T06:28:33 | 28 | 48 | 55 | -4 | 25 | 1.38 | 600 | 7 | 11.27 | 23 | 7.9819 | 478.9152 | 28 | 29 | 55 | 55 | 23 | 0
2025-01-11T06:29:33 | 29 | 48 | 55 | -4 | 25 | 1.38 | 610 | 7 | 11.27 | 23 | 7.9819 | 478.9152 | 29 | 30 | 55 | 56 | 23 | 96.6
2025-01-11T06:30:33 | 30 | 49 | 56 | -4 | 25 | 1.4 | 610 | 7 | 11.4333 | 23.3333 | 8.2831 | 496.9875 | 30 | 31 | 56 | 56 | 23.3333 | 0
2025-01-11T06:31:33 | 31 | 49 | 56 | -4 | 25 | 1.37 | 610 | 7 | 11.1883 | 22.8333 | 8.2831 | 496.9875 | 31 | 32 | 56 | 57 | 22.8333 | 95.9
2025-01-11T06:32:33 | 32 | 50 | 57 | -4 | 25 | 1.39 | 610 | 7 | 11.3517 | 23.1667 | 8.5843 | 515.0597 | 32 | 33 | 57 | 57 | 23.1667 | 0
2025-01-11T06:33:33 | 33 | 50 | 57 | -4 | 25 | 1.27 | 610 | 7 | 10.3717 | 21.1667 | 8.5843 | 515.0597 | 33 | 34 | 57 | 56 | 21.1667 | -88.9
2025-01-11T06:34:33 | 34 | 50 | 56 | -4 | 25 | 1.15 | 610 | 6 | 8.05 | 19.1667 | 8.4337 | 506.0236 | 34 | 35 | 56 | 57 | 19.1667 | 80.5
2025-01-11T06:35:33 | 35 | 49 | 57 | -4 | 25 | 1.02 | 610 | 8 | 9.52 | 17 | 8.4337 | 506.0236 | 35 | 36 | 57 | 58 | 17 | 71.4
2025-01-11T06:36:33 | 36 | 49 | 58 | -4 | 25 | 0.93 | 600 | 9 | 9.765 | 15.5 | 8.5843 | 515.0597 | 36 | 37 | 58 | 58 | 15.5 | 0
2025-01-11T06:37:33 | 37 | 49 | 58 | -4 | 25 | 0.94 | 600 | 9 | 9.87 | 15.6667 | 8.5843 | 515.0597 | 37 | 38 | 58 | 56 | 15.6667 | -131.6
2025-01-11T06:38:33 | 38 | 50 | 56 | -4 | 25 | 1.03 | 610 | 6 | 7.21 | 17.1667 | 8.4337 | 506.0236 | 38 | 39 | 56 | 56 | 17.1667 | 0
2025-01-11T06:39:33 | 39 | 49 | 56 | -4 | 25 | 1.04 | 610 | 7 | 8.4933 | 17.3333 | 8.2831 | 496.9875 | 39 | 40 | 56 | 58 | 17.3333 | 145.6
2025-01-11T06:40:33 | 40 | 49 | 58 | -4 | 25 | 0.96 | 610 | 9 | 10.08 | 16 | 8.5843 | 515.0597 | 40 | 41 | 58 | 58 | 16 | 0
2025-01-11T06:41:33 | 41 | 49 | 58 | -4 | 25 | 0.94 | 610 | 9 | 9.87 | 15.6667 | 8.5843 | 515.0597 | 41 | 42 | 58 | 56 | 15.6667 | -131.6
2025-01-11T06:42:33 | 42 | 50 | 56 | -4 | 25 | 1.05 | 610 | 6 | 7.35 | 17.5 | 8.4337 | 506.0236 | 42 | 43 | 56 | 56 | 17.5 | 0
2025-01-11T06:43:33 | 43 | 50 | 56 | -4 | 25 | 1.05 | 610 | 6 | 7.35 | 17.5 | 8.4337 | 506.0236 | 43 | 44 | 56 | 57 | 17.5 | 73.5
2025-01-11T06:44:33 | 44 | 49 | 57 | -4 | 25 | 0.96 | 610 | 8 | 8.96 | 16 | 8.4337 | 506.0236 | 44 | 45 | 57 | 58 | 16 | 67.2
2025-01-11T06:45:33 | 45 | 49 | 58 | -4 | 25 | 0.91 | 610 | 9 | 9.555 | 15.1667 | 8.5843 | 515.0597 | 45 | 46 | 58 | 56 | 15.1667 | -127.4
2025-01-11T06:46:33 | 46 | 49 | 56 | -4 | 25 | 0.93 | 610 | 7 | 7.595 | 15.5 | 8.2831 | 496.9875 | 46 | 47 | 56 | 55 | 15.5 | -65.1
2025-01-11T06:47:33 | 47 | 49 | 55 | -4 | 25 | 0.94 | 610 | 6 | 6.58 | 15.6667 | 8.1325 | 487.9513 | 47 | 48 | 55 | 56 | 15.6667 | 65.8
2025-01-11T06:48:33 | 48 | 49 | 56 | -4 | 25 | 0.92 | 610 | 7 | 7.5133 | 15.3333 | 8.2831 | 496.9875 | 48 | 49 | 56 | 58 | 15.3333 | 128.8
2025-01-11T06:49:33 | 49 | 49 | 58 | -4 | 25 | 0.93 | 610 | 9 | 9.765 | 15.5 | 8.5843 | 515.0597 | 49 | 50 | 58 | 56 | 15.5 | -130.2
2025-01-11T06:50:33 | 50 | 49 | 56 | -4 | 25 | 0.94 | 610 | 7 | 7.6767 | 15.6667 | 8.2831 | 496.9875 | 50 | 51 | 56 | 56 | 15.6667 | 0
2025-01-11T06:51:33 | 51 | 49 | 56 | -4 | 25 | 0.96 | 610 | 7 | 7.84 | 16 | 8.2831 | 496.9875 | 51 | 52 | 56 | 57 | 16 | 67.2
2025-01-11T06:52:33 | 52 | 49 | 57 | -4 | 25 | 0.93 | 610 | 8 | 8.68 | 15.5 | 8.4337 | 506.0236 | 52 | 53 | 57 | 51 | 15.5 | -390.6 | 115.4236 | -940.4594 | -2.8242
2025-01-11T06:53:33 | 53 | 49 | 51 | -4 | 25 | 0.94 | 480 | 2 | 2.1933 | 15.6667 | 7.5301 | 451.8068 | 53 | 54 | 51 | 45 | 15.6667 | -394.8 | 57.0068
2025-01-11T06:54:33 | 54 | 48 | 45 | -3 | 25 | 1.41 | 0 | -3 | -4.935 | 23.5 | 6.4759 | 388.5538 | 54 | 55 | 45 | 37 | 23.5 | -789.6 | -401.0462
2025-01-11T06:55:33 | 55 | 45 | 37 | -2 | 25 | 1.43 | 0 | -8 | -13.3467 | 23.8333 | 4.8193 | 289.1564 | 55 | 56 | 37 | 27 | 23.8333 | -1001 | -711.8436
2025-01-11T06:56:33 | 56 | 40 | 27 | -1 | 25 | 1.44 | 0 | -13 | -21.84 | 24 | 2.5602 | 153.6143 | 56 | 57 | 27 | 33 | 24 | 604.8
2025-01-11T06:57:33 | 57 | 35 | 33 | 1 | 25 | 1.45 | 370 | -2 | -3.3833 | 24.1667 | 2.7108 | 162.6504 | 57 | 58 | 33 | 38 | 24.1667 | 507.5
2025-01-11T06:58:33 | 58 | 36 | 38 | 1 | 25 | 1.43 | 550 | 2 | 3.3367 | 23.8333 | 3.6145 | 216.8673 | 58 | 59 | 38 | 40 | 23.8333 | 200.2
2025-01-11T06:59:33 | 59 | 36 | 40 | 0 | 25 | 1.43 | 550 | 4 | 6.6733 | 23.8333 | 3.9157 | 234.9395

## OriginalData
datetime | on_off_bin | htg_on_off | dhw_on_off | RWT | LWT | ambient | room_temp | dhw_temp | amps_in | volts_in | capacity | setLWT | flowrate | ability | energy_in | energy_out | MD02_tmp | MD02_hmd | comp_freq | fan | energy in | LWT-RWT | energy out
2025-01-11T06:00:33 | 10000001101000 | 1 | 0 | 50 | 56 | -4 | 25 | 45 | 18 | 219 | 14 | 58 | 1.03 | 7.55 | 22306 | 1292 | 17.7 | 36.9 | 55 | 610 | 0.0657 | 6 | 0.11588
2025-01-11T06:01:33 | 10000001101000 | 1 | 0 | 49 | 58 | -4 | 25 | 45 | 23 | 217 | 14 | 58 | 0.93 | 9.42 | 22306 | 1292 | 17.7 | 36.9 | 67 | 610 | 0.083183 | 9 | 0.15694
2025-01-11T06:02:33 | 10000001101000 | 1 | 0 | 49 | 58 | -4 | 25 | 45 | 16 | 220 | 14 | 58 | 0.93 | 9.07 | 22306 | 1292 | 17.7 | 36.8 | 51 | 610 | 0.058667 | 9 | 0.15694 | 0.25833 | 9.765
2025-01-11T06:03:33 | 10000001101000 | 1 | 0 | 49 | 56 | -4 | 25 | 45 | 16 | 220 | 14 | 58 | 0.95 | 6.86 | 22307 | 1292 | 17.7 | 36.8 | 51 | 610 | 0.058667 | 7 | 0.12469
2025-01-11T06:04:33 | 10000001101000 | 1 | 0 | 49 | 56 | -4 | 25 | 45 | 18 | 220 | 14 | 58 | 0.93 | 7.44 | 22307 | 1292 | 17.7 | 36.8 | 55 | 610 | 0.066 | 7 | 0.12206
2025-01-11T06:05:33 | 10000001101000 | 1 | 0 | 49 | 57 | -4 | 25 | 45 | 22 | 219 | 14 | 58 | 0.89 | 8.83 | 22307 | 1292 | 17.7 | 36.8 | 65 | 610 | 0.0803 | 8 | 0.1335
2025-01-11T06:06:33 | 10000001101000 | 1 | 0 | 49 | 57 | -4 | 25 | 45 | 16 | 221 | 14 | 58 | 0.92 | 8.95 | 22307 | 1292 | 17.7 | 36.9 | 51 | 610 | 0.058933 | 8 | 0.138
2025-01-11T06:07:33 | 10000001101000 | 1 | 0 | 49 | 56 | -4 | 25 | 45 | 16 | 221 | 14 | 58 | 0.95 | 7.21 | 22307 | 1293 | 17.7 | 36.7 | 51 | 610 | 0.058933 | 7 | 0.12469
2025-01-11T06:08:33 | 10000001101000 | 1 | 0 | 49 | 56 | -4 | 25 | 45 | 18 | 220 | 14 | 58 | 0.94 | 7.55 | 22307 | 1293 | 17.7 | 36.8 | 55 | 610 | 0.066 | 7 | 0.12337
2025-01-11T06:09:33 | 10000001101000 | 1 | 0 | 49 | 58 | -4 | 25 | 45 | 19 | 220 | 14 | 58 | 0.93 | 9.18 | 22307 | 1293 | 17.7 | 36.7 | 61 | 610 | 0.069667 | 9 | 0.15694
2025-01-11T06:10:33 | 1010000001101000 | 1 | 0 | 49 | 50 | -4 | 25 | 45 | 2 | 226 | 14 | 58 | 1.06 | 4.07 | 22307 | 1293 | 17.7 | 36.7 | 29 | 30 | 0.0075333 | 1 | 0.019875
2025-01-11T06:11:33 | 1010000001101000 | 1 | 0 | 47 | 41 | -3 | 25 | 45 | 2 | 225 | 14 | 58 | 1.41 | 4.07 | 22307 | 1293 | 17.7 | 36.7 | 37 | 0 | 0.0075 | -6 | -0.15862
2025-01-11T06:12:33 | 1010000001101000 | 1 | 0 | 44 | 35 | -2 | 25 | 45 | 3 | 225 | 14 | 58 | 1.43 | 4.07 | 22307 | 1293 | 17.7 | 36.7 | 37 | 0 | 0.01125 | -9 | -0.24131
2025-01-11T06:13:33 | 10000001101000 | 1 | 0 | 38 | 27 | 0 | 25 | 45 | 6 | 224 | 14 | 58 | 1.44 | 4.07 | 22307 | 1293 | 17.7 | 36.6 | 32 | 0 | 0.0224 | -11 | -0.297
2025-01-11T06:14:33 | 10000001101000 | 1 | 0 | 35 | 38 | 1 | 25 | 45 | 9 | 224 | 14 | 58 | 1.45 | 4.07 | 22307 | 1293 | 17.7 | 36.6 | 40 | 590 | 0.0336 | 3 | 0.081562
2025-01-11T06:15:33 | 10000001101000 | 1 | 0 | 35 | 39 | 0 | 25 | 45 | 9 | 222 | 14 | 58 | 1.41 | 4.07 | 22307 | 1293 | 17.7 | 36.6 | 41 | 610 | 0.0333 | 4 | 0.10575
2025-01-11T06:16:33 | 10000001101000 | 1 | 0 | 36 | 40 | -1 | 25 | 45 | 14 | 220 | 14 | 58 | 1.41 | 4.07 | 22307 | 1293 | 17.7 | 36.6 | 55 | 620 | 0.051333 | 4 | 0.10575
2025-01-11T06:17:33 | 10000001101000 | 1 | 0 | 37 | 42 | -2 | 25 | 45 | 18 | 218 | 14 | 58 | 1.41 | 4.07 | 22307 | 1293 | 17.7 | 36.5 | 67 | 630 | 0.0654 | 5 | 0.13219
2025-01-11T06:18:33 | 10000001101000 | 1 | 0 | 39 | 45 | -2 | 25 | 45 | 19 | 219 | 14 | 58 | 1.4 | 9.42 | 22307 | 1293 | 17.7 | 36.5 | 67 | 630 | 0.06935 | 6 | 0.1575
2025-01-11T06:19:33 | 10000001101000 | 1 | 0 | 40 | 48 | -2 | 25 | 45 | 23 | 218 | 14 | 58 | 1.39 | 11.39 | 22307 | 1294 | 17.7 | 36.5 | 75 | 630 | 0.083567 | 8 | 0.2085
2025-01-11T06:20:33 | 10000001101000 | 1 | 0 | 42 | 49 | -3 | 25 | 45 | 23 | 218 | 14 | 58 | 1.37 | 10.93 | 22307 | 1294 | 17.7 | 36.5 | 75 | 630 | 0.083567 | 7 | 0.17981
2025-01-11T06:21:33 | 10000001101000 | 1 | 0 | 43 | 50 | -3 | 25 | 45 | 23 | 218 | 14 | 58 | 1.32 | 11.04 | 22307 | 1294 | 17.7 | 36.4 | 73 | 620 | 0.083567 | 7 | 0.17325
2025-01-11T06:22:33 | 10000001101000 | 1 | 0 | 44 | 51 | -3 | 25 | 45 | 23 | 219 | 14 | 58 | 1.31 | 10.46 | 22307 | 1294 | 17.7 | 36.4 | 73 | 610 | 0.08395 | 7 | 0.17194
2025-01-11T06:23:33 | 10000001101000 | 1 | 0 | 45 | 52 | -3 | 25 | 45 | 23 | 219 | 14 | 58 | 1.3 | 10.81 | 22308 | 1294 | 17.7 | 36.4 | 73 | 610 | 0.08395 | 7 | 0.17062
2025-01-11T06:24:33 | 10000001101000 | 1 | 0 | 46 | 53 | -3 | 25 | 45 | 23 | 219 | 14 | 58 | 1.38 | 10.81 | 22308 | 1294 | 17.6 | 36.5 | 73 | 610 | 0.08395 | 7 | 0.18113
2025-01-11T06:25:33 | 10000001101000 | 1 | 0 | 46 | 53 | -3 | 25 | 45 | 23 | 218 | 14 | 58 | 1.39 | 11.28 | 22308 | 1294 | 17.6 | 36.5 | 72 | 610 | 0.083567 | 7 | 0.18244
2025-01-11T06:26:33 | 10000001101000 | 1 | 0 | 47 | 54 | -3 | 25 | 45 | 23 | 218 | 14 | 58 | 1.37 | 10.93 | 22308 | 1294 | 17.7 | 36.6 | 71 | 610 | 0.083567 | 7 | 0.17981
2025-01-11T06:27:33 | 10000001101000 | 1 | 0 | 48 | 54 | -4 | 25 | 45 | 23 | 218 | 14 | 58 | 1.38 | 10.81 | 22308 | 1295 | 17.6 | 36.5 | 71 | 610 | 0.083567 | 6 | 0.15525
2025-01-11T06:28:33 | 10000001101000 | 1 | 0 | 48 | 55 | -4 | 25 | 45 | 24 | 218 | 14 | 58 | 1.38 | 10.81 | 22308 | 1295 | 17.6 | 36.6 | 71 | 600 | 0.0872 | 7 | 0.18113
2025-01-11T06:29:33 | 10000001101000 | 1 | 0 | 48 | 55 | -4 | 25 | 45 | 24 | 219 | 14 | 58 | 1.38 | 11.04 | 22308 | 1295 | 17.6 | 36.6 | 71 | 610 | 0.0876 | 7 | 0.18113
2025-01-11T06:30:33 | 10000001101000 | 1 | 0 | 49 | 56 | -4 | 25 | 45 | 24 | 218 | 14 | 58 | 1.4 | 11.16 | 22308 | 1295 | 17.6 | 36.6 | 72 | 610 | 0.0872 | 7 | 0.18375
2025-01-11T06:31:33 | 10000001101000 | 1 | 0 | 49 | 56 | -4 | 25 | 45 | 24 | 218 | 14 | 58 | 1.37 | 10.58 | 22308 | 1296 | 17.6 | 36.6 | 71 | 610 | 0.0872 | 7 | 0.17981
2025-01-11T06:32:33 | 10000001101000 | 1 | 0 | 50 | 57 | -4 | 25 | 45 | 24 | 219 | 14 | 58 | 1.39 | 10.93 | 22308 | 1296 | 17.6 | 36.6 | 71 | 610 | 0.0876 | 7 | 0.18244
2025-01-11T06:33:33 | 10000001101000 | 1 | 0 | 50 | 57 | -4 | 25 | 45 | 21 | 221 | 14 | 58 | 1.27 | 11.04 | 22308 | 1296 | 17.6 | 36.7 | 64 | 610 | 0.07735 | 7 | 0.16669
2025-01-11T06:34:33 | 10000001101000 | 1 | 0 | 50 | 56 | -4 | 25 | 45 | 21 | 221 | 14 | 58 | 1.15 | 9.18 | 22308 | 1296 | 17.6 | 36.7 | 64 | 610 | 0.07735 | 6 | 0.12937
2025-01-11T06:35:33 | 10000001101000 | 1 | 0 | 49 | 57 | -4 | 25 | 45 | 23 | 220 | 14 | 58 | 1.02 | 8.6 | 22309 | 1297 | 17.6 | 36.6 | 68 | 610 | 0.084333 | 8 | 0.153
2025-01-11T06:36:33 | 10000001101000 | 1 | 0 | 49 | 58 | -4 | 25 | 45 | 23 | 219 | 14 | 58 | 0.93 | 9.65 | 22309 | 1297 | 17.6 | 36.7 | 69 | 600 | 0.08395 | 9 | 0.15694
2025-01-11T06:37:33 | 10000001101000 | 1 | 0 | 49 | 58 | -4 | 25 | 45 | 21 | 220 | 14 | 58 | 0.94 | 9.76 | 22309 | 1297 | 17.6 | 36.7 | 64 | 600 | 0.077 | 9 | 0.15862
2025-01-11T06:38:33 | 10000001101000 | 1 | 0 | 50 | 56 | -4 | 25 | 45 | 18 | 222 | 14 | 58 | 1.03 | 7.09 | 22309 | 1297 | 17.6 | 36.7 | 55 | 610 | 0.0666 | 6 | 0.11588
2025-01-11T06:39:33 | 10000001101000 | 1 | 0 | 49 | 56 | -4 | 25 | 45 | 20 | 220 | 14 | 58 | 1.04 | 7.44 | 22309 | 1297 | 17.6 | 36.7 | 62 | 610 | 0.073333 | 7 | 0.1365
2025-01-11T06:40:33 | 10000001101000 | 1 | 0 | 49 | 58 | -4 | 25 | 45 | 24 | 218 | 14 | 58 | 0.96 | 10.23 | 22309 | 1297 | 17.7 | 36.6 | 69 | 610 | 0.0872 | 9 | 0.162
2025-01-11T06:41:33 | 10000001101000 | 1 | 0 | 49 | 58 | -4 | 25 | 45 | 20 | 219 | 14 | 58 | 0.94 | 9.88 | 22309 | 1297 | 17.6 | 36.6 | 62 | 610 | 0.073 | 9 | 0.15862
2025-01-11T06:42:33 | 10000001101000 | 1 | 0 | 50 | 56 | -4 | 25 | 45 | 17 | 221 | 14 | 58 | 1.05 | 7.32 | 22309 | 1297 | 17.6 | 36.6 | 53 | 610 | 0.062617 | 6 | 0.11812
2025-01-11T06:43:33 | 10000001101000 | 1 | 0 | 50 | 56 | -4 | 25 | 45 | 18 | 220 | 14 | 58 | 1.05 | 7.32 | 22309 | 1298 | 17.7 | 36.6 | 55 | 610 | 0.066 | 6 | 0.11812
2025-01-11T06:44:33 | 10000001101000 | 1 | 0 | 49 | 57 | -4 | 25 | 45 | 23 | 218 | 14 | 58 | 0.96 | 8.37 | 22309 | 1298 | 17.6 | 36.7 | 67 | 610 | 0.083567 | 8 | 0.144
2025-01-11T06:45:33 | 10000001101000 | 1 | 0 | 49 | 58 | -4 | 25 | 45 | 20 | 219 | 14 | 58 | 0.91 | 9.65 | 22309 | 1298 | 17.6 | 36.6 | 63 | 610 | 0.073 | 9 | 0.15356
2025-01-11T06:46:33 | 10000001101000 | 1 | 0 | 49 | 56 | -4 | 25 | 45 | 16 | 220 | 14 | 58 | 0.93 | 6.86 | 22309 | 1298 | 17.7 | 36.6 | 51 | 610 | 0.058667 | 7 | 0.12206
2025-01-11T06:47:33 | 10000001101000 | 1 | 0 | 49 | 55 | -4 | 25 | 45 | 18 | 219 | 14 | 58 | 0.94 | 7.09 | 22310 | 1298 | 17.6 | 36.6 | 56 | 610 | 0.0657 | 6 | 0.10575
2025-01-11T06:48:33 | 10000001101000 | 1 | 0 | 49 | 56 | -4 | 25 | 45 | 22 | 218 | 14 | 58 | 0.92 | 8.14 | 22310 | 1298 | 17.6 | 36.6 | 65 | 610 | 0.079933 | 7 | 0.12075
2025-01-11T06:49:33 | 10000001101000 | 1 | 0 | 49 | 58 | -4 | 25 | 45 | 19 | 220 | 14 | 58 | 0.93 | 9.53 | 22310 | 1298 | 17.7 | 36.5 | 60 | 610 | 0.069667 | 9 | 0.15694
2025-01-11T06:50:33 | 10000001101000 | 1 | 0 | 49 | 56 | -4 | 25 | 45 | 16 | 221 | 14 | 58 | 0.94 | 7.09 | 22310 | 1298 | 17.7 | 36.6 | 51 | 610 | 0.058933 | 7 | 0.12337
2025-01-11T06:51:33 | 10000001101000 | 1 | 0 | 49 | 56 | -4 | 25 | 45 | 18 | 220 | 14 | 58 | 0.96 | 7.44 | 22310 | 1299 | 17.6 | 36.6 | 55 | 610 | 0.066 | 7 | 0.126
2025-01-11T06:52:33 | 10000001101000 | 1 | 0 | 49 | 57 | -4 | 25 | 45 | 22 | 219 | 14 | 58 | 0.93 | 8.6 | 22310 | 1299 | 17.7 | 36.6 | 65 | 610 | 0.0803 | 8 | 0.1395
2025-01-11T06:53:33 | 1010000001101000 | 1 | 0 | 49 | 51 | -4 | 25 | 45 | 4 | 224 | 14 | 58 | 0.94 | 3.95 | 22310 | 1299 | 17.7 | 36.6 | 29 | 480 | 0.014933 | 2 | 0.03525
2025-01-11T06:54:33 | 1010000001101000 | 1 | 0 | 48 | 45 | -3 | 25 | 45 | 2 | 226 | 14 | 58 | 1.41 | 3.95 | 22310 | 1299 | 17.7 | 36.6 | 35 | 0 | 0.0075333 | -3 | -0.079312
2025-01-11T06:55:33 | 1010000001101000 | 1 | 0 | 45 | 37 | -2 | 25 | 45 | 2 | 226 | 14 | 58 | 1.43 | 3.95 | 22310 | 1299 | 17.7 | 36.5 | 37 | 0 | 0.0075333 | -8 | -0.2145
2025-01-11T06:56:33 | 1010000001101000 | 1 | 0 | 40 | 27 | -1 | 25 | 45 | 6 | 224 | 14 | 58 | 1.44 | 3.95 | 22310 | 1299 | 17.7 | 36.5 | 37 | 0 | 0.0224 | -13 | -0.351
2025-01-11T06:57:33 | 10000001101000 | 1 | 0 | 35 | 33 | 1 | 25 | 45 | 5 | 224 | 14 | 58 | 1.45 | 3.95 | 22310 | 1299 | 17.7 | 36.5 | 29 | 370 | 0.018667 | -2 | -0.054375
2025-01-11T06:58:33 | 10000001101000 | 1 | 0 | 36 | 38 | 1 | 25 | 45 | 9 | 224 | 14 | 58 | 1.43 | 3.95 | 22310 | 1299 | 17.7 | 36.4 | 41 | 550 | 0.0336 | 2 | 0.053625
2025-01-11T06:59:33 | 10000001101000 | 1 | 0 | 36 | 40 | 0 | 25 | 45 | 14 | 222 | 14 | 58 | 1.43 | 3.95 | 22310 | 1299 | 17.7 | 36.4 | 55 | 550 | 0.0518 | 4 | 0.10725
|  |  |  | 46.1667 | 51.2333 |  |  |  | 17.2167 | 220.3667 |  |  | 1.1713 |  | 4 | 7 |  |  |  |  | 4.4769 |  | 6.6766 | 1.4913
These are the Midea
rounded 'running totals', end of hour minus start of hour provides a sanity check on the calculated values
Mean values for the hour for variables shown
The calculated values in row 62
are the values that apear in the
hour data file (calculated by a
python script). The other minute
rows are the minute values,
normally bever seen but added here for interest's sake. Sums aren't identical to calculated value due to rounding errors. Note how during defrosts the energy out goes negative, relecting the fact energy is flowing the 'wrong way'. Also note that strictly speaking these values are kW (power) for each minute but when summed over the hour they become energy (kWh), 4.48kW for one hour is 4.48kWh etc
60m
trailing
COP