## Full List of Parameters
Modbus Address | Register Type | Level | Group | Code | Function_Description | Default | Min | Max | Unit | Read Value | Remarks
0 | Input | U | 1 | 0 | Return water temperature | - | -20 | 100 | 1°C | 19 | monitor display No.d0
1 | Input | U | 1 | 1 | Compressor operating frequency | - | 0 | 200 | 1Hz | 0 | monitor display No.d1
2 | Input | U | 1 | 2 | Discharge temperature | - | -20 | 150 | 1°C | 20 | monitor display No.d2
3 | Input | U | 1 | 3 | Current consumption value | - | 0 | 9900 | 100W | 0 | monitor display No.d3
4 | Input | U | 1 | 4 | Fan control number of rotation | - | 0 | 1000 | 10rpm | 0
5 | Input | U | 1 | 5 | Defrost temperature | - | -20 | 100 | 1°C | 16 | monitor display No.d5
6 | Input | U | 1 | 6 | Outdoor air temperature | - | -20 | 100 | 1°C | 18 | monitor display No.d6
7 | Input | U | 1 | 7 | Water pump control number of rotation | - | 0 | 9900 | 100rpm | 0 | monitor display No.d7
8 | Input | U | 1 | 8 | Suction temperature | - | -20 | 100 | 1°C | 19 | monitor display No.d8
9 | Input | U | 1 | 9 | Outgoing water temperature | - | -20 | 100 | 1°C | 21 | monitor display No.d9
10 | Input | U | 1 | 10 | Selected operating mode (0=Heating/Cooling OFF, 1=Heating, 2=Cooling) | 0 | 0 | 2 | - | 0 | Set by Remote controller or remote contact
11 | Input | U | 1 | 11 | Room air set temperature of Zone1(Master) | 25 | 12 | 40 | 0.5°C | 200 | Set by Master Remote controller
12 | Input | U | 1 | 12 | Room air set temperature of Zone2(Slave) | 25 | 12 | 40 | 0.5°C | 250 | Set by Slave Remote controller
13 | Input | U | 1 | 13 | Selected DHW operating mode (0=disable, 1=Comfort, 2=Economy, 3=Force) | 0 | 0 | 3 | - | 0 | Set by Remote controller
14 | Input | U | 1 | 14 | Day (0=Monday, 1=Tuesday, 2=Wednesday, 3=Thursday, 4=Friday, 5=Saturday, 6=Sunday) | 0 | 0 | 6 | - | 0
15 | Input | U | 1 | 15 | Clock | 12:00 | 0:00 | 23:59 | 1min | 0
|  | U | 1 | 16 | Heating/Cooling time bands setting Zone1 (0=disable, 1=active (Comfort or Economy)) | 0 | 0 | 1 | -
|  | U | 1 | 17 | Heating/Cooling time bands setting Zone2 (0=disable, 1=active (Comfort or Economy)) | 0 | 0 | 1 | -
|  | U | 1 | 18 | DHW time band setting (0=disable, 1=enable) | 0 | 0 | 1 | -
|  | U | 1 | 19 | Low tariff and Night mode setting (0=disable, 1=Low tariff, 2=Night mode, 3=Low tariff and Night mode) | 0 | 0 | 3 | - |  | Set by Remote controller or remote contact
|  | U | 1 | 20 | Room relative humidity value | - | 0 | 100 | 1%
|  | I | 1 | 21 | Integration electricity time | - | 0 | 9999 | x100Hr
|  | I | 1 | 22 | Integration operation time | - | 0 | 9999 | x100Hr
|  | I | 1 | 23 | Integration Heating operation time | - | 0 | 9999 | x100Hr
|  | I | 1 | 24 | Integration Cooling operation time | - | 0 | 9999 | x100Hr
|  | I | 1 | 25 | Integration DHW operation time | - | 0 | 9999 | x100Hr
|  | I | 1 | 26 | Software version number of Main PCB | - | 0 | 9999 | -
|  | I | 1 | 27 | Software version number of Control PCB | - | 0 | 9999 | -
|  | I | 1 | 28 | Software version number of Remote controller (Master) | - | 0 | 9999 | -
|  | I | 1 | 29 | Software version number of Remote controller (Slave) | - | 0 | 9999 | -
16 | Input | I | 1 | 31 | DHW tank temperature (Terminal 7-8) | - | -20 | 100 | 0.5°C | 470
17 | Input | I | 1 | 32 | Outdoor air temperature (Terminal 9-10) | - | -20 | 100 | 0.5°C | 65336
18 | Input | I | 1 | 33 | Buffer tank temperature (Terminal 11-12) | - | -20 | 100 | 0.5°C | 65336
19 | Input | I | 1 | 34 | Mix water temperature (Terminal 13-14) | - | -20 | 100 | 0.5°C | 65336
20 | Input | I | 1 | 35 | Humidity sensor (Terminal 17-18) | - | 0 | 100 | 1% | 0
|  | I | 1 | 36 | DHW remote contact (Terminal 18-19) (0=open, 1=close) | - | 0 | 1 | -
|  | I | 1 | 37 | Configurable input (Terminal 20-21) (0=open, 1=close) | - | 0 | 1 | -
|  | I | 1 | 38 | Dual set point control (Terminal 22-23) (0=open, 1=close) | - | 0 | 1 | -
|  | I | 1 | 39 | Heating/Cooling mode remote contact (Terminal 24-25) (0=open, 1=close) | - | 0 | 1 | -
|  | I | 1 | 40 | Flow switch (Terminal 26-27) (0=open, 1=close) | - | 0 | 1 | -
|  | I | 1 | 41 | Night mode (Terminal 28-29) (0=open, 1=close) | - | 0 | 1 | -
|  | I | 1 | 42 | Low tariff (Terminal 30-31) (0=open, 1=close) | - | 0 | 1 | -
21 | Input | I | 1 | 50? | ?Current error code |  |  |  |  | 32381
22 | Input | I | 1 | 51? | ?Error code once before | -32539 |  |  |  | 33004
23 | Input | I | 1 | 52? | ?Error code twice before | -32540 |  |  |  | 32995
24 | Input | I | 1 | 53? | ?Error code three times before | -32541 |  |  |  | 32994
25 | Input | I | 1 | 54? | ?Error code four times before | -32542 |  |  |  | 32993
26 | Input | I | 1 | 55? | ?Error code five times before | -32543 |  |  |  | 32993
27 | Input | I | 1 | 56? | ?Error code six times before | -32591 |  |  |  | 32993
28 | Input | I | 1 | 57? | ?Error code seven times before | 32381 |  |  |  | 32993
29 | Input | I | 1 | 58? | ?Error code eight times before | 32381 |  |  |  | 32993
30 | Input | I | 1 | 59? | ?Error code nine times before | 32381 |  |  |  | 32993
31 | Input | I | 1 | 60? | ?Error code ten times before | 32381 |  |  |  | 32993
32 | Input | U | 1 | 72 | Plate heat exchanger temperature | - | -20 | 100 | 1°C | 20 | monitor display No.d4
|  | I | 2 | 1 | Adjust the temperature read by the sensor in Remote controller | 0 | -5 | 5 | 0.1°C |  | Master/Slave Remote controller
|  | U | 2 | 2 | Sound ON/OFF of buzzer (0=OFF, 1=ON) | 1 | 0 | 1 | - |  | Master/Slave Remote controller
|  | U | 2 | 3 | Back light display at door open (0=OFF, 1=ON) | 1 | 0 | 1 | - |  | Master/Slave Remote controller
|  | U | 2 | 4 | Time to turn off the back light | 60 | 10 | 300 | 10sec |  | Master/Slave Remote controller
|  | U | 2 | 5 | Time to back to normal indication | 120 | 10 | 300 | 10sec |  | Master/Slave Remote controller
|  | U | 2 | 6 | Long pressing time to accept the button | 3 | 2 | 5 | 1sec |  | Master/Slave Remote controller
|  | I | 2 | 11 | Adjust the temperature read by the sensor in Remote controller | 0 | -5 | 5 | 0.1°C |  | Slave Remote controller
|  | U | 2 | 12 | Sound ON/OFF of buzzer (0=OFF, 1=ON) | 1 | 0 | 1 | - |  | Slave Remote controller
|  | U | 2 | 13 | Back light display at door open (0=OFF, 1=ON) | 1 | 0 | 1 | - |  | Slave Remote controller
|  | U | 2 | 14 | Time to turn off the back light | 60 | 10 | 300 | 10sec |  | Slave Remote controller
|  | U | 2 | 15 | Time to back to normal indication | 120 | 10 | 300 | 10sec |  | Slave Remote controller
1 | Coil | I | 3 | 0 | Operation at the time of reboot after blackout 0 = disable 1 = enable | 1
|  | I | 4 | 0 | Which Remote controller will measure the Room air temperature to stop Fan coil System (0=Master Remote controller, 1=Slave Remote controller, 2=Master or Slave Remote controller) | 0 | 0 | 2 | -
|  | I | 4 | 1 | Hysteresis of Room air temperature to restart Fan coil system | 1 | 0.5 | 10 | 0.5°C
|  | I | 11 | 0 | Time band is ON/OFF on Monday (0=OFF, 1=ON) | 0 | 0 | 1 | -
|  | I | 11 | 1 | Comfort room set temperature on Monday | 20 | 12 | 40 | 0.5°C
|  | I | 11 | 2 | Economy room set temperature on Monday | 18 | 12 | 40 | 0.5°C
|  | I | 11 | 3 | 1st ON time on Monday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 4 | 1st OFF time on Monday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 5 | 2nd ON time on Monday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 6 | 2nd OFF time on Monday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 7 | 3rd ON time on Monday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 8 | 3rd OFF time on Monday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 10 | Time band is ON/OFF on Tuesday (0=OFF, 1=ON) | 0 | 0 | 1 | -
|  | I | 11 | 11 | Comfort room set temperature on Tuesday | 20 | 12 | 40 | 0.5°C
|  | I | 11 | 12 | Economy room set temperature on Tuesday | 18 | 12 | 40 | 0.5°C
|  | I | 11 | 13 | 1st ON time on Tuesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 14 | 1st OFF time on Tuesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 15 | 2nd ON time on Tuesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 16 | 2nd OFF time on Tuesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 17 | 3rd ON time on Tuesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 18 | 3rd OFF time on Tuesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 20 | Time band is ON/OFF on Wednesday (0=OFF, 1=ON) | 0 | 0 | 1 | -
|  | I | 11 | 21 | Comfort room set temperature on Wednesday | 20 | 12 | 40 | 0.5°C
|  | I | 11 | 22 | Economy room set temperature on Wednesday | 18 | 12 | 40 | 0.5°C
|  | I | 11 | 23 | 1st ON time on Wednesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 24 | 1st OFF time on Wednesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 25 | 2nd ON time on Wednesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 26 | 2nd OFF time on Wednesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 27 | 3rd ON time on Wednesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 28 | 3rd OFF time on Wednesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 30 | Time band is ON/OFF on Thursday (0=OFF, 1=ON) | 0 | 0 | 1 | -
|  | I | 11 | 31 | Comfort room set temperature on Thursday | 20 | 12 | 40 | 0.5°C
|  | I | 11 | 32 | Economy room set temperature on Thursday | 18 | 12 | 40 | 0.5°C
|  | I | 11 | 33 | 1st ON time on Thursday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 34 | 1st OFF time on Thursday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 35 | 2nd ON time on Thursday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 36 | 2nd OFF time on Thursday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 37 | 3rd ON time on Thursday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 38 | 3rd OFF time on Thursday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 40 | Time band is ON/OFF on Friday (0=OFF, 1=ON) | 0 | 0 | 1 | -
|  | I | 11 | 41 | Comfort room set temperature on Friday | 20 | 12 | 40 | 0.5°C
|  | I | 11 | 42 | Economy room set temperature on Friday | 18 | 12 | 40 | 0.5°C
|  | I | 11 | 43 | 1st ON time on Friday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 44 | 1st OFF time on Friday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 45 | 2nd ON time on Friday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 46 | 2nd OFF time on Friday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 47 | 3rd ON time on Friday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 48 | 3rd OFF time on Friday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 50 | Time band is ON/OFF on Saturday (0=OFF, 1=ON) | 0 | 0 | 1 | -
|  | I | 11 | 51 | Comfort room set temperature on Saturday | 20 | 12 | 40 | 0.5°C
|  | I | 11 | 52 | Economy room set temperature on Saturday | 18 | 12 | 40 | 0.5°C
|  | I | 11 | 53 | 1st ON time on Saturday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 54 | 1st OFF time on Saturday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 55 | 2nd ON time on Saturday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 56 | 2nd OFF time on Saturday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 57 | 3rd ON time on Saturday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 58 | 3rd OFF time on Saturday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 60 | Time band is ON/OFF on Sunday (0=OFF, 1=ON) | 0 | 0 | 1 | -
|  | I | 11 | 61 | Comfort room set temperature on Sunday | 20 | 12 | 40 | 0.5°C
|  | I | 11 | 62 | Economy room set temperature on Sunday | 18 | 12 | 40 | 0.5°C
|  | I | 11 | 63 | 1st ON time on Sunday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 64 | 1st OFF time on Sunday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 65 | 2nd ON time on Sunday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 66 | 2nd OFF time on Sunday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 67 | 3rd ON time on Sunday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 68 | 3rd OFF time on Sunday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 70 | Time band is ON/OFF on Weekday (5days) (0=OFF, 1=ON) | 0 | 0 | 1 | -
|  | I | 11 | 71 | Comfort room set temperature on Weekday (5days) | 20 | 12 | 40 | 0.5°C
|  | I | 11 | 72 | Economy room set temperature on Weekday (5days) | 18 | 12 | 40 | 0.5°C
|  | I | 11 | 73 | 1st ON time on Weekday (5days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 74 | 1st OFF time on Weekday (5days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 75 | 2nd ON time on Weekday (5days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 76 | 2nd OFF time on Weekday (5days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 77 | 3rd ON time on Weekday (5days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 78 | 3rd OFF time on Weekday (5days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 80 | Time band is ON/OFF on Weekend (2days) (0=OFF, 1=ON) | 0 | 0 | 1 | -
|  | I | 11 | 81 | Comfort room set temperature on Weekend (2days) | 20 | 12 | 40 | 0.5°C
|  | I | 11 | 82 | Economy room set temperature on Weekend (2days) | 18 | 12 | 40 | 0.5°C
|  | I | 11 | 83 | 1st ON time on Weekend (2days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 84 | 1st OFF time on Weekend (2days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 85 | 2nd ON time on Weekend (2days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 86 | 2nd OFF time on Weekend (2days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 87 | 3rd ON time on Weekend (2days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 88 | 3rd OFF time on Weekend (2days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 90 | Time band is ON/OFF on Everyday (7days) (0=OFF, 1=ON) | 0 | 0 | 1 | -
|  | I | 11 | 91 | Comfort room set temperature on Everyday (7days) | 20 | 12 | 40 | 0.5°C
|  | I | 11 | 92 | Economy room set temperature on Everyday (7days) | 18 | 12 | 40 | 0.5°C
|  | I | 11 | 93 | 1st ON time on Everyday (7days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 94 | 1st OFF time on Everyday (7days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 95 | 2nd ON time on Everyday (7days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 96 | 2nd OFF time on Everyday (7days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 97 | 3rd ON time on Everyday (7days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 11 | 98 | 3rd OFF time on Everyday (7days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 0 | Time band is ON/OFF on Monday (0=OFF, 1=ON) | 0 | 0 | 1 | -
|  | I | 12 | 1 | Comfort room set temperature on Monday | 20 | 12 | 40 | 0.5°C
|  | I | 12 | 2 | Economy room set temperature on Monday | 18 | 12 | 40 | 0.5°C
|  | I | 12 | 3 | 1st ON time on Monday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 4 | 1st OFF time on Monday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 5 | 2nd ON time on Monday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 6 | 2nd OFF time on Monday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 7 | 3rd ON time on Monday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 8 | 3rd OFF time on Monday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 10 | Time band is ON/OFF on Tuesday (0=OFF, 1=ON) | 0 | 0 | 1 | -
|  | I | 12 | 11 | Comfort room set temperature on Tuesday | 20 | 12 | 40 | 0.5°C
|  | I | 12 | 12 | Economy room set temperature on Tuesday | 18 | 12 | 40 | 0.5°C
|  | I | 12 | 13 | 1st ON time on Tuesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 14 | 1st OFF time on Tuesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 15 | 2nd ON time on Tuesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 16 | 2nd OFF time on Tuesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 17 | 3rd ON time on Tuesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 18 | 3rd OFF time on Tuesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 20 | Time band is ON/OFF on Wednesday (0=OFF, 1=ON) | 0 | 0 | 1 | -
|  | I | 12 | 21 | Comfort room set temperature on Wednesday | 20 | 12 | 40 | 0.5°C
|  | I | 12 | 22 | Economy room set temperature on Wednesday | 18 | 12 | 40 | 0.5°C
|  | I | 12 | 23 | 1st ON time on Wednesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 24 | 1st OFF time on Wednesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 25 | 2nd ON time on Wednesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 26 | 2nd OFF time on Wednesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 27 | 3rd ON time on Wednesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 28 | 3rd OFF time on Wednesday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 30 | Time band is ON/OFF on Thursday (0=OFF, 1=ON) | 0 | 0 | 1 | -
|  | I | 12 | 31 | Comfort room set temperature on Thursday | 20 | 12 | 40 | 0.5°C
|  | I | 12 | 32 | Economy room set temperature on Thursday | 18 | 12 | 40 | 0.5°C
|  | I | 12 | 33 | 1st ON time on Thursday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 34 | 1st OFF time on Thursday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 35 | 2nd ON time on Thursday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 36 | 2nd OFF time on Thursday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 37 | 3rd ON time on Thursday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 38 | 3rd OFF time on Thursday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 40 | Time band is ON/OFF on Friday (0=OFF, 1=ON) | 0 | 0 | 1 | -
|  | I | 12 | 41 | Comfort room set temperature on Friday | 20 | 12 | 40 | 0.5°C
|  | I | 12 | 42 | Economy room set temperature on Friday | 18 | 12 | 40 | 0.5°C
|  | I | 12 | 43 | 1st ON time on Friday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 44 | 1st OFF time on Friday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 45 | 2nd ON time on Friday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 46 | 2nd OFF time on Friday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 47 | 3rd ON time on Friday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 48 | 3rd OFF time on Friday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 50 | Time band is ON/OFF on Saturday (0=OFF, 1=ON) | 0 | 0 | 1 | -
|  | I | 12 | 51 | Comfort room set temperature on Saturday | 20 | 12 | 40 | 0.5°C
|  | I | 12 | 52 | Economy room set temperature on Saturday | 18 | 12 | 40 | 0.5°C
|  | I | 12 | 53 | 1st ON time on Saturday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 54 | 1st OFF time on Saturday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 55 | 2nd ON time on Saturday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 56 | 2nd OFF time on Saturday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 57 | 3rd ON time on Saturday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 58 | 3rd OFF time on Saturday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 60 | Time band is ON/OFF on Sunday (0=OFF, 1=ON) | 0 | 0 | 1 | -
|  | I | 12 | 61 | Comfort room set temperature on Sunday | 20 | 12 | 40 | 0.5°C
|  | I | 12 | 62 | Economy room set temperature on Sunday | 18 | 12 | 40 | 0.5°C
|  | I | 12 | 63 | 1st ON time on Sunday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 64 | 1st OFF time on Sunday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 65 | 2nd ON time on Sunday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 66 | 2nd OFF time on Sunday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 67 | 3rd ON time on Sunday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 68 | 3rd OFF time on Sunday | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 70 | Time band is ON/OFF on Weekday (5days) (0=OFF, 1=ON) | 0 | 0 | 1 | -
|  | I | 12 | 71 | Comfort room set temperature on Weekday (5days) | 20 | 12 | 40 | 0.5°C
|  | I | 12 | 72 | Economy room set temperature on Weekday (5days) | 18 | 12 | 40 | 0.5°C
|  | I | 12 | 73 | 1st ON time on Weekday (5days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 74 | 1st OFF time on Weekday (5days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 75 | 2nd ON time on Weekday (5days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 76 | 2nd OFF time on Weekday (5days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 77 | 3rd ON time on Weekday (5days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 78 | 3rd OFF time on Weekday (5days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 80 | Time band is ON/OFF on Weekend (2days) (0=OFF, 1=ON) | 0 | 0 | 1 | -
|  | I | 12 | 81 | Comfort room set temperature on Weekend (2days) | 20 | 12 | 40 | 0.5°C
|  | I | 12 | 82 | Economy room set temperature on Weekend (2days) | 18 | 12 | 40 | 0.5°C
|  | I | 12 | 83 | 1st ON time on Weekend (2days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 84 | 1st OFF time on Weekend (2days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 85 | 2nd ON time on Weekend (2days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 86 | 2nd OFF time on Weekend (2days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 87 | 3rd ON time on Weekend (2days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 88 | 3rd OFF time on Weekend (2days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 90 | Time band is ON/OFF on Everyday (7days) (0=OFF, 1=ON) | 0 | 0 | 1 | -
|  | I | 12 | 91 | Comfort room set temperature on Everyday (7days) | 20 | 12 | 40 | 0.5°C
|  | I | 12 | 92 | Economy room set temperature on Everyday (7days) | 18 | 12 | 40 | 0.5°C
|  | I | 12 | 93 | 1st ON time on Everyday (7days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 94 | 1st OFF time on Everyday (7days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 95 | 2nd ON time on Everyday (7days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 96 | 2nd OFF time on Everyday (7days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 97 | 3rd ON time on Everyday (7days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 12 | 98 | 3rd OFF time on Everyday (7days) | 0:00 | 0:00 | 24:00 | 15min
|  | I | 13 | 1 | DHW Comfort 1st ON time | 0:00 | 0:00 | 24:00 | 15min
|  | I | 13 | 2 | DHW Comfort 1st OFF time | 0:00 | 0:00 | 24:00 | 15min
|  | I | 13 | 3 | DHW Comfort 2nd ON time | 0:00 | 0:00 | 24:00 | 15min
|  | I | 13 | 4 | DHW Comfort 2nd OFF time | 0:00 | 0:00 | 24:00 | 15min
|  | I | 13 | 5 | DHW Comfort 3rd ON time | 0:00 | 0:00 | 24:00 | 15min
|  | I | 13 | 6 | DHW Comfort 3rd OFF time | 0:00 | 0:00 | 24:00 | 15min
|  | I | 13 | 11 | Low tariff 1st ON time | 0:00 | 0:00 | 24:00 | 15min
|  | I | 13 | 12 | Low tariff 1st OFF time | 0:00 | 0:00 | 24:00 | 15min
|  | I | 13 | 13 | Low tariff 2nd ON time | 0:00 | 0:00 | 24:00 | 15min
|  | I | 13 | 14 | Low tariff 2nd OFF time | 0:00 | 0:00 | 24:00 | 15min
|  | I | 13 | 15 | Low tariff 3rd ON time | 0:00 | 0:00 | 24:00 | 15min
|  | I | 13 | 16 | Low tariff 3rd OFF time | 0:00 | 0:00 | 24:00 | 15min
|  | I | 13 | 21 | Night mode 1st ON time | 0:00 | 0:00 | 24:00 | 15min
|  | I | 13 | 22 | Night mode 1st OFF time | 0:00 | 0:00 | 24:00 | 15min
|  | I | 13 | 23 | Night mode 2nd ON time | 0:00 | 0:00 | 24:00 | 15min
|  | I | 13 | 24 | Night mode 2nd OFF time | 0:00 | 0:00 | 24:00 | 15min
|  | I | 13 | 25 | Night mode 3rd ON time | 0:00 | 0:00 | 24:00 | 15min
|  | I | 13 | 26 | Night mode 3rd OFF time | 0:00 | 0:00 | 24:00 | 15min
2 | Coil | I | 21 | 0 | Heating Zone1, enable Outgoing water set point (0=Fixed set point, 1=Climatic curve) | 0 | 0 | 1 | -
2 | Holding | I | 21 | 1 | Heating Zone1, Fixed Outgoing water set point in Heating | 45 | 23 | 60 | 0.5°C | 255
3 | Holding | I | 21 | 2 | Max. Outgoing water temperature in Heating mode (Tm1) Zone1 | 45 | 23 | 60 | 0.5°C | 300
4 | Holding | I | 21 | 3 | Min. Outgoing water temperature in Heating mode (Tm2) Zone1 | 30 | 23 | 60 | 0.5°C | 230
5 | Holding | I | 21 | 4 | Min. Outdoor air temperature corresponding to max. Outgoing water temperature (Te1) Zone1 | 0 | -20 | 50 | 0.5°C | 65506
6 | Holding | I | 21 | 5 | Max. Outdoor air temperature corresponding to max. Outgoing water temperature (Te2) Zone1 | 20 | 0 | 40 | 0.5°C | 160
3 | Coil | I | 21 | 10 | Heating Zone2, enable Outgoing water set point (0=Fixed set point, 1=Climatic curve enabled) | 0 | 0 | 1 | -
7 | Holding | I | 21 | 11 | Heating Zone2, Fixed Outgoing water set point in Heating | 45 | 23 | 60 | 0.5°C | 450
8 | Holding | I | 21 | 12 | Max. Outgoing water temperature in Heating mode (Tm1) Zone2 | 45 | 23 | 60 | 0.5°C | 450
9 | Holding | I | 21 | 13 | Min. Outgoing water temperature in Heating mode (Tm2) Zone2 | 30 | 23 | 60 | 0.5°C | 300
10 | Holding | I | 21 | 14 | Min. Outdoor air temperature corresponding to max. Outgoing water temperature (Te1) Zone2 | 0 | -20 | 50 | 0.5°C | 0
11 | Holding | I | 21 | 15 | Max. Outdoor air temperature corresponding to max. Outgoing water temperature (Te2) Zone2 | 20 | 0 | 40 | 0.5°C | 200
4 | Coil | I | 21 | 20 | Cooling Zone1, enable Outgoing water set point (0=Fixed set point, 1=Climatic curve enabled) | 0 | 0 | 1 | -
12 | Holding | I | 21 | 21 | Cooling Zone1, Fixed Outgoing water set point in Cooling | 7 | 7 | 23 | 0.5°C | 70
13 | Holding | I | 21 | 22 | Max. Outgoing water temperature in Cooling mode (Tm1) Zone1 | 20 | 7 | 23 | 0.5°C | 200
14 | Holding | I | 21 | 23 | Min. Outgoing water temperature in Cooling mode (Tm2) Zone1 | 18 | 7 | 23 | 0.5°C | 180
15 | Holding | I | 21 | 24 | Min. Outdoor air temperature corresponding to max. Outgoing water temperature (Te1) Zone1 | 25 | 0 | 50 | 0.5°C | 250
16 | Holding | I | 21 | 25 | Max. Outdoor air temperature corresponding to max. Outgoing water temperature (Te2) Zone1 | 35 | 0 | 50 | 0.5°C | 350
5 | Coil | I | 21 | 30 | Cooling Zone2, enable Outgoing water set point (0=Fixed set point, 1=Climatic Curve Enabled) | 0 | 0 | 1 | -
17 | Holding | I | 21 | 31 | Cooling Zone2, Fixed Outgoing water set point in Cooling | 7 | 7 | 23 | 0.5°C | 70
18 | Holding | I | 21 | 32 | Max. Outgoing water temperature in Cooling mode (Tm1) Zone2 | 20 | 7 | 23 | 0.5°C | 200
19 | Holding | I | 21 | 33 | Min. Outgoing water temperature in Cooling mode (Tm2) Zone2 | 18 | 7 | 23 | 0.5°C | 180
20 | Holding | I | 21 | 34 | Min. Outdoor air temperature corresponding to max. Outgoing water temperature (Te1) Zone2 | 25 | 0 | 50 | 0.5°C | 250
21 | Holding | I | 21 | 35 | Max. Outdoor air temperature corresponding to max. Outgoing water temperature (Te2) Zone2 | 35 | 0 | 50 | 0.5°C | 350
22 | Holding | I | 21 | 41 | Hysteresis of water set point in Heating and DHW | 8 | 0.5 | 10 | 0.5°C | 40
23 | Holding | I | 21 | 42 | Hysteresis of water set point in Cooling | 8 | 0.5 | 10 | 0.5°C | 80
24 | Holding | I | 21 | 51 | Low tariff deferential water set point for Heating | 5 | 0 | 60 | 0.5°C | 50
25 | Holding | I | 21 | 52 | Low tariff deferential water set point for Cooling | 5 | 0 | 60 | 0.5°C | 50
99 | Holding | I | 21 | 61 | Buffer tank set point for Heating | 45 | 23 | 60 | 0.5°C
100 | Holding | I | 21 | 62 | Buffer tank set point for Cooling | 7 | 7 | 23 | 0.5°C
26 | Holding | I | 31 | 1 | DHW production priority setting (0=DHW is unavailable, 1=DHW is available and priority DHW over space Heating, 2=DHW is available and priority space Heating over DHW) | 0 | 0 | 2 | - | 1
27 | Holding | I | 31 | 2 | Type of configuration to heat the DHW (0=Heat pump + Heater, 1=Heat pump only, 2=Heater only) | 1 | 0 | 2 | - | 1
28 | Holding | I | 31 | 11 | DHW Comfort set temperature | 50 | 40 | 60 | 0.5°C | 470
29 | Holding | I | 31 | 12 | DHW Economy set temperature | 40 | 30 | 50 | 0.5°C | 430
30 | Holding | I | 31 | 13 | DHW set point hysteresis | 3 | 0.5 | 10 | 0.5°C | 30
31 | Holding | I | 31 | 14 | DHW Over boost mode set point | 60 | 50 | 90 | 0.5°C | 600
|  | I | 31 | 15 | DHW Over boost mode set point hysteresis | 5 | 0.5 | 10 | 0.5°C
32 | Holding | I | 31 | 21 | Max. time for DHW request | 60 | 0 | 900 | 1min | 60
|  | I | 31 | 22 | Min. time for space Heating/Cooling | 15 | 0 | 900 | 1min
33 | Holding | I | 31 | 31 | Delay time on DHW heater from OFF compressor | 30 |  |  | 1min | 30
|  | I | 31 | 32 | Conditions to be available DHW heaters (0=always enabled, 1=depends on Outdoor air temperature) | 1 | 0 | 1 | -
34 | Holding | I | 31 | 33 | Outdoor air temperature to enable DHW heaters | -5 | -20 | 20 | 0.5°C | 65486
35 | Holding | I | 31 | 34 | Outdoor air temperature hysteresis to disable DHW heaters | 5 | 0.5 | 10 | 0.5°C | 50
36 | Holding | S | 31 | 44 | Anti-legionella set point |  |  |  | 0.5°C | 650
6 | coil | I | 31 | 40 | Anti-legionella function (0=disable, 1=enable) | 0 | 0 | 1 | -
|  | I | 31 | 41 | Anti-legionella operation day of week (0=Mon, 1=Tue, 2=Wed, 3=Thu, 4=Fri, 5=Sat, 6=Sun) | 0 | 0 | 6 | -
|  | I | 31 | 42 | Start time of the day at which the DHW should be heated for Anti-legionella | 1:00 | 0:00 | 23:00 | 1:00
7 | Coil | I | 41 | 0 | The HP unit turns ON/OFF based on (0=Room set point, 1=Water set point) | 1 | 0 | 1 | -
|  | I | 41 | 1 | Hysteresis of Heating Room air set point | 0.5 | 0.5 | 5 | 0.5°C
|  | I | 41 | 2 | Hysteresis of Cooling Room air set point | 0.5 | 0.5 | 5 | 0.5°C
37 | Holding | I | 41 | 11 | Max. frequency of Night mode | 80 | 50 | 100 | 5% | 80
38 | Holding | I | 41 | 21 | Min. time compressor ON/OFF time | 0 | 0 | 0 | 1sec | 0
39 | Holding | I | 41 | 22 | Delay time pump OFF from compressor OFF | 30 | 0 | 900 | 1sec | 30
40 | Holding | I | 41 | 23 | Delay time compressor ON from pump ON | 30 | 0 | 900 | 1sec | 30
41 | Holding | I | 42 | 0 | Type of configuration of Main water pump (0=always ON, 1=ON/OFF based on Buffer tank temperature, 2=ON/OFF based on Sniffing cycles) | 0 | 0 | 2 | - | 0 | To be set to the following combinations Par5111=0 > Par4200=0 or 2 Par5111=1 > Par4200=0 or 1 or 2
42 | Holding | I | 42 | 1 | Time ON Main water pump for Sniffing cycle | 3 | 1 | 15 | 1min | 3
43 | Holding | I | 42 | 2 | Time OFF Main water pump | 5 | 5 | 30 | 1min | 5
44 | Holding | I | 42 | 3 | Delay time OFF Main water pump from OFF compressor | 3 | 1 | 15 | 1min | 3
45 | Holding | I | 42 | 11 | OFF time for Unlock pump function start | 48 | 0 | 240 | 1Hr | 48
46 | Holding | I | 42 | 12 | Time ON Main water pump for Unlock pump function | 5 | 0 | 10 | 1sec | 5
47 | Holding | I | 42 | 13 | Time ON water pump1 for Unlock pump function | 5 | 0 | 10 | 1sec | 5
48 | Holding | I | 42 | 14 | Time ON water pump2 for Unlock pump function | 5 | 0 | 10 | 1sec | 5
49 | Holding | I | 42 | 20 | Type of operation of additional water pump (0=disable, 1=depending on Main water pump setting, 2=depending on Main water pump setting but always OFF when the DHW mode is activated, 3=always ON apart if any alarms are activated or if the HP unit is in OFF mode, 4=ON/OFF based on Room air temperature) | 0 | 0 | 4 | - | 0
50 | Holding | I | 43 | 1 | Start temperature of Frost protection on Room air temperature | 14 | 0 | 40 | 0.5°C | 140
51 | Holding | I | 43 | 2 | Hysteresis of Room air temperature of Frost protection | 1 | 0.5 | 5 | 0.5°C | 10
52 | Holding | I | 43 | 3 | Water temperature of Frost protection | 35 | 10 | 60 | 0.5°C | 350
53 | Holding | I | 43 | 4 | Delay time OFF Main water pump from OFF Frost protection operation function | 30 | 0 | 120 | 1sec | 30
9 | Coil | I | 43 | 10 | Frost protection by outdoor temperature 0=disable 1 = enable
54 | Holding | I | 43 | 11 | Start temperature of Frost protection on Outdoor air temperature | 4 | 0 | 10 | 0.5°C | 40
55 | Holding | I | 43 | 12 | Hysteresis of Outdoor air temperature | 3 | 0.5 | 5 | 0.5°C | 30
56 | Holding | I | 43 | 13 | Backup heater set point during Frost protection | 4 | 0 | 10 | 0.5°C | 40
57 | Holding | I | 43 | 14 | Hysteresis of Outgoing water temperature | 3 | 0.5 | 5 | 0.5°C | 30
10 | Coil | I | 43 | 20 | Frost protection based on Outgoing water temperature 0=disable 1 = enable
|  | I | 43 | 21 | Start temperature of Frost protection on Outgoing water temperature | 4 | 0 | 10 | 0.5°C
|  | I | 43 | 22 | Hysteresis of Outgoing water temperature | 3 | 0.5 | 5 | 0.5°C
11 | Coil | I | 43 | 30 | DHW storage frost protection 0=disable 1 = enable
58 | Holding | I | 43 | 31 | Start temperature of Frost protection on DHW tank temperature | 5 | 0 | 60 | 0.5°C | 50
59 | Holding | I | 43 | 32 | Hysteresis of DHW tank temperature | 3 | 0.5 | 5 | 0.5°C | 30
12 | Coil | I | 43 | 40 | Secondary system circuit frost protection 0=disable 1 = enable
60 | Holding | I | 44 | 1 | Room relative humidity value | 60 | 0 | 100 | 1% | 60
|  | I | 44 | 2 | Hysteresis value | 10 | 1 | 100 | 1%
|  | I | 44 | 3 | Humidity sensor property Voltage value1 | 0 | 0 | 10 | 0.1V
|  | I | 44 | 4 | Humidity sensor property Voltage value2 | 10 | 0 | 10 | 0.1V
|  | I | 44 | 5 | Humidity sensor property Function value1 | 0 | 0 | 100 | 1%
|  | I | 44 | 6 | Humidity sensor property Function value2 | 100 | 0 | 100 | 1%
13 | Coil | I | 44 | 10 | Compensation for room humidity (0=disable, 1=enable) | 1 | 0 | 1 | -
61 | Holding | I | 44 | 11 | Room relative humidity value to start increasing Outgoing water temperature set point | 55 | 0 | 100 | 1% | 55
62 | Holding | I | 44 | 12 | Max. Outgoing temperature hysteresis corresponding to 100% relative humidity | 10 | 0.5 | 20 | 0.5°C | 100
63 | Holding | I | 45 | 1 | Mixing valve runtime (from the fully closed to the fully open position) | 120 | 0 | 900 | 10sec | 12
64 | Holding | I | 45 | 2 | Mixing valve integral factor |  |  |  |  | 6
65 | Holding | I | 45 | 3 | Max Water temperature in mixing circuit |  |  |  |  | 500
66 | Holding | I | 45 | 11 | 3way valve change over time | 60 | 1 | 900 | 1sec | 60
67 | Holding | I | 45 | 21 | Flow switch alarm delay time at. Pump start up |  |  |  |  | 15
68 | Holding | I | 45 | 22 | Flow switch alarm delay time in steady operation of the water pump |  |  |  |  | 2
69 | Holding | I | 45 | 23 | The number of retry until displaying alarm |  |  |  |  | 5
70 | Holding | I | 45 | 24 | The time of repeating retry until displaying alarm |  |  |  |  | 60
71 | Holding | I | 46 | 0 | Backup heater type of function (0=disable, 1=Replacement mode, 2=Emergency mode, 3=Supplementary mode) | 0 | 0 | 3 | - | 0
72 | Holding | I | 46 | 1 | Manual water set point | 50 | 40 | 60 | 0.5°C | 500
73 | Holding | I | 46 | 2 | Manual water temperature hysteresis | 5 | 0.5 | 10 | 0.5°C | 50
74 | Holding | I | 46 | 3 | Delay time of the heater OFF that avoid flow switch alarm |  |  |  | 1 sec | 10
75 | Holding | I | 46 | 4 | Heater activation delay time | 5 | 0 | 900 | 1min | 5
76 | Holding | I | 46 | 5 | Integration time for starting heaters | 600 | 0 | 900 | 0C*sec | 600 | Par4600 and Par4700 are synchronized Par4600=1, 2, 3 > Par4700=0 Par470=1, 2 > Par4600=0 (Outgoing water temperature/Actual temperature) x Integration time calculate every 1sec.
14 | coil | I | 46 | 10 | Conditions to be available Backup heaters (0=always enabled, 1=depends on Outdoor air temperature) | 1 | 0 | 1 | -
77 | Holding | I | 46 | 11 | Outdoor air temperature to enable Backup heaters and disable compressor | -5 | -20 | 20 | 0.5°C | 65486
78 | Holding | I | 46 | 12 | Outdoor air temperature hysteresis to disable Backup heaters and enable compressor | 5 | 0.5 | 10 | 0.5°C | 50
79 | Holding | I | 46 | 13 | Outdoor air temperature to enable Backup heaters (Supplementary mode) | 5 | -20 | 20 | 0.5°C | 50
80 | Holding | I | 46 | 14 | Outdoor air temperature hysteresis to disable Backup heaters (Supplementary mode) | 5 | 0.5 | 10 | 0.5°C | 50
81 | Holding | I | 46 | 20 | Freeze protection functions (0=disable, 1=enabled during Start-up, 2=enabled during Defrost, 3=enabled during Start-up and Defrost) | 0 | 0 | 3 | - | 0
82 | Holding | I | 46 | 21 | Outgoing water temperature set point during Start-up | 8 | 0 | 60 | 0.5°C | 80
83 | Holding | I | 46 | 22 | Hysteresis water temperature set point during Start-up | 5 | 0.5 | 10 | 0.5°C | 50
|  | I | 46 | 23 | Outgoing water temperature set point during Defrost | 24 | 10 | 50 | 0.5°C
|  | I | 46 | 24 | Hysteresis water temperature set point during Defrost | 5 | 0.5 | 10 | 0.5°C
84 | Holding | I | 47 | 0 | EHS type of function (0=disable, 1=Replacement mode, 2=Supplementary mode) | 0 | 0 | 2 | - | 0
|  | I | 47 | 1 | Conditions to be available EHS (0=always enabled, 1=depends on Outdoor air temperature) | 1 | 0 | 1 | -
85 | Holding | I | 47 | 2 | Outdoor air temperature to enable EHS and disable compressor | -5 | -20 | 20 | 0.5°C | 65486
86 | Holding | I | 47 | 3 | Outdoor air temperature hysteresis to disable EHS and enable compressor | 5 | 0.5 | 10 | 0.5°C | 50
87 | Holding | I | 47 | 4 | Outdoor air temperature to enable EHS (Supplementary mode) | 5 | -20 | 20 | 0.5°C | 50
88 | Holding | I | 47 | 5 | Outdoor air temperature hysteresis to disable EHS (Supplementary mode) | 5 | 0.5 | 10 | 0.5°C | 50
89 | Holding | I | 47 | 6 | EHS activation delay time | 5 | 0 | 900 | 1min | 5
90 | Holding | I | 47 | 7 | Integration time for starting EHS | 600 | 0 | 900 | 0C*sec | 600 | Par4600 and Par4700 are synchronized Par4600=1, 2, 3 > Par4700=0 Par470=1, 2 > Par4600=0 (Outgoing water temperature/Actual temperature) x Integration time Calculate every 1 sec
16 | Coil | I | 51 | 1 | Terminal 1-2-3 : Remote Controller (1=enable) | 1 | 1 | 1 | -
17 | Coil | I | 51 | 4 | Terminal 4-5-6 : 3way mixing valve (0=disable, 1=enable) | 0 | 0 | 1 | -
18 | Coil | I | 51 | 7 | Terminal 7-8 : DHW tank temperature probe (0=disable, 1=enable) | 0 | 0 | 1 | -
19 | Coil | I | 51 | 9 | Terminal 9-10 : Outdoor air temperature probe (additional) (0=disable, 1=enable) | 0 | 0 | 1 | -
20 | Coil | I | 51 | 11 | Terminal 11-12 : Buffer tank temperature probe (0=disable, 1=enable) | 0 | 0 | 1 | - |  | To be set to the following combinations Par5111=0 > Par4200=0 or 2 Par5111=1 > Par4200=0 or1 or 2
21 | Coil | I | 51 | 13 | Terminal 13-14 : Mix Water temperature probe (0=disable, 1=enable) | 0 | 0 | 1 | -
22 | Coil | I | 51 | 15 | Terminal 15-16-32 : RS485 Mod Bus (0=disable, 1=enable) | 1 | 0 | 1 | -
23 | Coil | I | 51 | 17 | Terminal 17-18 : Humidity sensor (0=disable, 1=enable) | 0 | 0 | 1 | -
24 | Coil | I | 51 | 19 | Terminal 19-18 : DHW remote contact (0=disable (Remote controller only), 1=enable) | 0 | 0 | 1 | -
91 | Holding | I | 51 | 20 | Terminal 20-21 : ON/OFF remote contact or EHS Alarm input (0=disable (Remote controller only), 1=ON/OFF remote contact, 2=EHS Alarm input) | 0 | 0 | 2 | - | 1
25 | Coil | I | 51 | 22 | Terminal 22-23 : Dual set point control (0=disable, 1=enable) | 1 | 0 | 1 | - |  | ON/OFF by Remote controller 0=enable 1=ON/disable OFF/enable 2=enable
92 | Holding | I | 51 | 24 | Terminal 24-25 : Heating/Cooling mode remote contact (0=disable (Remote controller only), 1=Cooling is CLOSE contact Heating is OPEN contact, 2=Cooling is OPEN contact Heating is CLOSE contact) | 0 | 0 | 2 | - | 1
26 | Coil | I | 51 | 26 | Terminal 26-27 : Flow switch (0=disable, 1=enable) | 1 | 0 | 1 | -
27 | Coil | I | 51 | 28 | Terminal 28-29 : Night mode (0=disable (Remote controller only), 1=enable) | 0 | 0 | 1 | - |  | Par5128 and Par5130 are synchronized in same value
28 | Coil | I | 51 | 30 | Terminal 30-31 : Low tariff (0=disable (Remote controller only), 1=enable) | 0 | 0 | 1 | -
29 | Coil | I | 51 | 41 | Terminal 41-42 : EHS (External heat source for space heating) (0=disable, 1=enable) | 0 | 0 | 1 | -
30 | Coil | I | 51 | 43 | Terminal 43-44 : Heating/Cooling mode output (0=disable, 1=Indication of Cooling mode (CLOSE=Cooling), 2=indication of Heating mode (CLOSE=Heating)) | 0 | 0 | 2 | -
31 | Coil | I | 51 | 45 | Terminal 45 : Dehumidifier (0=disable, 1=enable) | 0 | 0 | 1 | -
32 | Coil | I | 51 | 46 | Terminal 46 : DHW Electric heater or Backup heater (0=DHW Electric heater, 1=Backup heater) | 0 | 0 | 1 | -
93 | Holding | I | 51 | 47 | Terminal 47 : Alarm (Configurable output) (0=disable, 1=Alarm, 2=Ambient temperature reached) | 0 | 0 | 2 | - | 0
94 | Holding | I | 51 | 48 | Terminal 48 : Pump1 (0=disable, 1=1st Additional water pump1 for Zone1) | 0 | 0 | 1 | - | 0
95 | Holding | I | 51 | 49 | Terminal 49 : Pump2 (0=disable, 1=2nd Additional water pump2 for Zone2) | 0 | 0 | 1 | - | 0
96 | Holding | I | 51 | 50 | Terminal 50-51-52 : DHW 3way valve (1=enable) | 1 | 1 | 1 | - | 0
97 | Holding |  |  |  | Room set point target Master C? |  |  |  |  | 200
98 | Holding |  |  |  | Room set point target Slave C? |  |  |  |  | 250

## Input Registers
Modbus Address | Register Type | Level | Group | Code | Function_Description | Default | Min | Max | Unit | Curent Values | Remarks
0 | Input | U | 01 | 00 | Return water temperature | - | -20 | 100 | 1°C | 19 | monitor display No.d0
1 | Input | U | 01 | 01 | Compressor operating frequency | - | 0 | 200 | 1Hz | 0 | monitor display No.d1
2 | Input | U | 01 | 02 | Discharge temperature | - | -20 | 150 | 1°C | 20 | monitor display No.d2
3 | Input | U | 01 | 03 | Current consumption value | - | 0 | 9900 | 100W | 0 | monitor display No.d3
4 | Input | U | 01 | 04 | Fan control number of rotation | - | 0 | 1000 | 10rpm | 0
5 | Input | U | 01 | 05 | Defrost temperature | - | -20 | 100 | 1°C | 16 | monitor display No.d5
6 | Input | U | 01 | 06 | Outdoor air temperature | - | -20 | 100 | 1°C | 18 | monitor display No.d6
7 | Input | U | 01 | 07 | Water pump control number of rotation | - | 0 | 9900 | 100rpm | 0 | monitor display No.d7
8 | Input | U | 01 | 08 | Suction temperature | - | -20 | 100 | 1°C | 19 | monitor display No.d8
9 | Input | U | 01 | 09 | Outgoing water temperature | - | -20 | 100 | 1°C | 21 | monitor display No.d9
10 | Input | U | 01 | 10 | Selected operating mode (0=Heating/Cooling OFF, 1=Heating, 2=Cooling) | 0 | 0 | 2 | - | 0 | Set by Remote controller or remote contact
11 | Input | U | 01 | 11 | Room air set temperature of Zone1(Master) | 25 | 12 | 40 | 0.5°C | 200 | Set by Master Remote controller
12 | Input | U | 01 | 12 | Room air set temperature of Zone2(Slave) | 25 | 12 | 40 | 0.5°C | 250 | Set by Slave Remote controller
13 | Input | U | 01 | 13 | Selected DHW operating mode (0=disable, 1=Comfort, 2=Economy, 3=Force) | 0 | 0 | 3 | - | 0 | Set by Remote controller
14 | Input | U | 01 | 14 | Day (0=Monday, 1=Tuesday, 2=Wednesday, 3=Thursday, 4=Friday, 5=Saturday, 6=Sunday) | 0 | 0 | 6 | - | 0
15 | Input | U | 01 | 15 | Clock | 12:00 | 0:00 | 23:59 | 1min | 0
16 | Input | I | 01 | 31 | DHW tank temperature (Terminal 7-8) | - | -20 | 100 | 0.5°C | 470
17 | Input | I | 01 | 32 | Outdoor air temperature (Terminal 9-10) | - | -20 | 100 | 0.5°C | 65336
18 | Input | I | 01 | 33 | Buffer tank temperature (Terminal 11-12) | - | -20 | 100 | 0.5°C | 65336
19 | Input | I | 01 | 34 | Mix water temperature (Terminal 13-14) | - | -20 | 100 | 0.5°C | 65336
20 | Input | I | 01 | 35 | Humidity sensor (Terminal 17-18) | - | 0 | 100 | 1% | 0
21 | Input | I | 01 | 50? | ?Current error code |  |  |  |  | 32381
22 | Input | I | 01 | 51? | ?Error code once before | -32539 |  |  |  | 33004
23 | Input | I | 01 | 52? | ?Error code twice before | -32540 |  |  |  | 32995
24 | Input | I | 01 | 53? | ?Error code three times before | -32541 |  |  |  | 32994
25 | Input | I | 01 | 54? | ?Error code four times before | -32542 |  |  |  | 32993
26 | Input | I | 01 | 55? | ?Error code five times before | -32543 |  |  |  | 32993
27 | Input | I | 01 | 56? | ?Error code six times before | -32591 |  |  |  | 32993
28 | Input | I | 01 | 57? | ?Error code seven times before | 32381 |  |  |  | 32993
29 | Input | I | 01 | 58? | ?Error code eight times before | 32381 |  |  |  | 32993
30 | Input | I | 01 | 59? | ?Error code nine times before | 32381 |  |  |  | 32993
31 | Input | I | 01 | 60? | ?Error code ten times before | 32381 |  |  |  | 32993
32 | Input | U | 01 | 72 | Plate heat exchanger temperature | - | -20 | 100 | 1°C | 20 | monitor display No.d4

## Holding Registers
Modbus Address | Register Type | Level | Group | Code | Function_Description | Default | Min | Max | Unit | Current Values | Remarks
0 | [9 empty] | 0
1 | [9 empty] | 0
2 | Holding | I | 21 | 01 | Heating Zone1, Fixed Outgoing water set point in Heating | 45 | 23 | 60 | 0.5°C | 255
3 | Holding | I | 21 | 02 | Max. Outgoing water temperature in Heating mode (Tm1) Zone1 | 45 | 23 | 60 | 0.5°C | 300
4 | Holding | I | 21 | 03 | Min. Outgoing water temperature in Heating mode (Tm2) Zone1 | 30 | 23 | 60 | 0.5°C | 230
5 | Holding | I | 21 | 04 | Min. Outdoor air temperature corresponding to max. Outgoing water temperature (Te1) Zone1 | 0 | -20 | 50 | 0.5°C | 65506
6 | Holding | I | 21 | 05 | Max. Outdoor air temperature corresponding to max. Outgoing water temperature (Te2) Zone1 | 20 | 0 | 40 | 0.5°C | 160
7 | Holding | I | 21 | 11 | Heating Zone2, Fixed Outgoing water set point in Heating | 45 | 23 | 60 | 0.5°C | 450
8 | Holding | I | 21 | 12 | Max. Outgoing water temperature in Heating mode (Tm1) Zone2 | 45 | 23 | 60 | 0.5°C | 450
9 | Holding | I | 21 | 13 | Min. Outgoing water temperature in Heating mode (Tm2) Zone2 | 30 | 23 | 60 | 0.5°C | 300
10 | Holding | I | 21 | 14 | Min. Outdoor air temperature corresponding to max. Outgoing water temperature (Te1) Zone2 | 0 | -20 | 50 | 0.5°C | 0
11 | Holding | I | 21 | 15 | Max. Outdoor air temperature corresponding to max. Outgoing water temperature (Te2) Zone2 | 20 | 0 | 40 | 0.5°C | 200
12 | Holding | I | 21 | 21 | Cooling Zone1, Fixed Outgoing water set point in Cooling | 7 | 7 | 23 | 0.5°C | 70
13 | Holding | I | 21 | 22 | Max. Outgoing water temperature in Cooling mode (Tm1) Zone1 | 20 | 7 | 23 | 0.5°C | 200
14 | Holding | I | 21 | 23 | Min. Outgoing water temperature in Cooling mode (Tm2) Zone1 | 18 | 7 | 23 | 0.5°C | 180
15 | Holding | I | 21 | 24 | Min. Outdoor air temperature corresponding to max. Outgoing water temperature (Te1) Zone1 | 25 | 0 | 50 | 0.5°C | 250
16 | Holding | I | 21 | 25 | Max. Outdoor air temperature corresponding to max. Outgoing water temperature (Te2) Zone1 | 35 | 0 | 50 | 0.5°C | 350
17 | Holding | I | 21 | 31 | Cooling Zone2, Fixed Outgoing water set point in Cooling | 7 | 7 | 23 | 0.5°C | 70
18 | Holding | I | 21 | 32 | Max. Outgoing water temperature in Cooling mode (Tm1) Zone2 | 20 | 7 | 23 | 0.5°C | 200
19 | Holding | I | 21 | 33 | Min. Outgoing water temperature in Cooling mode (Tm2) Zone2 | 18 | 7 | 23 | 0.5°C | 180
20 | Holding | I | 21 | 34 | Min. Outdoor air temperature corresponding to max. Outgoing water temperature (Te1) Zone2 | 25 | 0 | 50 | 0.5°C | 250
21 | Holding | I | 21 | 35 | Max. Outdoor air temperature corresponding to max. Outgoing water temperature (Te2) Zone2 | 35 | 0 | 50 | 0.5°C | 350
22 | Holding | I | 21 | 41 | Hysteresis of water set point in Heating and DHW | 8 | 0.5 | 10 | 0.5°C | 40
23 | Holding | I | 21 | 42 | Hysteresis of water set point in Cooling | 8 | 0.5 | 10 | 0.5°C | 80
24 | Holding | I | 21 | 51 | Low tariff deferential water set point for Heating | 5 | 0 | 60 | 0.5°C | 50
25 | Holding | I | 21 | 52 | Low tariff deferential water set point for Cooling | 5 | 0 | 60 | 0.5°C | 50
26 | Holding | I | 31 | 01 | DHW production priority setting (0=DHW is unavailable, 1=DHW is available and priority DHW over space Heating, 2=DHW is available and priority space Heating over DHW) | 0 | 0 | 2 | - | 1
27 | Holding | I | 31 | 02 | Type of configuration to heat the DHW (0=Heat pump + Heater, 1=Heat pump only, 2=Heater only) | 1 | 0 | 2 | - | 1
28 | Holding | I | 31 | 11 | DHW Comfort set temperature | 50 | 40 | 60 | 0.5°C | 470
29 | Holding | I | 31 | 12 | DHW Economy set temperature | 40 | 30 | 50 | 0.5°C | 430
30 | Holding | I | 31 | 13 | DHW set point hysteresis | 3 | 0.5 | 10 | 0.5°C | 30
31 | Holding | I | 31 | 14 | DHW Over boost mode set point | 60 | 50 | 90 | 0.5°C | 600
32 | Holding | I | 31 | 21 | Max. time for DHW request | 60 | 0 | 900 | 1min | 60
33 | Holding | I | 31 | 31 | Delay time on DHW heater from OFF compressor | 30 |  |  | 1min | 30
34 | Holding | I | 31 | 33 | Outdoor air temperature to enable DHW heaters | -5 | -20 | 20 | 0.5°C | 65486
35 | Holding | I | 31 | 34 | Outdoor air temperature hysteresis to disable DHW heaters | 5 | 0.5 | 10 | 0.5°C | 50
36 | Holding | S | 31 | 44 | Anti-legionella set point |  |  |  | 0.5°C | 650
37 | Holding | I | 41 | 11 | Max. frequency of Night mode | 80 | 50 | 100 | 5% | 80
38 | Holding | I | 41 | 21 | Min. time compressor ON/OFF time | 0 | 0 | 0 | 1sec | 0
39 | Holding | I | 41 | 22 | Delay time pump OFF from compressor OFF | 30 | 0 | 900 | 1sec | 30
40 | Holding | I | 41 | 23 | Delay time compressor ON from pump ON | 30 | 0 | 900 | 1sec | 30
41 | Holding | I | 42 | 00 | Type of configuration of Main water pump (0=always ON, 1=ON/OFF based on Buffer tank temperature, 2=ON/OFF based on Sniffing cycles) | 0 | 0 | 2 | - | 0 | To be set to the following combinations Par5111=0 uc0u8594 Par4200=0 or 2 Par5111=1 u8594 Par4200=0 or 1 or 2
42 | Holding | I | 42 | 01 | Time ON Main water pump for Sniffing cycle | 3 | 1 | 15 | 1min | 3
43 | Holding | I | 42 | 02 | Time OFF Main water pump | 5 | 5 | 30 | 1min | 5
44 | Holding | I | 42 | 03 | Delay time OFF Main water pump from OFF compressor | 3 | 1 | 15 | 1min | 3
45 | Holding | I | 42 | 11 | OFF time for Unlock pump function start | 48 | 0 | 240 | 1Hr | 48
46 | Holding | I | 42 | 12 | Time ON Main water pump for Unlock pump function | 5 | 0 | 10 | 1sec | 5
47 | Holding | I | 42 | 13 | Time ON water pump1 for Unlock pump function | 5 | 0 | 10 | 1sec | 5
48 | Holding | I | 42 | 14 | Time ON water pump2 for Unlock pump function | 5 | 0 | 10 | 1sec | 5
49 | Holding | I | 42 | 20 | Type of operation of additional water pump (0=disable, 1=depending on Main water pump setting, 2=depending on Main water pump setting but always OFF when the DHW mode is activated, 3=always ON apart if any alarms are activated or if the HP unit is in OFF mode, 4=ON/OFF based on Room air temperature) | 0 | 0 | 4 | - | 0
50 | Holding | I | 43 | 01 | Start temperature of Frost protection on Room air temperature | 14 | 0 | 40 | 0.5°C | 140
51 | Holding | I | 43 | 02 | Hysteresis of Room air temperature of Frost protection | 1 | 0.5 | 5 | 0.5°C | 10
52 | Holding | I | 43 | 03 | Water temperature of Frost protection | 35 | 10 | 60 | 0.5°C | 350
53 | Holding | I | 43 | 04 | Delay time OFF Main water pump from OFF Frost protection operation function | 30 | 0 | 120 | 1sec | 30
54 | Holding | I | 43 | 11 | Start temperature of Frost protection on Outdoor air temperature | 4 | 0 | 10 | 0.5°C | 40
55 | Holding | I | 43 | 12 | Hysteresis of Outdoor air temperature | 3 | 0.5 | 5 | 0.5°C | 30
56 | Holding | I | 43 | 13 | Backup heater set point during Frost protection | 4 | 0 | 10 | 0.5°C | 40
57 | Holding | I | 43 | 14 | Hysteresis of Outgoing water temperature | 3 | 0.5 | 5 | 0.5°C | 30
58 | Holding | I | 43 | 31 | Start temperature of Frost protection on DHW tank temperature | 5 | 0 | 60 | 0.5°C | 50
59 | Holding | I | 43 | 32 | Hysteresis of DHW tank temperature | 3 | 0.5 | 5 | 0.5°C | 30
60 | Holding | I | 44 | 01 | Room relative humidity value | 60 | 0 | 100 | 1% | 60
61 | Holding | I | 44 | 11 | Room relative humidity value to start increasing Outgoing water temperature set point | 55 | 0 | 100 | 1% | 55
62 | Holding | I | 44 | 12 | Max. Outgoing temperature hysteresis corresponding to 100% relative humidity | 10 | 0.5 | 20 | 0.5°C | 100
63 | Holding | I | 45 | 01 | Mixing valve runtime (from the fully closed to the fully open position) | 120 | 0 | 900 | 10sec | 12
64 | Holding | I | 45 | 02 | Mixing valve integral factor |  |  |  |  | 6
65 | Holding | I | 45 | 03 | Max Water temperature in mixing circuit |  |  |  |  | 500
66 | Holding | I | 45 | 11 | 3way valve change over time | 60 | 1 | 900 | 1sec | 60
67 | Holding | I | 45 | 21 | Flow switch alarm delay time at. Pump start up |  |  |  |  | 15
68 | Holding | I | 45 | 22 | Flow switch alarm delay time in steady operation of the water pump |  |  |  |  | 2
69 | Holding | I | 45 | 23 | The number of retry until displaying alarm |  |  |  |  | 5
70 | Holding | I | 45 | 24 | The time of repeating retry until displaying alarm |  |  |  |  | 60
71 | Holding | I | 46 | 00 | Backup heater type of function (0=disable, 1=Replacement mode, 2=Emergency mode, 3=Supplementary mode) | 0 | 0 | 3 | - | 0
72 | Holding | I | 46 | 01 | Manual water set point | 50 | 40 | 60 | 0.5°C | 500
73 | Holding | I | 46 | 02 | Manual water temperature hysteresis | 5 | 0.5 | 10 | 0.5°C | 50
74 | Holding | I | 46 | 03 | Delay time of the heater OFF that avoid flow switch alarm |  |  |  | 1 sec | 10
75 | Holding | I | 46 | 04 | Heater activation delay time | 5 | 0 | 900 | 1min | 5
76 | Holding | I | 46 | 05 | Integration time for starting heaters | 600 | 0 | 900 | 0C*sec | 600 | Par4600 and Par4700 are synchronized Par4600=1, 2, 3 uc0u8594 Par4700=0 Par470=1, 2 u8594 Par4600=0 (Outgoing water temperature/Actual temperature) x Integration time calculate every 1sec.
77 | Holding | I | 46 | 11 | Outdoor air temperature to enable Backup heaters and disable compressor | -5 | -20 | 20 | 0.5°C | 65486
78 | Holding | I | 46 | 12 | Outdoor air temperature hysteresis to disable Backup heaters and enable compressor | 5 | 0.5 | 10 | 0.5°C | 50
79 | Holding | I | 46 | 13 | Outdoor air temperature to enable Backup heaters (Supplementary mode) | 5 | -20 | 20 | 0.5°C | 50
80 | Holding | I | 46 | 14 | Outdoor air temperature hysteresis to disable Backup heaters (Supplementary mode) | 5 | 0.5 | 10 | 0.5°C | 50
81 | Holding | I | 46 | 20 | Freeze protection functions (0=disable, 1=enabled during Start-up, 2=enabled during Defrost, 3=enabled during Start-up and Defrost) | 0 | 0 | 3 | - | 0
82 | Holding | I | 46 | 21 | Outgoing water temperature set point during Start-up | 8 | 0 | 60 | 0.5°C | 80
83 | Holding | I | 46 | 22 | Hysteresis water temperature set point during Start-up | 5 | 0.5 | 10 | 0.5°C | 50
84 | Holding | I | 47 | 00 | EHS type of function (0=disable, 1=Replacement mode, 2=Supplementary mode) | 0 | 0 | 2 | - | 0
85 | Holding | I | 47 | 02 | Outdoor air temperature to enable EHS and disable compressor | -5 | -20 | 20 | 0.5°C | 65486
86 | Holding | I | 47 | 03 | Outdoor air temperature hysteresis to disable EHS and enable compressor | 5 | 0.5 | 10 | 0.5°C | 50
87 | Holding | I | 47 | 04 | Outdoor air temperature to enable EHS (Supplementary mode) | 5 | -20 | 20 | 0.5°C | 50
88 | Holding | I | 47 | 05 | Outdoor air temperature hysteresis to disable EHS (Supplementary mode) | 5 | 0.5 | 10 | 0.5°C | 50
89 | Holding | I | 47 | 06 | EHS activation delay time | 5 | 0 | 900 | 1min | 5
90 | Holding | I | 47 | 07 | Integration time for starting EHS | 600 | 0 | 900 | 0C*sec | 600 | Par4600 and Par4700 are synchronized Par4600=1, 2, 3 uc0u8594 Par4700=0 Par470=1, 2 u8594 Par4600=0 (Outgoing water temperature/Actual temperature) x Integration time Calculate every 1 sec
91 | Holding | I | 51 | 20 | Terminal 20-21 : ON/OFF remote contact or EHS Alarm input (0=disable (Remote controller only), 1=ON/OFF remote contact, 2=EHS Alarm input) | 0 | 0 | 2 | - | 1
92 | Holding | I | 51 | 24 | Terminal 24-25 : Heating/Cooling mode remote contact (0=disable (Remote controller only), 1=Cooling is CLOSE contact Heating is OPEN contact, 2=Cooling is OPEN contact Heating is CLOSE contact) | 0 | 0 | 2 | - | 1
93 | Holding | I | 51 | 47 | Terminal 47 : Alarm (Configurable output) (0=disable, 1=Alarm, 2=Ambient temperature reached) | 0 | 0 | 2 | - | 0
94 | Holding | I | 51 | 48 | Terminal 48 : Pump1 (0=disable, 1=1st Additional water pump1 for Zone1) | 0 | 0 | 1 | - | 0
95 | Holding | I | 51 | 49 | Terminal 49 : Pump2 (0=disable, 1=2nd Additional water pump2 for Zone2) | 0 | 0 | 1 | - | 0
96 | Holding | I | 51 | 50 | Terminal 50-51-52 : DHW 3way valve (1=enable) | 1 | 1 | 1 | - | 0
97 | Holding |  |  |  | Room set point target Master C? |  |  |  |  | 200
98 | Holding |  |  |  | Room set point target Slave C? |  |  |  |  | 250
99 | Holding | I | 21 | 61 | Buffer tank set point for Heating | 45 | 23 | 60 | 0.5°C
100 | Holding | I | 21 | 62 | Buffer tank set point for Cooling | 7 | 7 | 23 | 0.5°C

## Coil Registers
Modbus Address | Register Type | Level | Group | Code | Function_Description | Default | Min | Max | Unit | Read Value | Remarks
1 | Coil | I | 3 | 00 | Operation at the time of reboot after blackout 0 = disable 1 = enable | 1 | 0 | 1 |  | TRUE
2 | Coil | I | 21 | 00 | Heating Zone1, enable Outgoing water set point (0=Fixed set point, 1=Climatic curve) | 0 | 0 | 1 | - | TRUE
3 | Coil | I | 21 | 10 | Heating Zone2, enable Outgoing water set point (0=Fixed set point, 1=Climatic curve enabled) | 0 | 0 | 1 | - | FALSE
4 | Coil | I | 21 | 20 | Cooling Zone1, enable Outgoing water set point (0=Fixed set point, 1=Climatic curve enabled) | 0 | 0 | 1 | - | FALSE
5 | Coil | I | 21 | 30 | Cooling Zone2, enable Outgoing water set point (0=Fixed set point, 1=Climatic Curve Enabled) | 0 | 0 | 1 | - | FALSE
6 | coil | I | 31 | 40 | Anti-legionella function (0=disable, 1=enable) | 0 | 0 | 1 | - | TRUE
7 | Coil | I | 41 | 00 | The HP unit turns ON/OFF based on (0=Room set point, 1=Water set point) | 1 | 0 | 1 | - | TRUE
9 | Coil | I | 43 | 10 | Frost protection by outdoor temperature 0=disable 1 = enable |  |  |  |  | FALSE
10 | Coil | I | 43 | 20 | Frost protection based on Outgoing water temperature 0=disable 1 = enable |  |  |  |  | FALSE
11 | Coil | I | 43 | 30 | DHW storage frost protection 0=disable 1 = enable |  |  |  |  | FALSE
12 | Coil | I | 43 | 40 | Secondary system circuit frost protection 0=disable 1 = enable |  |  |  |  | FALSE
13 | Coil | I | 44 | 10 | Compensation for room humidity (0=disable, 1=enable) | 1 | 0 | 1 | - | TRUE
14 | coil | I | 46 | 10 | Conditions to be available Backup heaters (0=always enabled, 1=depends on Outdoor air temperature) | 1 | 0 | 1 | - | FALSE
16 | Coil | I | 51 | 01 | Terminal 1-2-3 : Remote Controller (1=enable) | 1 | 1 | 1 | - | TRUE
17 | Coil | I | 51 | 04 | Terminal 4-5-6 : 3way mixing valve (0=disable, 1=enable) | 0 | 0 | 1 | - | TRUE
18 | Coil | I | 51 | 07 | Terminal 7-8 : DHW tank temperature probe (0=disable, 1=enable) | 0 | 0 | 1 | - | TRUE
19 | Coil | I | 51 | 09 | Terminal 9-10 : Outdoor air temperature probe (additional) (0=disable, 1=enable) | 0 | 0 | 1 | - | FALSE
20 | Coil | I | 51 | 11 | Terminal 11-12 : Buffer tank temperature probe (0=disable, 1=enable) | 0 | 0 | 1 | - | TRUE | To be set to the following combinations Par5111=0 > Par4200=0 or 2 Par5111=1 > Par4200=0 or1 or 2
21 | Coil | I | 51 | 13 | Terminal 13-14 : Mix Water temperature probe (0=disable, 1=enable) | 0 | 0 | 1 | - | FALSE
22 | Coil | I | 51 | 15 | Terminal 15-16-32 : RS485 Mod Bus (0=disable, 1=enable) | 1 | 0 | 1 | - | FALSE
23 | Coil | I | 51 | 17 | Terminal 17-18 : Humidity sensor (0=disable, 1=enable) | 0 | 0 | 1 | - | FALSE
24 | Coil | I | 51 | 19 | Terminal 19-18 : DHW remote contact (0=disable (Remote controller only), 1=enable) | 0 | 0 | 1 | - | TRUE
25 | Coil | I | 51 | 22 | Terminal 22-23 : Dual set point control (0=disable, 1=enable) | 1 | 0 | 1 | - | FALSE | ON/OFF by Remote controller 0=enable 1=ON/disable OFF/enable 2=enable
26 | Coil | I | 51 | 26 | Terminal 26-27 : Flow switch (0=disable, 1=enable) | 1 | 0 | 1 | - | TRUE
27 | Coil | I | 51 | 28 | Terminal 28-29 : Night mode (0=disable (Remote controller only), 1=enable) | 0 | 0 | 1 | - | TRUE | Par5128 and Par5130 are synchronized in same value
28 | Coil | I | 51 | 30 | Terminal 30-31 : Low tariff (0=disable (Remote controller only), 1=enable) | 0 | 0 | 1 | - | TRUE
29 | Coil | I | 51 | 41 | Terminal 41-42 : EHS (External heat source for space heating) (0=disable, 1=enable) | 0 | 0 | 1 | - | TRUE
30 | Coil | I | 51 | 43 | Terminal 43-44 : Heating/Cooling mode output (0=disable, 1=Indication of Cooling mode (CLOSE=Cooling), 2=indication of Heating mode (CLOSE=Heating)) | 0 | 0 | 2 | - | TRUE
31 | Coil | I | 51 | 45 | Terminal 45 : Dehumidifier (0=disable, 1=enable) | 0 | 0 | 1 | - | FALSE
32 | Coil | I | 51 | 46 | Terminal 46 : DHW Electric heater or Backup heater (0=DHW Electric heater, 1=Backup heater) | 0 | 0 | 1 | - | FALSE
33 | [9 empty] | FALSE
34 | [9 empty] | FALSE